## Sheet1
| CreatedOn | Notification | OrderNum | ShortText | FLOC | LongText | Question | Answer
0 | 2019-03-15 | 30761040 | 90231415 | Abrupt decrease in 18B Pump pressure | S4CW -4CWE7 | * **************Incident Description************** * Notification 000030761040 Details * *********************************************************** * 03/15/2019 15:26:32 INCIDENT REPORT (INCIDENT REPORT) * Report submitted by: James Franklin ENTITY\INCIDENT: * * CONDITION DESCRIPTION/LOCATION (THE INAPPROPRIATE ACTION AND ITS NEGATIVE EFFECT/INCLUDE A DETAILED LOCATION DESCRIPTION): * During regular inspection on 03/15/2019, 18B Pump was found operating at a significantly lower pressure than usual. Initial measurement showed 34 psig, which is lower than the average operating pressure of the pump. All necessary pressure checks were made and potential leak points inspected. Noise and heat generation appear to be in normal range, but the decreased pressure could indicate an internal compromise in the pump or a problem in the supply line. * * ACTIVITIES, PROCESSES, PROCEDURES INVOLVED: * Regular monitoring and safety checks * * WHY DID CONDITION HAPPEN? * Cause currently unknown, suspect problem with supply line or internal pump damage. * * CONSEQUENCES: * Potential reduced pump efficiency, internal damage, and process disruption * * REQUIREMENTS IMPACTED: * Normal operation, potential safety hazard * * ADVERSE PHYSICAL CONDITIONS: * Abnormally low pressure in the 18B Pump * * WHO WAS NOTIFIED: * Supervisor, Maintenance Team, 4th Floor Control Room * * KNOWLEDGEABLE INDIVIDUALS: * Maintenance Team, Pump Specialist Team * * REPEAT OR SIMILAR CONDITION: * No, first time * * IMMEDIATE ACTIONS AND RECOMMENDED ACTIONS: * Isolate 18B Pump and investigate for internal damage or supply line obstructions. Repair or replacement may be required, pending investigation results. * 03/16/2019 11:59:00 JAMES FRANKLIN (INCIDENT) * The preliminary investigation shows there may be debris buildup causing the noticeable decrease in pump pressure. Further checks required to confirm. | What immediate actions were recommended following the discovery of abnormally low pressure in the 18B Pump? | Isolate 18B Pump and investigate for internal damage or supply line obstructions. Repair or replacement may be required, pending investigation results.
1 | 2020-11-18 | 30958076 | 80230196 | Reduced output from 5B Generator | S5GN -5GNE2-GENR | * **************Incident Description************** * Notification 000030958076 Details * *********************************************************** * 11/18/2020 07:22:19 INCIDENT REPORT (INCIDENT REPORT) * Report submitted by: Daniel Thomas ENTITY\INCIDENT: * * CONDITION DESCRIPTION/LOCATION (THE INAPPROPRIATE ACTION AND ITS NEGATIVE EFFECT/INCLUDE A DETAILED LOCATION DESCRIPTION): * Routine daily plant data analysis showed 5B Generator output reduced by 20% post regular maintenance under work order 80218907, compared to pre-maintenance values. All parameters including temperature, flow rates, and vibration are within normal limits, but output is reduced. The generator alarm was not triggered because all parameters were within the limits, only observable through data analysis. * * ACTIVITIES, PROCESSES, PROCEDURES INVOLVED: * S5.OP.GN-0002 Generator Monitoring and Analysis Procedure * * WHY DID CONDITION HAPPEN? * Not certain, possibly due to an issue during the recent maintenance work, or a latent defect in the generator. * * CONSEQUENCES: * Reduction in power generation capacity, potentially reducing plant operational flexibility. * * REQUIREMENTS IMPACTED: * Generation targets * * ADVERSE PHYSICAL CONDITIONS: * Reduced output power * * WHO WAS NOTIFIED: * Site manager, Maintenance Team, Operational Support Team * * KNOWLEDGEABLE INDIVIDUALS: * Operational Support Team, Maintenance Team Lead * * REPEAT OR SIMILAR CONDITION: * No, this is a unique condition. * * IMMEDIATE ACTIONS AND RECOMMENDED ACTIONS: * Have the maintenance team re-inspect and perform advanced diagnostics on the 5B Generator under work order 80230196. * 11/20/2020 15:31:52 JOHN DOE (INCIDENT) * The advanced diagnostics found loose connections on the excitation system, causing reduced performance. Connections tightened, generator returned to normal performance. Recommend improving maintenance procedures to ensure connection tightening is not overlooked. | What was found as the cause of reduced performance from the 5B Generator during advanced diagnostics? | The advanced diagnostics found loose connections on the excitation system, causing reduced performance.
2 | 2018-09-15 | 30751256 | 80212345 | Rapid frequency change in Pump 18A | S4CW -4CWE5 | * **************Incident Description************** * Notification 000030751256 Details * *********************************************************** * 09/15/2018 15:17:04 INCIDENT REPORT (INCIDENT REPORT) * Report submitted by: Jake Foster 323-654-7890 ENTITY\INCIDENT: * * CONDITION DESCRIPTION/LOCATION (THE INAPPROPRIATE ACTION AND ITS NEGATIVE EFFECT/INCLUDE A DETAILED LOCATION DESCRIPTION): * During a routine system check, significant frequency fluctuation was detected on Pump 18A. The frequency, which is supposed to remain steady around 50 Hertz, showed rapid variations between 45 and 55 Hertz. This type of behavior is not typical of Pump 18A under normal operating conditions. * * ACTIVITIES, PROCESSES, PROCEDURES INVOLVED: * Regular System Monitoring, S4.OP-SO.CW-0006 * * WHY DID CONDITION HAPPEN? * Initial assessments suggest the frequency fluctuation could either be caused by internal pump damage or malfunctioning of the electrical circuit associated with the pump. * * CONSEQUENCES: * Instability of the pump, risk of pump failure, potential impact on operational efficiency. * * REQUIREMENTS IMPACTED: * Operational Stability * * ADVERSE PHYSICAL CONDITIONS: * High Frequency Fluctuation in Pump 18A. * * WHO WAS NOTIFIED: * On-duty Supervisor, Maintenance team * * KNOWLEDGEABLE INDIVIDUALS: * Maintenance Team, Engineering Team, Supervisor * * REPEAT OR SIMILAR CONDITION: * No, this is the first reported instance. * * IMMEDIATE ACTIONS AND RECOMMENDED ACTIONS: * Immediate action is to isolate and shut down pump 18A for detailed inspection. If the issue persists despite cleanup and basic fixes, a comprehensive investigation with the possibility of pump replacement should be considered. * 09/19/2018 08:43:17 ADAM BLACK * Post-inspection, it was found that the issue of the frequency fluctuation was due to minor internal damage. Repair works have been completed and the pump is back to its normal operation. | What was the immediate action recommended after detecting the frequency fluctuation in Pump 18A? | Immediate action is to isolate and shut down pump 18A for detailed inspection. If the issue persists despite cleanup and basic fixes, a comprehensive investigation with the possibility of pump replacement should be considered.
3 | 2019-11-17 | 30958230 | 80523058 | Unusual noise from 3B Pump motor | S5CW -5CWE2 | * **************Incident Description************** * Notification 000030958230 Details * *********************************************************** * 11/17/2019 07:31:12 INCIDENT REPORT (INCIDENT REPORT) * Report submitted by: Emily Baker ENTITY\INCIDENT: * * CONDITION DESCRIPTION/LOCATION (THE INAPPROPRIATE ACTION AND ITS NEGATIVE EFFECT/INCLUDE A DETAILED LOCATION DESCRIPTION): * During the early morning rounds, operator reported an unusual noise from 3B Pump motor in Unit 5. After immediate shutdown and extraction, a significant amount of filth was found lodged in the pump's interior. This suggests a problem with the filtration system. No heat or other unusual conditions were detected in the surrounding pumps. * * ACTIVITIES, PROCESSES, PROCEDURES INVOLVED: * S5.OP.AB-CW-0002, S5.OP-SO.CW-0002 * * WHY DID CONDITION HAPPEN: * Likely due to failure of the filtration system. * * CONSEQUENCES: * Potential motor damage, higher energy use, reduction of output and performance. * * REQUIREMENTS IMPACTED: * Normal operation, bearable noise levels. * * ADVERSE PHYSICAL CONDITIONS: * Unusually high noise levels from 3B Pump motor. * * WHO WAS NOTIFIED: * Supervisor, Maintenance Team * * KNOWLEDGEABLE INDIVIDUALS: * Thompson, Davis, Lee * * REPEAT OR SIMILAR CONDITION: * No * * IMMEDIATE AND RECOMMENDED ACTIONS: * Inspect filtration systems and remove blockages if any. Install the re-conditioned, and thoroughly cleaned, 3B pump motor after the completion of inspection. Setup review and revise cleaning and maintenance protocols. * 11/18/2019 10:53:02 EMILY BAKER (INCIDENT) * Filters inspected and found a large amount of debris. Filters replaced and system rechecked. 3B pump motor reinstalled and noise has significantly dropped to normal levels. Advised regular inspection and maintenance of filters. | What was the immediate action recommended after the noise was reported from the 3B Pump motor in Unit 5? | Inspect filtration systems and remove blockages if any. Install the re-conditioned, and thoroughly cleaned, 3B pump motor after the completion of inspection. Setup review and revise cleaning and maintenance protocols.
4 | 2016-09-15 | 30751904 | 80225619 | Fuse M87 tripped | S4EL -4EL1746 | * **************Incident Description************** * Notification 000030751904 Details * *********************************************************** * 09/15/2016 14:14:17 INCIDENT REPORT (INCIDENT REPORT) * Report submitted by: Fred Johnson, ENTITY\INCIDENT: * * CONDITION DESCRIPTION/LOCATION (THE INAPPROPRIATE ACTION AND ITS NEGATIVE EFFECT/INCLUDE A DETAILED LOCATION DESCRIPTION): * Fuse M87 has tripped again. Fuse was reset at 1115 following guidance in S4.EL-TS.EL-0002. At 1400, it tripped again. A test was conducted and it was observed that the fuse was hot to touch. Further testing is required to identify the cause. * * ACTIVITIES, PROCESSES, PROCEDURES INVOLVED: * Troubleshooting and resetting of M87 fuse, S4.EL-TS.EL-0002. * * WHY DID CONDITION HAPPEN? * The underlying issue is not determined yet, although the fault could be with the circuit. * * CONSEQUENCES: * Recurring outages of circuit M87. Loss of other associated equipment. * * REQUIREMENTS IMPACTED: * Critical Electrical systems, control system redundancies. * * ADVERSE PHYSICAL CONDITIONS: * Heat in M87 fuse. * * WHO WAS NOTIFIED: * Supervisor, Electrical Maintenance Team * * KNOWLEDGEABLE INDIVIDUALS: * Supervisor, Electrical Maintenance Team, Engineering Department * * REPEAT OR SIMILAR CONDITION: * Yes, multiple recent occurrences with M87 fuse. * * IMMEDIATE ACTIONS AND RECOMMENDED ACTIONS: * Electrical team to perform an analysis of M87 circuit. If fault is found, allocate a repair work order. * 09/22/2016 10:22:59 TOM WILLIAMS (INCIDENT) * The electrical analysis of M87 circuit was conducted and revealed that the circuit was drawing more current than rated. A component in the circuit, relay R45, showed signs of malfunctions that may have caused the high current draw. Recommend replacing relay R45 and tracking it under a new notification. | What was the result of the electrical analysis of the M87 circuit? | The electrical analysis of M87 circuit was conducted and revealed that the circuit was drawing more current than rated. A component in the circuit, relay R45, showed signs of malfunctions that may have caused the high current draw.
5 | 2019-12-01 | 30982374 | 80234567 | Leak detected in 23B Pump | S4CW -4CWE8 | * **************Incident Description************** * Notification 000030982374 Details * *********************************************************** * 12/01/2019 10:12:37 INCIDENT REPORT (INCIDENT REPORT) * Report submitted by: James Richardson ENTITY\INCIDENT: * * CONDITION DESCRIPTION/LOCATION (THE INAPPROPRIATE ACTION AND ITS NEGATIVE EFFECT/INCLUDE A DETAILED LOCATION DESCRIPTION): * After recent maintenance, a leak was observed in the seal of 23B Pump. The maintenance team had worked on this pump under work order 80504836 in Sep 2019 with the aim to replace the old seal. The issue of leak is a significant problem as the leaked substance might enter other components causing overall performance degradation. * * ACTIVITIES, PROCESSES, PROCEDURES INVOLVED: * Maintenance, S4.OP-AB.CW-0001 * * WHY DID CONDITION HAPPEN? * Possibly due to substandard seal or improper installation. * * CONSEQUENCES: * Potential damage to other components, reduced overall system efficiency, pump outage. * * REQUIREMENTS IMPACTED: * Normal operation, Environmental compliance, Safety standards. * * ADVERSE PHYSICAL CONDITIONS: * Leak at pump seal * * WHO WAS NOTIFIED: * Supervisor, Health and Safety Officer, Maintenance Manager. * * KNOWLEDGEABLE INDIVIDUALS: * Maintenance Manager, Seal Supplier, Site Engineer. * * REPEAT OR SIMILAR CONDITION: * No * * IMMEDIATE ACTIONS AND RECOMMENDED ACTIONS: * Immediate shutdown of the pump. Arrangement for replacement of the seal. New seal to be tested for conformity before installation. Investigation to be initiated to determine cause of substandard replacement part. * 12/01/2019 14:30:51 James Richardson (INCIDENT) * The 23B pump has been temporarily shut off. New seal ordered and will be express delivered. Investigation initiated to audit supplier for quality control issues. | What was the immediate action taken following the detection of the leak at the 23B Pump? | Immediate shutdown of the pump.
6 | 2020-02-22 | 40056923 | 91125643 | Unexpected vibration from 8C Cooling Pump | S4CW -4CWE2 | * **************Incident Description************** * Notification 000040056923 Details * *********************************************************** * 02/22/2020 13:23:11 INCIDENT REPORT (INCIDENT REPORT) * Report submitted by: William Banks ENTITY\INCIDENT: * * CONDITION DESCRIPTION/LOCATION (THE INAPPROPRIATE ACTION AND ITS NEGATIVE EFFECT/INCLUDE A DETAILED LOCATION DESCRIPTION): * At approximately 1300 hours, 02/22/2020, during a standard operating check, significant vibration was detected in 8C cooling pump. Pump was isolated and shut down immediately to prevent damage to ancillary equipment. An abnormal vibration was also noted at the motor. No immediate external hindrances were noted. * ACTIVITIES, PROCESSES, PROCEDURES INVOLVED: * S4.OP.AB.CW-0002, S4.OP-SO.CW-0002 * * WHY DID CONDITION HAPPEN? * The cause of the unexpected vibration is currently unknown but could be attributed to a potential mechanical fault internally. Further inspection is required. * * CONSEQUENCES: * Potential equipment failure and efficiency loss if operation was continued. * * REQUIREMENTS IMPACTED: * Availability of 8C Pump. * * ADVERSE PHYSICAL CONDITIONS: * Excessive Vibrations from 8C Cooling Pump, possible internal mechanical fault. * * WHO WAS NOTIFIED: * Control Room, Maintenance Department. * * KNOWLEDGEABLE INDIVIDUALS: * Johnson, Smith, Lee, Wilson. * * REPEAT OR SIMILAR CONDITION: * No known previous incidents with the same pump. * * IMMEDIATE ACTIONS AND RECOMMENDED ACTIONS: * Maintenance to investigate and repair 8C Pump as necessary. Measures to be taken to verify the integrity of other comparable pumps. * Updated: WILLIAM BANKS 02.22.2020 14:35:45 * ------------------------------------------------------------ * 02/25/2020 09:02:51 JANE DOE (MAINTENANCE) * Investigation found that the pump's bearings were worn out, leading to the excessive vibration. Bearings have been replaced, and the pump is back | What was the identified cause of the excessive vibrations in the 8C cooling pump? | Investigation found that the pump's bearings were worn out, leading to the excessive vibration.
7 | 2019-05-12 | 30781253 | 80254930 | Anomaly on 16B cooling fan | S4CE -4CE3W5 | * **************Incident Description************** * Notification 000030781253 Details * *********************************************************** * 05/12/2019 10:35:40 INCIDENT REPORT (INCIDENT REPORT) * Report submitted by: Angela Green 123-654-9890 ENTITY\INCIDENT: * CONDITION DESCRIPTION/LOCATION (THE INAPPROPRIATE ACTION AND ITS NEGATIVE EFFECT/INCLUDE A DETAILED LOCATION DESCRIPTION): * The 16B cooling fan in S4 exhibit irregular rev output during inspections, despite normal temperature readings. Vibration sensor also detected intermittent irregularities. Initial suggestion is worn bearings, and no external damage is evident. * * ACTIVITIES, PROCESSES, PROCEDURES INVOLVED: * S4.OP.AB-CW-0003, S4.OP-SO.CW-0002 * * WHY DID CONDITION HAPPEN? * Unconfirmed, but initial findings suggest worn bearings or insufficient lubrication. * * CONSEQUENCES: * Increased risk of failure if not maintained properly might result in overheating. * * REQUIREMENTS IMPACTED: * Regular operation of the cooling system. * * ADVERSE PHYSICAL CONDITIONS: * Increased vibrations, irregular rev of 16B cooling fan motor. * * WHO WAS NOTIFIED: * Control Room, Maintenance Team * * KNOWLEDGEABLE INDIVIDUALS: * Davis, Williams, Thompson * * REPEAT OR SIMILAR CONDITION: * No * * IMMEDIATE ACTIONS AND RECOMMENDED ACTIONS: * Dismantle and inspect 16B cooling fan for worn components, especially bearings. Perform immediate maintenance if necessary. * 05/15/2019 14:22:12 Angela Green (INCIDENT) * Maintenance discovered worn bearings as initially suspected. The fan motor was replaced, and the system is back to normal operation. Future preventive measures have been suggested to adopt. | What immediate actions were recommended in response to the irregularities of the 16B cooling fan? | Dismantle and inspect 16B cooling fan for worn components, especially bearings. Perform immediate maintenance if necessary.
8 | 2018-10-09 | 30762435 | 80234372 | High vibration in 10B pump | S4CW -4CWE2 | * **************Incident Description************** * Notification 000030762435 Details * *********************************************************** * 10/09/2018 11:27:20 INCIDENT REPORT (INCIDENT REPORT) * Report submitted by: Lisa Miller ENTITY\INCIDENT: * * CONDITION DESCRIPTION/LOCATION (THE INAPPROPRIATE ACTION AND ITS NEGATIVE EFFECT/INCLUDE A DETAILED LOCATION DESCRIPTION): * At 2245 on 10/8/18, noticeable vibration was detected from 10B pump during standard monitoring. The vibration levels observed were higher than the usually recorded values for this pump. The pump status was monitored closely and a decision was made to shut down the pump to avoid potential damage. * * ACTIVITIES, PROCESSES, PROCEDURES INVOLVED: * S4.OP.AB-CW-0003, S4.OP-SO.CW-0002 * * WHY DID CONDITION HAPPEN? * Causes are not clear at the moment, but the pump might have been overloaded or has internal damage. * * CONSEQUENCES: * High vibration could cause pump failure or damage, and potentially lead to operational disruptions. * * REQUIREMENTS IMPACTED: * Continuous running of pump * * ADVERSE PHYSICAL CONDITION: * High vibrations from 10B pump * * WHO WAS NOTIFIED: * Control Room, Maintenance Department * * KNOWLEDGEABLE INDIVIDUALS: * Bell, Thompson, Rodriguez * * REPEAT OR SIMILAR CONDITION: * No * * IMMEDIATE AND RECOMMENDED ACTIONS: * Maintenance checks on 10B Pump. If necessary, arrange for pump repair or replacement. * * Updated: LISA MILLER 10/09/2018 23:29:18 * ------------------------------------------------------------ * 10/14/2018 19:32:47 JOHN DOE (INCIDENT) * Inspection results showed that an imbalance of the impeller was causing the vibrations. It wasn’t an overload condition, but due to wear and tear over time. The impeller was replaced and pump vibrations have returned to standard levels after the repair. | What was the identified cause of the high vibrations from pump 10B? | Inspection results showed that an imbalance of the impeller was causing the vibrations. It wasn’t an overload condition, but due to wear and tear over time.
9 | 2020-09-15 | 31023512 | 80259012 | 16B Pump motor cool down delayed | S4CW -4CWE7 | * **************Incident Description************** * Notification 000031023512 Details * *********************************************************** * 09/15/2020 14:32:00 INCIDENT REPORT (INCIDENT REPORT) * Report submitted by: Robert Green ENTITY\INCIDENT: * * CONDITION DESCRIPTION/LOCATION (THE INAPPROPRIATE ACTION AND ITS NEGATIVE EFFECT/INCLUDE A DETAILED LOCATION DESCRIPTION): After routine maintenance, it was observed during the 16B Pump restart that cooled down was delayed. According to our standard norms, it usually cools down within 1 hr. But it took more than 2 hours. It may be an indication that either the coolant is not functioning properly or there is some obstruction in the pump. * * ACTIVITIES, PROCESSES, PROCEDURES INVOLVED: * Conducted S4.OP-AB.CW-0002, S4.OP-SO.CW-0004 procedures. * * WHY DID CONDITION HAPPEN? * Current cause is unidentified. It could be due to coolant malfunction or obstruction in pump. * * CONSEQUENCES: * Potential damaging of motor due to overheating and loss of efficiency, * REQUIREMENTS IMPACTED: * Efficient operation of the pump motor and safety measures. * * ADVERSE PHYSICAL CONDITIONS: * Delay in cool down of 16B pump motor post operation. * * WHO WAS NOTIFIED: * Supervisor, Maintenance Team * * KNOWLEDGEABLE INDIVIDUALS: * Manager, Technician, Safety officer, * * REPEAT OR SIMILAR CONDITION: * No, first occurrence. * * IMMEDIATE ACTIONS AND RECOMMENDED ACTIONS: * Advised technical team for thorough inspection and run diagnostics for the coolant system for 16B Pump motor. * 09/15/2020 19:10:26 ROBERT GREEN (INCIDENT) * Upon further inspection, it was concluded that there was a minor obstruction in the coolant line. The issue has been rectified and the motor is operating within the regular temperature range. | What immediate and recommended actions were suggested after observing the delayed cool down of the 16B pump motor? | Advised technical team for thorough inspection and run diagnostics for the coolant system for 16B Pump motor.
10 | 2018-12-23 | 30923845 | 81206214 | 30B compressor failure | S4AC -4ACE7 | * **************Incident Description************** * Notification 000030923845 Details * *********************************************************** * 12/23/2018 16:57:00 INCIDENT REPORT (INCIDENT REPORT) * Report submitted by: Emily Thompson ENTITY\INCIDENT: * * CONDITION DESCRIPTION/LOCATION (THE INAPPROPRIATE ACTION AND ITS NEGATIVE EFFECT/INCLUDE A DETAILED LOCATION DESCRIPTION): * During regular inspection, the 30B compressor failed to start. Previous maintenance was performed under work order 81198750, but the compressor has again failed. There seems to be an underlying issue that needs investigation. The unreliable operation of 30B compressor is a great concern. * * ACTIVITIES, PROCESSES, PROCEDURES INVOLVED: * Regular inspection and condition monitoring via S4.OP-AB.AC-0001. * * WHY DID CONDITION HAPPEN? * Unknown, even though the compressor underwent recent maintenance. * * CONSEQUENCES: * Potential disruption in providing adequate conditioned air throughout the system. * * REQUIREMENTS IMPACTED: * Regular system operation and maintenance plan. * * ADVERSE PHYSICAL CONDITIONS: * Compressor failure to start. * * WHO WAS NOTIFIED: * Maintenance Supervisor, AC system Operators. * * KNOWLEDGEABLE INDIVIDUALS: * John Green, Harry Potter, Stephanie Meyer * * REPEAT OR SIMILAR CONDITION: * Yes, this issue was supposedly fixed under work order 81198750, but it has reoccurred. * * IMMEDIATE ACTIONS AND RECOMMENDED ACTIONS: * Immediate inspection and failure analysis of the 30B compressor. Evaluation of maintenance procedures and implementation of corrective actions. * 12/28/2018 08:36:56 JOHN GREEN (INCIDENT) * Upon further investigation, it was identified that the failure was due to an overpressurization of the suction lines. The cause was a malfunctioning relief valve which has now been replaced. The compressor has been tested and is now in operation. | What was the identified cause of the 30B compressor failure after further investigation? | The failure was due to an overpressurization of the suction lines. The cause was a malfunctioning relief valve which has now been replaced.
11 | 2020-10-30 | 30984321 | 90987234 | Motor 16C overheating | S5CW -5CWE7-BHDR | * **************Incident Description************** * Notification 000030984321 Details * *********************************************************** * 10/29/2020 14:12:46 INCIDENT REPORT (INCIDENT REPORT) * Report submitted by: Mark Johnson 432-765-0987 * ENTITY\INCIDENT: * * 1) CONDITION DESCRIPTION/LOCATION (THE INAPPROPRIATE ACTION AND ITS NEGATIVE EFFECT/INCLUDE A DETAILED LOCATION DESCRIPTION) * * During regular monitoring operation, the 16C motor was found to be overheating. A distinct smell of something burning was also reported. Although, an immediate shutdown was initiated, the cause of overheating still remains unknown. * * 2) ACTIVITIES, PROCESSES, PROCEDURES INVOLVED: * S5.OP.AB-BH-0004, S5.OP-SO.BH-0002 * * 3) WHY DID CONDITION HAPPEN? * Uncertain, but prior reports of similar instances suggest possible buildup of dust, corrosion or faulty wiring. * * 4) CONSEQUENCES: * Potential motor failure, interruption to services, increased maintenance costs * * 5) REQUIREMENTS IMPACTED: * Potential delay in resuming normal operation. * * 6) ADVERSE PHYSICAL CONDITIONS: * Individual reports of discomfort due to smell, temperature rise in the vicinity * * 7) WHO WAS NOTIFIED: * Operations Supervisor, Maintenance Team * * 8) KNOWLEDGEABLE INDIVIDUALS: * Peters, R. Sullivan, Adams * * 9) REPEAT OR SIMILAR CONDITION: * Yes, prior instances but under different circumstances * * 10) IMMEDIATE AND RECOMMENDED ACTIONS: * Immediate inspection and maintenance required. Further investigation to prevent future reoccurrence recommended. * 10/30/2020 17:32:22 ADAM SULLIVAN (INCIDENT) * Inspection reveals damaged wiring likely due to age and humidity. Replacement and comprehensive maintenance scheduled. | What was the immediate action taken when the overheating of the 16C motor was detected? | an immediate shutdown was initiated
12 | 2020-09-14 | 308972545 | 85560788 | 34B Generator unusual vibration | S4CG -4CWE5-GENB | * **************Incident Description************** * Notification 0000308972545 Details * *********************************************************** * 09/14/2020 15:01:00 INCIDENT REPORT (INCIDENT REPORT) * Report submitted by: Lily Green ENTITY\INCIDENT: * * CONDITION DESCRIPTION/LOCATION (THE INAPPROPRIATE ACTION AND ITS NEGATIVE EFFECT/INCLUDE A DETAILED LOCATION DESCRIPTION): * At 1450 on 9/14/20, the operator reported unusual vibration from 34B Generator. The Generator was immediately put offline as a precautionary measure. The vibration level returned to normal once it was put off and the shaking did not cause any physical damage. Inspection revealed no immediate cause. Previously repaired OrderNum 80256780. * * ACTIVITIES, PROCESSES, PROCEDURES INVOLVED: * S4.OP.AB-CG-0005, S4.OP-SO.CT-0005 * * WHY DID CONDITION HAPPEN?: * Unknown, possibly due to imbalance or loss of alignment. * * CONSEQUENCES: * If not detected early, could have led to significant damage to the generator. * * REQUIREMENTS IMPACTED: * Interruption of power generation. * * ADVERSE PHYSICAL CONDITIONS: * Unusual vibration on 34B generator, but no observable damage. * * WHO WAS NOTIFIED: * Control Room, Maintenance Department * * KNOWLEDGEABLE INDIVIDUALS: * Adams, Clark, Wilson * * REPEAT OR SIMILAR CONDITION: * Yes, previous similar condition with same generator. * * IMMEDIATE ACTIONS AND RECOMMENDED ACTIONS: * Maintenance team to inspect and determine cause of the vibration. * * Updated: LILY GREEN 09.14.2020 17:34:52 * ------------------------------------------------------------ * 10/02/2020 11:04:30 JOHN PARKER (MAINTENANCE) * After detailed inspection and analysis, found loosen bolts in the rotor assembly were the cause of the vibration. The bolts were tightened, and the generator was put back in operation. No further anomalies have been noticed. Recommend | What immediate action was taken when unusual vibration was reported from the 34B Generator? | The Generator was immediately put offline as a precautionary measure. The vibration level returned to normal once it was put off and the shaking did not cause any physical damage.
13 | 2018-12-10 | 30981253 | 90234567 | Smell of burning from 30B pump | S5CW -5CWE4-MTRD | * **************Incident Description************** * Notification 000030981253 Details * *********************************************************** * SUMMARY: ANALYZE CURRENT EVENTS IN LINE WITH * ****PS-AA-120 "ISSUE IDENTIFICATION AND SCREENING PROCESS"***** * * 1) Condition Description/Location (The inappropriate action and its negative effect/Include a detailed location description): * At 1542 on 12/10/18, a burning smell was detected coming from the 30B Pump. The pump was shut down swiftly from Unit 5 Control Room and the smell ceased. Staff team and Control Room inspections did not identify any obvious signs of damage but a pronounced smell of burning was present. Temperature readings were parallel to other pumps in operation and no external signs of damage were observed. S5.OP-AB.CW-0001 Pump Abnormality was initiated due to the shutdown of 30B Pump. * * 2) ACTIVITIES, PROCESSES, PROCEDURES INVOLVED: * S5.OP.AB-CW-0001, S5.OP-SO.CW-0001 * * 3) WHY DID CONDITION HAPPEN: * Uncertain, despite similar instances with pump motors * * 4) CONSEQUENCES: * No immediate issues identified, but potential internal damage could cause a future reduction in efficiency. * * 5) REQUIREMENTS IMPACTED: * Unavailable pump * * 6) ADVERSE PHYSICAL CONDITION: * Smell of burning from 30B Pump motor, potential internal issue * * 7) WHO WAS NOTIFIED: * Unit 5 Control Room, Staff team * * 8) KNOWLEDGEABLE INDIVIDUALS: * Thompson, Harris, Lopez * * 9) REPEAT OR SIMILAR CONDITION: * Potential, if not resolved * * 10) IMMEDIATE AND RECOMMENDED ACTIONS: * Maintenance to investigate and address the problem with 30B Pump Motor * * Updated: JACOB STONE 12.10.2018 17:22:45 | What was the reaction following the detection of a burning smell from the 30B Pump? | The pump was shut down swiftly from Unit 5 Control Room and the smell ceased. Staff team and Control Room inspections did not identify any obvious signs of damage but a pronounced smell of burning was present.
14 | 2018-04-16 | 40963217 | 90247832 | 16B AC pump vibration anomaly | S4AC -4ACE7 | * **************Incident Description************** * Notification 000040963217 Details * *********************************************************** * 04/16/2018 07:34:18 INCIDENT REPORT (INCIDENT REPORT) * Report submitted by: Daniel Astor ENTITY\INCIDENT: * * CONDITION DESCRIPTION/LOCATION (THE INAPPROPRIATE ACTION AND ITS NEGATIVE EFFECT/INCLUDE A DETAILED LOCATION DESCRIPTION): * During morning rounds, raised vibration levels were noted on the 16B AC Pump. This hasn't been observed previously on this pump. Pump parameters were within normal operating range. Believing it might be due to potential mechanical imbalance or bearing wear. * * ACTIVITIES, PROCESSES, PROCEDURES INVOLVED: * Regular operational rounds * * WHY DID CONDITION HAPPEN? * Potential Mechanical imbalance or Bearing Wear. * * CONSEQUENCES: * Potential pump failure, operational difficulties. * * REQUIREMENTS IMPACTED: * Continued safe and efficient operation. * * ADVERSE PHYSICAL CONDITIONS: * Increased vibration levels on 16B AC pump. * * WHO WAS NOTIFIED: * Plant Supervisor * * KNOWLEDGEABLE INDIVIDUALS: * Operational Staff, Maintenance Engineering team. * * REPEAT OR SIMILAR CONDITION: * No, this is first such occurrence. * * IMMEDIATE ACTIONS AND RECOMMENDED ACTIONS: * Initiated a work order for a detailed inspection and possible maintenance. * 04/16/2018 12:04:48 DANIEL ASTOR (INCIDENT) * A maintenance order has been placed for immediate inspection and necessary action based on the findings. | What are the potential consequences of increased vibration levels on the 16B AC pump? | Potential pump failure, operational difficulties.
15 | 2016-05-27 | 30785456 | 80233554 | Noticeable vibration from 30C motor | S4CW -4CWE7 | * **************Incident Description************** * Notification 000030785456 Details * *********************************************************** * 05/27/2016 13:34:10 INCIDENT REPORT (INCIDENT REPORT) * Report submitted by: David Francis ENTITY\INCIDENT: * CONDITION DESCRIPTION/LOCATION (THE INAPPROPRIATE ACTION AND ITS NEGATIVE EFFECT/INCLUDE A DETAILED LOCATION DESCRIPTION): * Today, while conducting a routine check, noticed a persistent vibration from 30C pump motor. The sudden presence of this vibration is unusual. The onsite team has isolated the pump for safety, and initial inspection suggests no external damage. * * ACTIVITIES, PROCESSES, PROCEDURES INVOLVED: * Routine inspections, safety protocols in case of unusual activities * * WHY DID CONDITION HAPPEN? * The reason behind the vibration is still uncertain. Some contributing factors could be mechanical issues, unbalanced load or debris. * * CONSEQUENCES: * Potential wear on the pump affecting its efficiency, possible damage to parts due to continuous vibration. * * REQUIREMENTS IMPACTED: * Regular active duty of the pump * * ADVERSE PHYSICAL CONDITIONS: * Significant vibration detected in the 30C motor * * WHO WAS NOTIFIED: * Operational Control team, Site manager * * KNOWLEDGEABLE INDIVIDUALS: * Maintenance team, Site manager, Process engineer * * REPEAT OR SIMILAR CONDITION: * No similar prior instance reported. * * IMMEDIATE ACTIONS AND RECOMMENDED ACTIONS: * Conduct comprehensive investigation to identify the exact cause, implement necessary remedial actions, consider a thorough motor overhaul if required. * 05/30/2016 15:34:31 DAVID FRANCIS (INCIDENT) * After detailed analysis, the Maintenance team found the motor to be imbalanced due to a worn-out bearing, which was replaced. The machine function has been restored to normal after the fix. | What was the detected issue with the 30C pump motor and what were the immediate recommendations? | Today, while conducting a routine check, noticed a persistent vibration from 30C pump motor. The sudden presence of this vibration is unusual. The onsite team has isolated the pump for safety, and initial inspection suggests no external damage. Conduct comprehensive investigation to identify the exact cause, implement necessary remedial actions, consider a thorough motor overhaul if required.
16 | 2019-04-30 | 30841190 | 90290561 | Unstable Flow rate 33B pump | S3CW -3CWE7 | * **************Incident Description************** * Notification 000030841190 Details * *********************************************************** * 04/30/2019 08:41:00 INCIDENT REPORT (INCIDENT) * Report submitted by: David Johnson ENTITY\INCIDENT: * * CONDITION DESCRIPTION/LOCATION (THE INAPPROPRIATE ACTION AND ITS NEGATIVE EFFECT/INCLUDE A DETAILED LOCATION DESCRIPTION): * At 0830, operator noted that 33B pump was demonstrating unstable flow rate. Flow rate was fluctuating between 1000 gpm and 1200 gpm intermittently. This was not consistent with normal pump operation. * * ACTIVITIES, PROCESSES, PROCEDURES INVOLVED: * Routine pump conditions monitoring. * * WHY DID CONDITION HAPPEN? * Unknown, potential mechanical or electrical control fluctuation. * * CONSEQUENCES: * Increase in maintenance needs, potential reduction in pump lifecycle, uncertainty in system control. * * REQUIREMENTS IMPACTED: * Expected pump flow rate control * * ADVERSE PHYSICAL CONDITIONS: * Unstable pump flow rate * * WHO WAS NOTIFIED: * Maintenance Supervisor/ INCIDENT TEAM * * KNOWLEDGEABLE INDIVIDUALS: * Maintenance team, and system engineer * * REPEAT OR SIMILAR CONDITION: * No, first time reported * * IMMEDIATE ACTIONS AND RECOMMENDED ACTIONS: * Maintenance team to inspect motor and control circuit. Engineering review on pump control. * 05/01/2019 14:11:56 DAVID JOHNSON (INCIDENT) * Follow up investigation identified an issue with the voltage regulator on the pump control circuit. Replacement parts ordered and will be replaced next maintenance cycle. | What was the identified issue causing the unstable flow rate in the 33B pump? | Follow up investigation identified an issue with the voltage regulator on the pump control circuit.
17 | 2018-04-14 | 30789420 | 80256789 | High voltage reading on 23A Pump | S4TR -4GRE6 | * **************Incident Description************** * Notification 000030789420 Details * *********************************************************** * 04/14/2018 09:32:21 INCIDENT REPORT (INCIDENT REPORT) * Report submitted by: Tom Anderson * ENTITY\INCIDENT: * * 1) CONDITION DESCRIPTION/LOCATION (THE INAPPROPRIATE ACTION AND ITS NEGATIVE EFFECT/INCLUDE A DETAILED LOCATION DESCRIPTION): * During a routine inspection on 14/04/18, the 23A Pump registered high voltage readings beyond its normal range. Immediate shutdown was initiated from the Unit 4 Control Room as a precautionary measure. * * 2) ACTIVITIES, PROCESSES, PROCEDURES INVOLVED: * S4.OP.AB-TR-0001, S4.OP-SO.TR-0001 * * 3) WHY DID CONDITION HAPPEN: * The exact cause is still unknown pending inspection. Previous incidences allude to possible issues with the voltage regulator. * * 4) CONSEQUENCES: * Potential pump failure or damage. Possible efficiency loss when the unit is back online. * * 5) REQUIREMENTS IMPACTED: * Suspension of normal pump operation * * 6) ADVERSE PHYSICAL CONDITION: * High voltage readings from 23A Pump, likely internal complications. * * 7) WHO WAS NOTIFIED: * Control Room, Electrical Department * * 8) KNOWLEDGEABLE INDIVIDUALS: * Williams, Thompson, Rogers * * 9) REPEAT OR SIMILAR CONDITION: * No previous instances of this exact condition. However, similar reports of high voltage on other units. * * 10) IMMEDIATE AND RECOMMENDED ACTIONS: * Further diagnostic checks to be carried out by Electrical Department on 23A Pump motor * * Updated: TOM ANDERSON 04.14.2018 11:02:45 * ------------------------------------------------------------ * 04/29/2018 09:02:01 JANE DOE (NUSER) * Comprehensive inspection revealed voltage regulator faults as the cause of the high voltage readings. Repairs have been carried out and | What was the identified issue causing high voltage readings in the 23A Pump? | Comprehensive inspection revealed voltage regulator faults as the cause of the high voltage readings.
18 | 2016-11-15 | 30798362 | 80233315 | Coolant leak from 16B motor pump | S4CW -4CWE7 | * **************Incident Description************** * Notification 000030798362 Details * *********************************************************** * 11/15/2016 15:35:27 INCIDENT REPORT (INCIDENT REPORT) * Report submitted by: Daniel White ENTITY\INCIDENT: * * CONDITION DESCRIPTION/LOCATION (THE INAPPROPRIATE ACTION AND ITS NEGATIVE EFFECT/INCLUDE A DETAILED LOCATION DESCRIPTION): * During the morning shift, maintenance team noticed a small coolant leak from 16B Pump motor. The leak appeared to be originating from the seal that prevents coolant from leaking out from the cooling section. The pump was promptly shut down to prevent further leakage and the affected area was cleaned. * * ACTIVITIES, PROCESSES, PROCEDURES INVOLVED: * Routine inspection * * WHY DID CONDITION HAPPEN? * Seal failure, possibly due to ageing or manufacturing defect. * * CONSEQUENCES: * Potential overheating of motor pump if coolant loss is substantial, leading to equipment damage and inefficiency. * * REQUIREMENTS IMPACTED: * Pump operation and efficiency * * ADVERSE PHYSICAL CONDITIONS: * Coolant leak from 16B Pump motor * * WHO WAS NOTIFIED: * Shift Supervisor, Maintenance Team * * KNOWLEDGEABLE INDIVIDUALS: * Daniel White, Maintenance Team, Shift Supervisor * * REPEAT OR SIMILAR CONDITION: * No, this is the first occurrence * * IMMEDIATE ACTIONS AND RECOMMENDED ACTIONS: * Planned maintenance to replace leaking seal in 16B motor pump and check for potential damage. Bring the pump back online after repair and testing. * 11/16/2016 12:14:47 DANIEL WHITE (INCIDENT) * Seal replacement and subsequent integrity checks were carried out successfully. 16B pump motor is back in operation with normal parameters. An inspection schedule has been set to monitor for any future leaks. | What was the cause of the coolant leak from the 16B Pump motor? | Seal failure, possibly due to ageing or manufacturing defect.
19 | 2019-11-10 | 31046086 | 80252714 | Abnormal vibration in 18A pump post calibration | S4CW -4CWE7 | * **************Incident Description************** * Notification 000031046086 Details * *********************************************************** * 11/10/2019 10:15:28 INCIDENT REPORT (INCIDENT REPORT) * Report submitted by: Daniel Green ENTITY\INCIDENT: * * CONDITION DESCRIPTION/LOCATION (THE INAPPROPRIATE ACTION AND ITS NEGATIVE EFFECT/INCLUDE A DETAILED LOCATION DESCRIPTION): * Post calibration check on 18A pump showed abnormal vibration at standard RPM. This is an uncharacteristic behaviour since the pump was just serviced under work order 80252822. The high-frequency vibration indicates a possible misalignment or imbalance caused during the maintenance. There was no temperature or pressure anomaly detected. * * ACTIVITIES, PROCESSES, PROCEDURES INVOLVED: * Regular post-maintenance calibration check and vibration analysis * * WHY DID CONDITION HAPPEN? * Possible procedural error or overlooked imbalance during the last maintenance service. * * CONSEQUENCES: * Increased wear and tear, reduced efficiency, and potential equipment failure if the vibration issue is not addressed promptly. * * REQUIREMENTS IMPACTED: * Equipment expected to be in operational state post routine check-up * * ADVERSE PHYSICAL CONDITIONS: * High vibration levels at the 18A pump with no known cause * * WHO WAS NOTIFIED: * Supervisor, Maintenance Team * * KNOWLEDGEABLE INDIVIDUALS: * Maintenance Team * * REPEAT OR SIMILAR CONDITION: * No, this is a new issue * * IMMEDIATE ACTIONS AND RECOMMENDED ACTIONS: * Prompt reevaluation of maintenance work performed on the 18A pump. Necessary recalibration or possible overhaul depending on the discovered cause. * 11/12/2019 09:12:15 DANIEL GREEN (INCIDENT) * The maintenance team performed a comprehensive evaluation and confirmed an imbalance in the pump rotor. Recalibration was completed and the pump is back in standard operational state. Recommend reinforcing quality checks post maintenance to avoid similar incidents moving forward. | What was the cause of the high vibration levels at the 18A pump? | The high-frequency vibration indicates a possible misalignment or imbalance caused during the maintenance.
20 | 2022-03-22 | 31078955 | 80570023 | Vibration in 18B Pump Motor | S4CW -4CWE7 | * **************Incident Description************** * Notification 000031078955 Details * *********************************************************** * 03/22/2022 07:30:00 INCIDENT REPORT (INCIDENT REPORT) * Report submitted by: Roger Lloyd ENTITY\INCIDENT: * * CONDITION DESCRIPTION/LOCATION (THE INAPPROPRIATE ACTION AND ITS NEGATIVE EFFECT/INCLUDE A DETAILED LOCATION DESCRIPTION) * While conducting usual morning rounds, vibration was observed in the 18B Pump Motor. * Based on operations parameters and indications, operating under normal intake pressure, with a * temperature difference within normal limits. The unusual vibration was isolated to the motor. * * ACTIVITIES, PROCESSES, PROCEDURES INVOLVED: * Routine daily inspection S4.OP-AB.CW-0002. * * WHY DID CONDITION HAPPEN? * Not yet determined, with possibilities ranging from internal misalignment to potential bearing failure. * * CONSEQUENCES: * Damage to the motor, potential failure of the pump leading to system shutdown or inadequate pumping. * * REQUIREMENTS IMPACTED: * Pump 18B Normal operation * * ADVERSE PHYSICAL CONDITION: * Unusual vibration in motor. * * WHO WAS NOTIFIED: * Shift Supervisor, Maintenance Team * * KNOWLEDGEABLE INDIVIDUALS: * Shift Supervisor, Operations Team, Maintenance Professionals * * REPEAT OR SIMILAR CONDITION: * Not Known. * * IMMEDIATE ACTIONS AND RECOMMENDED ACTIONS: * Initiate work order under S4.OP-AB.CW-0002. Maintenance team to inspect and identify root cause. Pump to be monitored continuously until issue resolved. * 03/22/2022 14:59:23 ROGER LLOYD (INCIDENT) * Work order initiated. Maintenance team commenced the initial inspection and reported no immediate risk. Long term assessment and potential overhaul suggested. Further updates to follow. | What immediate actions were recommended after observing a vibration in the pump motor? | Initiate work order under S4.OP-AB.CW-0002. Maintenance team to inspect and identify root cause. Pump to be monitored continuously until issue resolved.
21 | 2019-05-30 | 30952040 | 90478935 | 32B Motor run fail post installation | S4DW -4DWE5 | * **************Incident Description************** * Notification 000030952040 Details * *********************************************************** * 05/30/2019 14:15:45 INCIDENT REPORT (INCIDENT REPORT) * Report submitted by: Robert Evans 987-654-3210 ENTITY\INCIDENT: * CONDITION DESCRIPTION/LOCATION (THE INAPPROPRIATE ACTION AND ITS NEGATIVE EFFECT/INCLUDE A DETAILED LOCATION DESCRIPTION): * Post installation, the 32B Motor failed to run at 1535 on 5/30/19. The motor was immediately cut-off from the switch room. The emergency crew was called in for inspection. No fire or complications were noticed, but the high-pitched noise was heard. S4.OP-AB.DW-0005 for Drilling System was initiated due to the immediate turn-off of the 35B Motor. * * ACTIVITIES, PROCESSES, PROCEDURES INVOLVED: * S4.OP.AB.DW-0005, S4.OP-SO.DW-0003 * * WHY DID CONDITION HAPPEN? * At this point, the exact reason is still unknown, but it's suspected to be a mechanical fault. * * CONSEQUENCES: * Possible delay in drilling activity and potential for system damage. * * REQUIREMENTS IMPACTED: * Operational drill motor * * ADVERSE PHYSICAL CONDITIONS: * High-pitched noise from 32B Motor, possible internal complications * * WHO WAS NOTIFIED: * Operations Room, Emergency Duty Manager * * KNOWLEDGEABLE INDIVIDUALS: * Peterson, Jackson, Anderson * * REPEAT OR SIMILAR CONDITION: * No, this is the first report of such an event. * * IMMEDIATE ACTIONS AND RECOMMENDED ACTIONS: * Engineering and maintenance to investigate the 32B Motor * ***************************************** * Updated: ROBERT EVANS 05.30.2019 16:00:05 * ------------------------------------------------------------ * 06/02/2019 09:35:51 PETERSON (NUSER) * The investigation found a manufacturing defect within the rotor. | What was the immediate response after the 32B Motor failed? | The motor was immediately cut-off from the switch room. The emergency crew was called in for inspection. No fire or complications were noticed, but the high-pitched noise was heard. S4.OP-AB.DW-0005 for Drilling System was initiated due to the immediate turn-off of the 35B Motor.
22 | 2022-10-20 | 40985217 | 90561254 | 25B Blower high vibration post servicing | S4CW -4CWE2 | * **************Incident Description************** * Notification 000040985217 Details * *********************************************************** * 10/20/2022 14:15:47 INCIDENT REPORT (INCIDENT REPORT) * Report submitted by: Ronald Green ENTITY\INCIDENT: * * CONDITION DESCRIPTION/LOCATION (THE INAPPROPRIATE ACTION AND ITS NEGATIVE EFFECT/INCLUDE A DETAILED LOCATION DESCRIPTION): * In 01/2020, notification 40831550 identified that Blower 24A returned from maintenance with high vibration. The issue was addressed under work order 90521318 and a procedure revision was issued in Feb 2020 for S4.OP-SO.CW-0001 to update the guidance for high vibration. Limits were adjusted based on data from work order 90527802 which was used to replace the 24A blower motor. Since then, 25B blower was serviced in Aug 2021 under work order 90549850 and returned to service with high vibration. It appears that changes to the blower components may be affecting the normal vibrational behaviour of the motors. There is a need to clearly identify the changes made to the blowers and motors so that proper prescriptive measures can be developed and procedures updated. * * ACTIVITIES, PROCESSES, PROCEDURES INVOLVED: * Observation of motor vibrational differences and existing procedure guidance in S4.OP-SO.CW-0001. * * WHY DID CONDITION HAPPEN? * Unknown why vibrational anomalies were not identified prior to changes in the field. * * CONSEQUENCES: * Inadequate guidance in the CW procedures for vibration limits. * * REQUIREMENTS IMPACTED: * Ensuring equipment reliability by maintaining proper vibrational margins for motors in operation. * * ADVERSE PHYSICAL CONDITIONS: * High vibration level in Blower 25B * * WHO WAS NOTIFIED: * Supervisor, Maintenance Team * * KNOWLEDGEABLE INDIVIDUALS: * Maintenance Team, Supervisors, Engineers * * REPEAT OR SIMILAR CONDITION: * Yes, notification 40831550 which | What is the issue with the blower 24A and 25B? | Blower 24A returned from maintenance with high vibration. The issue was addressed under work order 90521318 and a procedure revision was issued in Feb 2020 for S4.OP-SO.CW-0001 to update the guidance for high vibration. 25B blower was serviced in Aug 2021 under work order 90549850 and returned to service with high vibration. It appears that changes to the blower components may be affecting the normal vibrational behaviour of the motors.
23 | 2018-02-28 | 30878952 | 90212345 | Sudden vibration on 18A Pump | S4CW -4CWE2 | * **************Incident Description************** * Notification 000030878952 Details * *********************************************************** * 02/28/2018 13:40:00 INCIDENT REPORT (INCIDENT REPORT) * Report submitted by: Lucas Grey ENTITY\INCIDENT: * * CONDITION/DESCRIPTION/LOCATION (THE INAPPROPRIATE ACTION AND ITS NEGATIVE EFFECT/INCLUDE DETAILED LOCATION DESCRIPTION): * During a quality check by night shift, unexpected vibration from 18A Pump was detected. Pump was shut down immediately, preventing any further reaction. No sign of apparent issues found on a quick inspection. The pump's condition is monitored under procedure S4.OP-P.CW-0001. * * ACTIVITIES, PROCESSES, PROCEDURES INVOLVED: * Monitoring of pump conditions, S4.OP-P.CW-0001, S4.OP.SO.CW-0321 * * WHY DID CONDITION HAPPEN? * Cause undetermined. Possible internal damage or misalignment of internal components. * * CONSEQUENCES: * Reduced pump function, potential for catastrophic failure if not addressed promptly. * * REQUIREMENTS IMPACTED: * Operational efficiency, safety measures. * * ADVERSE PHYSICAL CONDITIONS: * Excessive vibration from 18A Pump. * * WHO WAS NOTIFIED: * Maintenance Lead, Operations Supervisor. * * KNOWLEDGEABLE INDIVIDUALS: * Maintenance Lead, Operations Supervisor, and Quality Analysts. * * REPEAT OR SIMILAR CONDITION: * No, this is the first recorded incident involving 18A Pump. * * IMMEDIATE ACTIONS AND RECOMMENDED ACTIONS: * Shut down 18A Pump for immediate inspection. If necessary, schedule for maintenance and replace damaged parts as required. Procedures in S4.OP-P.CW-0001 should be followed. * 03/01/2018 09:07:15 LUCAS GREY (INCIDENT) * A thorough inspection and maintenance is scheduled for 18A Pump to address the matter and ensure system function. * 03/02/2018 10:55:21 JANE DOE (INCIDENT) * Post-ins | What was the initial problem observed during the night shift quality check? | During a quality check by night shift, unexpected vibration from 18A Pump was detected. Pump was shut down immediately, preventing any further reaction. No sign of apparent issues found on a quick inspection. The pump's condition is monitored under procedure S4.OP-P.CW-0001.
24 | 2020-04-10 | 40960374 | 80293810 | ALARM TRIPPED FOR 24B AIR COMPRESSOR | S4AC -4ACE2-COMP | * **************Incident Description************** * Notification 000040960374 Details * *********************************************************** * 04/10/2020 15:15:41 INCIDENT REPORT (INCIDENT REPORT) * Report submitted by: Elizabeth Jones 654-321-0987 ENTITY\INCIDENT: * * CONDITION DESCRIPTION/LOCATION (THE INAPPROPRIATE ACTION AND ITS NEGATIVE EFFECT/INCLUDE A DETAILED LOCATION DESCRIPTION): * At 1413 hours, the 24B compressor alarm tripped, indicating an abnormal operation. * The air pressure dropped to 80 psi from the standard 120 psi. On-site inspection revealed, * the 24B compressor was stopped. No visible signs of damage and the compressor * was at the normal temperature. * * ACTIVITIES, PROCESSES, PROCEDURES INVOLVED: * S4.OP-AB.AC-0002, S4.OP-SO.AC-0002 * * WHY DID CONDITION HAPPEN? * The root cause is yet unknown but could be due to sensor error or a sudden drop * in pressure due to mechanical failure. * * CONSEQUENCES: * The drop-in air pressure could lead to inadequate operations at the factory, * affecting machine functioning leading to potential production downtime. * * REQUIREMENTS IMPACTED: * Air source for factory machines * * ADVERSE PHYSICAL CONDITIONS: * Decreased air pressure * * WHO WAS NOTIFIED: * Supervisor, Factory Manager, Maintenance Team * * KNOWLEDGEABLE INDIVIDUALS: * Richardson, Kelly, Booth * * REPEAT OR SIMILAR CONDITION: * No * * IMMEDIATE ACTIONS AND RECOMMENDED ACTIONS: * The 24B compressor was restarted, and a detailed inspection is scheduled * to determine the root cause of the alarm trip. * * 04/11/2020 09:07:23 Robert Littlewood (MAINTENANCE) * The detailed inspection revealed that the pressure sensor malfunctioned, * causing the compressor to trip. The sensor has been replaced, and the compressor * is now working within the set parameters. | What was the immediate action taken after the 24B compressor alarm tripped? | The 24B compressor was restarted, and a detailed inspection is scheduled to determine the root cause of the alarm trip.
25 | 2020-12-15 | 30982745 | 90273501 | 18B Pump failed start attempt | S3CW -3CWE8 | * **************Incident Description************** * Notification 000030982745 Details * *********************************************************** * 12/15/2020 14:56:02 INCIDENT REPORT (INCIDENT REPORT) * Report submitted by: Jack Johnson ENTITY\INCIDENT: * * CONDITION DESCRIPTION/LOCATION (THE INAPPROPRIATE ACTION AND ITS NEGATIVE EFFECT/INCLUDE A DETAILED LOCATION DESCRIPTION): * Following the preventive maintenance conducted on 18B Pump Motor, the operator attempted to start 18B and it failed. Operator contacted the Maintenance Team. A field visit by the technician showed that the motor was not responding. In such scenarios, S3.OP-AB.CW-0001 did not provide any clear guidance for immediate resolution. * * ACTIVITIES, PROCESSES, PROCEDURES INVOLVED: * S3.OP-AB.CW-0001, S3.OP-SO.CW-0001 * * WHY DID CONDITION HAPPEN? * The cause is yet to be determined. * * CONSEQUENCES: * Unavailability of 18B pump and the impact on operational efficiency. * * REQUIREMENTS IMPACTED: * Pump start-high readiness condition. * * ADVERSE PHYSICAL CONDITIONS: * Failed pump * * WHO WAS NOTIFIED: * Maintenance Cluster, Technical Team * * KNOWLEDGEABLE INDIVIDUALS: * Johnson, Davis, Evans * * REPEAT OR SIMILAR CONDITION: * No, this is the first incident of failed start attempt after maintenance inspection. * * IMMEDIATE ACTIONS AND RECOMMENDED ACTIONS: * A detailed investigation should be conducted to ascertain the cause of the failure. Action should be taken to restart the pump. If necessary, replace faulty parts with the help of the Technical Team. * 12/20/2020 11:29:14 Jack Johnson (INCIDENT) * After the inspection, it was found that the starter controller was faulty. It is replaced now and the pump is expected to start properly now. Re-evaluation of preventive maintenance protocols may be required. | What immediate and recommended actions were suggested after the pump failure incident? | A detailed investigation should be conducted to ascertain the cause of the failure. Action should be taken to restart the pump. If necessary, replace faulty parts with the help of the Technical Team.
26 | 2018-12-15 | 30952736 | 80236841 | 8B Condenser abnormal vibration | S3CW -3CWE4 | * **************Incident Description************** * Notification 000030952736 Details * *********************************************************** * 12/15/2018 13:32:20 INCIDENT REPORT (INCIDENT REPORT) * Report submitted by: David Smith ENTITY\INCIDENT: * * CONDITION DESCRIPTION/LOCATION (THE INAPPROPRIATE ACTION AND ITS NEGATIVE EFFECT/INCLUDE A DETAILED LOCATION DESCRIPTION): * During a scheduled inspection, 8B Condenser has been found to have an abnormal vibration. The vibration amplitude and frequency have significantly increased from the baseline levels. This increased vibration could be an indication of a potential mechanical failure. * * ACTIVITIES, PROCEDURES, PROCESSES INVOLVED: * Scheduled inspection and vibration analysis. * * WHY DID CONDITION HAPPEN? * The exact reason is unknown at this time. It might be due to wear or mechanical misalignment. * * CONSEQUENCES: * Possible machine damage, reduced efficiency and could result in an unscheduled outage if not addressed timely. * * REQUIREMENTS IMPACTED: * Equipment reliability and operation. * * ADVERSE PHYSICAL CONDITIONS: * Abnormal vibrations from the 8B Condenser. * * WHO WAS NOTIFIED: * Operations Manager, Maintenance supervisor * * KNOWLEDGEABLE INDIVIDUALS: * David Smith, Tom Johnson, Gary Wilson * * REPEAT OR SIMILAR CONDITION: * No * * IMMEDIATE ACTIONS AND RECOMMENDED ACTIONS: * An immediate investigation is initiated to pinpoint the root cause of vibrations. Recommended initiating a work order for technical inspection and performing an in-depth vibration analysis. * 12/17/2018 09:43:51 LIZA MILLER (INCIDENT) * An expert visit to inspect the unit has been arranged. The machine will be kept under continuous observation till the issue gets resolved. Anticipate resolution without any significant operational disruption. | What actions were recommended following the discovery of abnormal vibrations in the 8B Condenser? | An immediate investigation is initiated to pinpoint the root cause of vibrations. Recommended initiating a work order for technical inspection and performing an in-depth vibration analysis.
27 | 2019-02-12 | 30789109 | 80198002 | Fuse blown at Pump 40C control panel | S4CW -4CWE8 | * **************Incident Description************** * Notification 000030789109 Details * *********************************************************** * 02/12/2019 10:35:00 INCIDENT REPORT (INCIDENT REPORT) * Report submitted by: Adam Baker ENTITY\INCIDENT: * * CONDITION DESCRIPTION/LOCATION (THE INAPPROPRIATE ACTION AND ITS NEGATIVE EFFECT/INCLUDE A DETAILED LOCATION DESCRIPTION): * On 2019-02-12 at 1020, the operator detected a power fault at the 40C Pump control panel. After visual inspection, the control panel indicated a blown fuse. Failure of control panel light for pump 40C was observed. * * ACTIVITIES, PROCESSES, PROCEDURES INVOLVED: * Power inspection of Control Panel S2.OP-AB.CP-0002 * * WHY DID CONDITION HAPPEN? * Unknown, initial suspicion of short-circuit or power surge. * * CONSEQUENCES: * Potential pump failure due to blown fuse, disruption in operations. * * REQUIREMENTS IMPACTED: * Normal operation * * ADVERSE PHYSICAL CONDITIONS: * Blown fuse, dark power light. * * WHO WAS NOTIFIED: * Maintenance Team, Supervisor * * KNOWLEDGEABLE INDIVIDUALS: * Tom Daniels, Mike Kelly, Steve Jackson * * REPEAT OR SIMILAR CONDITION: * No * * IMMEDIATE ACTIONS AND RECOMMENDED ACTIONS: * Change fuse, inspect for potential shorting, check voltage stability. * * 02/12/2019 14:02:24 PETER DAVIS (INCIDENT) * Fuse replaced, normal operation resumed. Electrical checking revealed no shorting. Further monitoring and inspection needed to ensure reliability of control panel. | Who was notified about the power fault at the control panel? | Maintenance Team, Supervisor
28 | 2021-04-30 | 30752894 | 80245698 | 11B motor sudden shutdown | S4CW -4CWE5 | * **************Incident Description************** * Notification 000030752894 Details * *********************************************************** * 04/30/2021 09:22:30 INCIDENT REPORT (INCIDENT REPORT) * Report submitted by: Sarah Thompson ENTITY\INCIDENT: * * CONDITION DESCRIPTION/LOCATION (THE INAPPROPRIATE ACTION AND ITS NEGATIVE EFFECT/INCLUDE A DETAILED LOCATION DESCRIPTION): * At 0830 on 4/30/21, the 11B Motor has shut down without any prior warning. The control room immediately initiated emergency protocols. An initial investigation showed no external problems in the electrical components or in the motor hardware itself. An odor of burnt metal was present. * * ACTIVITIES, PROCESSES, PROCEDURES INVOLVED: * S4.OP.AB-MT-0009, S4.OP-SO.MT-0002. * * WHY DID CONDITION HAPPEN? * The exact cause is unknown at the time of incident, previous reportings have shown internal mechanical failures in similar incidents. * * CONSEQUENCES: * Potential unsafe conditions, prolonged operational downtime and expensive repair or replacement. * * REQUIREMENTS IMPACTED: * The unexpected shutdown of the 11B motor impacts normal operation. * * ADVERSE PHYSICAL CONDITIONS: * Unexpected shutdown of the 11B motor. * * WHO WAS NOTIFIED: * Control Room, Maintenance Team * * KNOWLEDGEABLE INDIVIDUALS: * Operations Supervisor, Thompkins, Rodriguez, Johnson * * REPEAT OR SIMILAR CONDITION: * No, first occurrence. * * IMMEDIATE ACTIONS AND RECOMMENDED ACTIONS: * Initiation of S4.OP.AB-MT-0009 for dealing with motor abnormality, comprehensive inspection of the 11B Motor for identification of the issue for appropriate fixes. * 04/30/2021 16:12:32 SARAH THOMPSON (INCIDENT) * The inspection revealed the issue to be internal, the main rotor bearing had failed. Replacement parts have been ordered, the motor will be operational once the parts are installed and tested. | What immediate actions were taken after the incident with the 11B Motor? | Initiation of S4.OP.AB-MT-0009 for dealing with motor abnormality, comprehensive inspection of the 11B Motor for identification of the issue for appropriate fixes.
29 | 2020-05-27 | 30914972 | 90256432 | High vibration observed in 18B Pump | S4CW -4CWE5 | * **************Incident Description************** * Notification 000030914972 Details * *********************************************************** * 05/27/2020 14:45:10 INCIDENT REPORT (INCIDENT REPORT) * Report submitted by: David Robinson, 987-654-3210 ENTITY\INCIDENT: * * CONDITION DESCRIPTION/LOCATION (THE INAPPROPRIATE ACTION AND ITS NEGATIVE EFFECT/INCLUDE A DETAILED LOCATION DESCRIPTION): * During periodic maintenance activity, it was observed that 18B Pump was experiencing high vibration levels. The vibration levels were consistently higher than other similar units. An immediate inspection was called for to ascertain the condition and persistence of the high vibration levels. * * ACTIVITIES, PROCESSES, PROCEDURES INVOLVED: * Routine maintenance, vibration monitoring * * WHY DID CONDITION HAPPEN? * Unknown, it could be due to factors such as misalignment, wear and tear, imbalance, or other mechanical issues. * * CONSEQUENCES: * Reduced operational life of the pump, potential for catastrophic failure if left unattended. * * REQUIREMENTS IMPACTED: * Regular pump operations due to the immediate shutdown for inspection. * * ADVERSE PHYSICAL CONDITIONS: * High vibration levels at the 18B Pump. * * WHO WAS NOTIFIED: * Maintenance Supervisor, Safety Team * * KNOWLEDGEABLE INDIVIDUALS: * Maintenance Team, Safety Team * * REPEAT OR SIMILAR CONDITION: * No, first instance observed in this unit. * * IMMEDIATE ACTIONS AND RECOMMENDED ACTIONS: * Immediate inspection called to ascertain the health and condition of the 18B Pump. If the high vibration levels persist, procedures for repair or replacement should be initiated. * 05/27/2020 16:50:45 DAVID ROBINSON (INCIDENT) * The inspection revealed that the pump was misaligned which may have caused the high vibration levels. The pump has been realigned and vibrations are now within acceptable limits. Continuous monitoring has been recommended for the next 72 hours. | What immediate and recommended actions were taken following the high vibration levels of 18B Pump? | Immediate inspection called to ascertain the health and condition of the 18B Pump. If the high vibration levels persist, procedures for repair or replacement should be initiated. The inspection revealed that the pump was misaligned which may have caused the high vibration levels. The pump has been realigned and vibrations are now within acceptable limits. Continuous monitoring has been recommended for the next 72 hours.
30 | 2016-12-10 | 30974032 | 80261009 | Leaking from 16B coolant pump | S4CW -4CWE5 | * **************Incident Description************** * Notification 000030974032 Details * *********************************************************** * 12/10/2016 10:34:24 INCIDENT REPORT (INCIDENT REPORT) * Report submitted by: William Foster ENTITY\INCIDENT: * * CONDITION DESCRIPTION/LOCATION (THE INAPPROPRIATE ACTION AND ITS NEGATIVE EFFECT/INCLUDE A DETAILED LOCATION DESCRIPTION): * At 0930 on 12/10/16 inside the Main Control Room, the operator reported noticeable leak coming from the 16B Coolant Pump. The leak was not severe but prompted urgent attention. The current temperature of the coolant was about the same as other pumps in operation. The leak was quickly contained with an emergency shutdown of 16B Pump. Assistance from the local Fire Department and Operations Management did not reveal any significant fire threat but the smell of the coolant was present. * * ACTIVITIES, PROCESSES, PROCEDURES INVOLVED: * S4.OP.AB-CW-0010, S4.OP-SO.CW-0011 * * WHY DID CONDITION HAPPEN? * The initial reason is unclear, but possible wear and tear or mechanical failure of pump components may have contributed to this event. * * CONSEQUENCES: * Further inspection required to determine the extent of the damage. Potential loss of efficiency when the unit is restarted. * * REQUIREMENTS IMPACTED: * Operational requirements of 16B Pump. * * ADVERSE PHYSICAL CONDITIONS: * Leak from 16B Coolant Pump, which could mean potential internal damage. * * WHO WAS NOTIFIED: * Main Control Room personnel, Fire Department, Plant Manager * * KNOWLEDGEABLE INDIVIDUALS: * Peterson, Clark, Hamilton * * REPEAT OR SIMILAR CONDITION: * Not known at present. * * IMMEDIATE ACTIONS AND RECOMMENDED ACTIONS: * An immediate inspection of 16B Coolant Pump by the Maintenance Team and further investigation to pinpoint the cause of the leak. * 12/10/2016 14:19:15 WILLIAM FOSTER (INCIDENT) * Maintenance has inspected | What immediate and recommended actions were taken following the incident with the 16B Coolant Pump? | An immediate inspection of 16B Coolant Pump by the Maintenance Team and further investigation to pinpoint the cause of the leak.
31 | 2020-02-14 | 30985215 | 91029148 | Vibrations from 34B Pump motor | S3CW -3CWE7 | * **************Incident Description************** * Notification 000030985215 Details * *********************************************************** * 02/14/2020 07:32:18 INCIDENT REPORT (INCIDENT REPORT) * Report submitted by: Robert Green ENTITY\INCIDENT: * CONDITION DESCRIPTION/LOCATION (THE INAPPROPRIATE ACTION AND ITS NEGATIVE EFFECT/INCLUDE A DETAILED LOCATION DESCRIPTION): * During the morning shift, a distinct vibration was observed from the 34B Pump motor. The pump motor was immediately shut down from the Control Room. Mechanics on duty felt the vibration and noted it while the motor was running. A temporary halt in operation was implemented, and a detailed inspection was carried out. No visible damage was found on the exterior of the unit, but the unusual vibration signals potential issues. * * ACTIVITIES, PROCESSES, PROCEDURES INVOLVED: * Regular operations, S3.OP.AB.CW-0002 * * WHY DID CONDITION HAPPEN? * The cause is uncertain at this time, further investigation is required to identify the source of vibrations. * * CONSEQUENCES: * If not properly addressed, persistent vibrations could lead to motor failure. * * REQUIREMENTS IMPACTED: * Continuous operation of pump 34B * * ADVERSE PHYSICAL CONDITIONS: * Unusual vibrations from 34B Pump motor, that might indicate internal problems * * WHO WAS NOTIFIED: * Control Room, Maintenance Department * * KNOWLEDGEABLE INDIVIDUALS: * Mechanics Team and Control Room Operators * * REPEAT OR SIMILAR CONDITION: * No, this is the first incident of this nature on pump 34B. * * IMMEDIATE ACTIONS AND RECOMMENDED ACTIONS: * Maintenance Department to conduct a detailed inspection of 34B Pump Motor and ascertain the cause of vibrations. * 02/19/2020 10:45:57 ROBERT GREEN (INCIDENT) * An in-depth mechanical inspection revealed the issue was due to misalignment of the motor's rotor. The rotor has been realigned and the motor is now back in operation with no further vibrations. | What was the issue found in the detailed mechanical inspection of pump 34B, and how was it addressed? | An in-depth mechanical inspection revealed the issue was due to misalignment of the motor's rotor. The rotor has been realigned and the motor is now back in operation with no further vibrations.
32 | 2019-04-25 | 30910432 | 80248902 | Pump C42 Voltage Instability | S4CW -4CWE4-QRTS | * **************Incident Description************** * Notification 000030910432 Details * *********************************************************** * 04/25/2019 15:43:23 INCIDENT REPORT (INCIDENT REPORT) * Report submitted by: Lisa Johnson 123-654-7890 * ENTITY\INCIDENT: * * CONDITION DESCRIPTION/LOCATION (THE INAPPROPRIATE ACTION AND ITS NEGATIVE EFFECT/INCLUDE A DETAILED LOCATION DESCRIPTION): * During post-maintenance restart, abnormal voltage instability observed in C42 Pump motor control circuit. This was observed on the HMI during routine start sequence. The situation was immediately reported to the shift supervisor and further analysis was initiated. * * ACTIVITIES, PROCESSES, PROCEDURES INVOLVED: * Post-Maintenance Start-up Check, Control Circuit Inspection * * WHY DID CONDITION HAPPEN? * Unknown, possible control circuit issue or component failure. * * CONSEQUENCES: * Potential motor malfunction or failure, delayed operation. * * REQUIREMENTS IMPACTED: * Normal operation and post-maintenance start-up. * * ADVERSE PHYSICAL CONDITIONS: * Voltage instability in motor control circuit. * * WHO WAS NOTIFIED: * Shift Supervisor, Maintenance Coordinator * * KNOWLEDGEABLE INDIVIDUALS: * Shift Supervisor, Control System Technicians * * REPEAT OR SIMILAR CONDITION: * No, this is the first instance. * * IMMEDIATE ACTIONS AND RECOMMENDED ACTIONS: * Control circuit to be inspected by Control System Technicians. If needed, component replacement and further testing to be conducted. * 04/25/2019 18:45:33 LISA JOHNSON (INCIDENT) * Fault was traced to a defective voltage regulator module. The module has been replaced and systems re-tested. Voltage stability is now confirmed. Recommend starting the C42 pump under supervision. | What were the immediate actions taken following the voltage instability in the C42 Pump motor control circuit? | Control circuit to be inspected by Control System Technicians. If needed, component replacement and further testing to be conducted.
33 | 2022-03-20 | 40944325 | 90234523 | 10C Pump lower pressure after recent service | S4CW -4CWE5 | * **************Incident Description************** * Notification 000040944325 Details * *********************************************************** * 03/20/2022 07:15:33 INCIDENT REPORT (INCIDENT REPORT) * Report submitted by: David Green 987-654-3210 * ENTITY\INCIDENT: * * CONDITION DESCRIPTION/LOCATION (THE INAPPROPRIATE ACTION AND ITS NEGATIVE EFFECT/INCLUDE A DETAILED LOCATION DESCRIPTION): * Post recent service conducted on the 10C Pump, a drop in pressure was noticed. The pressure was recorded as being 5 psig lower than expected. This is inconsistent with typical performance post service and requires immediate investigation. Potential causes could involve a fault in the recent service or an underlying issue with the pump system. * * ACTIVITIES, PROCESSES, PROCEDURES INVOLVED: * Post-service inspection and testing, S4.OP-SO.CW-0003 * * WHY DID CONDITION HAPPEN? * Yet to be confirmed. Potential negligence during the service or underlying pump issue. * * CONSEQUENCES: * Inefficiency in operation, system instability * * REQUIREMENTS IMPACTED: * Pump efficiency and operation, S4.OP-SO.CW-0003 * * ADVERSE PHYSICAL CONDITIONS: * Lower than expected pressure at 10C Pump * * WHO WAS NOTIFIED: * Operations Manager, Maintenance Supervisor * * KNOWLEDGEABLE INDIVIDUALS: * Pump Operation Team, Maintenance Crew * * REPEAT OR SIMILAR CONDITION: * No, this is the first incident. * * IMMEDIATE ACTIONS AND RECOMMENDED ACTIONS: * Immediate re-inspection of 10C Pump. Identify cause for pressure drop and rectify. Review the conducted service and examine for negligence or faulty parts. * 03/21/2023 10:30:17 DAVID GREEN (INCIDENT) * Re-inspection initiated. Maintenance and diagnostic team on the task. Anomaly will be reported to the operations manager and the necessary adjustments will be made. | What immediate actions were suggested after noticing lower pressure in 10C Pump? | Immediate re-inspection of 10C Pump. Identify cause for pressure drop and rectify. Review the conducted service and examine for negligence or faulty parts.
34 | 2018-04-15 | 30746810 | 80245630 | MOTOR VIBRATION OBSERVED ON 15B PUMP | S4CW -4CWE5 | * **************Incident Description************** * Notification 000030746810 Details * *********************************************************** * 04/15/2018 13:43:00 INCIDENT REPORT (INCIDENT REPORT) * Report submitted by: Thomas Richards ENTITY\INCIDENT: * * CONDITION DESCRIPTION/LOCATION (THE INAPPROPRIATE ACTION AND ITS NEGATIVE EFFECT/INCLUDE A DETAILED LOCATION DESCRIPTION): * Unexpected vibration was noticed on the 15B Pump motor. As part of the regular monitoring and checkup, pump vibrations levels were checked using handheld vibration monitor. The vibration levels were found to be beyond the permissible limits which prompted an emergency shutdown. No immediate signs of external damage were observed. * * ACTIVITIES, PROCESSES, PROCEDURES INVOLVED: * Regular maintenance check. Consultation of S4.OP-AB.CW-0003 and S4.OP-PR.CW-0002. * * WHY DID CONDITION HAPPEN? * Unknown at this time, potential issues include misalignment, balance issues or bearing failure. * * CONSEQUENCES: * Potential pump failure, loss of efficiency and breakdown if ignored. * * REQUIREMENTS IMPACTED: * Regular workflow and pump operation. * * ADVERSE PHYSICAL CONDITIONS: * Increased vibration level on the 15B pump. * * WHO WAS NOTIFIED: * Maintenance Supervisor, Safety Officer, Operations Manager * * KNOWLEDGEABLE INDIVIDUALS: * Thomas Richards, Jane Doe, Alex Brown * * REPEAT OR SIMILAR CONDITION: * No, this is the first instance with such issue on 15B pump. * * IMMEDIATE ACTIONS AND RECOMMENDED ACTIONS: * Immediate inspection and troubleshooting, balancing checks and alignment, bearing inspections if required. * 04/17/2018 09:45:25 THOMAS RICHARDS (INCIDENT) * Inspection revealed that the issue was due to misalignment. The alignment was corrected, and the pump is now operating within normal parameters. | What was the issue identified with the 15B Pump motor and how was it resolved? | Inspection revealed that the issue was due to misalignment. The alignment was corrected, and the pump is now operating within normal parameters.
35 | 2019-09-25 | 30931274 | 90268313 | Leak detected in 18B Heat Exchanger | S4HE -4HEX-EX18 | * **************Incident Description************** * Notification: 30931274 Details * *********************************************************** * 09/25/2019 14:30:35 INCIDENT REPORT (INCIDENT REPORT) * Report submitted by: Daisy Williams 987-654-3210 * ENTITY\INCIDENT: * * CONDITION DESCRIPTION/LOCATION (THE INAPPROPRIATE ACTION AND ITS NEGATIVE EFFECT/INCLUDE A DETAILED LOCATION DESCRIPTION): * During standard maintenance procedure, technician Thompson noted water leak from the 18B Heat Exchanger located in Sector 3.C. Immediate shutdown was initiated as per the safety protocol and containment was established to avoid further spillage. No other damage was observed in the vicinity. * * ACTIVITIES, PROCESSES, PROCEDURES INVOLVED: * Standard Maintenance Check S4.MC-HE.0001 * * WHY DID CONDITION HAPPEN? * Preliminary findings suggest corrosion induced damage or fitting failure. * * CONSEQUENCES: * Potential coolent loss, equipment failure * * REQUIREMENTS IMPACTED: * Timely maintenance and containment efforts * * ADVERSE PHYSICAL CONDITIONS: * Water leak from heat exchanger * * WHO WAS NOTIFIED: * Maintenance Supervisor, Safety Team * * KNOWLEDGEABLE INDIVIDUALS: * Maintenance Team, Safety Officer * * REPEAT OR SIMILAR CONDITION: * No, isolated incident * * IMMEDIATE ACTIONS AND RECOMMENDED ACTIONS: * Investigate source of leakage, replace or repair as appropriate * 09/25/2019 16:05:10 TOM THOMPSON (INCIDENT) * The leak was from a damaged fitting. The fitting was replaced and the exchanger was tested for leaks. No further leak was observed. The exchanger is back to normal operation. | What immediate actions were recommended after the water leak incident? | Investigate source of leakage, replace or repair as appropriate
36 | 2020-09-15 | 30945612 | 90245638 | 16B Valve high pressure alert | S4CV -4CVE7 | * **************Incident Description************** * Notification 000030945612 Details * *********************************************************** * 09/15/2020 14:32:00 INCIDENT REPORT (INCIDENT REPORT) * Report submitted by: Emily Smith * * 1) CONDITION DESCRIPTION/LOCATION (THE INAPPROPRIATE ACTION AND ITS NEGATIVE EFFECT/INCLUDE A DETAILED LOCATION DESCRIPTION): * During a system check, notification was triggered on the console for a high-pressure alert on the 16B Valve. Located in unit 4, the valve was flagged at a pressure of 120 psi; normal range is 95-100 psi. Immediate inspection was performed by on-duty personnel, but no signs of damage or leakage were detected. * * 2) ACTIVITIES, PROCESSES, PROCEDURES INVOLVED: * S4.OP.AB-CV-0002, S4.OP-SO.CV-0003 * * 3) WHY DID CONDITION HAPPEN: * No clear reason at this time, although valves have shown high-pressure alerts in the past due to sediment build-up. * * 4) CONSEQUENCES: * If constant, a high-pressure scenario could result in valve damage and failure. * * 5) REQUIREMENTS IMPACTED: * System efficiency, potential safety risk * * 6) ADVERSE PHYSICAL CONDITION: * Higher than normal pressure within 16B Valve, potential internal damage * * 7) WHO WAS NOTIFIED: * Supervisor, Maintenance Team * * 8) KNOWLEDGEABLE INDIVIDUALS: * Watson, Davis, Chen * * 9) REPEAT OR SIMILAR CONDITION: * Yes, occasional * * 10) IMMEDIATE AND RECOMMENDED ACTIONS: * Submit maintenance order to investigate cause of high pressure within 16B Valve, clean and maintenance as needed. * * Updated: Emily Smith 09.15.2020 16:15:29 * ------------------------------------------------------------ * 09/25/2020 08:53:17 MARK JONES (NUSER) * After inspection and maintenance, the valve pressure is now | What could be potential reasons for the high-pressure alert in the 16B Valve? | No clear reason at this time, although valves have shown high-pressure alerts in the past due to sediment build-up.
37 | 2017-05-15 | 30843570 | 80234515 | Engine 72B oil pressure abnormal | S4EB -4EBE72 | * **************Incident Description************** * Notification 000030843570 Details * *********************************************************** * 15/05/2017 06:21:42 INCIDENT REPORT (INCIDENT REPORT) * Report submitted by: Karen Lee ENTITY\INCIDENT: * * CONDITION DESCRIPTION/LOCATION (THE INAPPROPRIATE ACTION AND ITS NEGATIVE EFFECT/INCLUDE A DETAILED LOCATION DESCRIPTION): * During a routine system check at 0520 on 5/15/17, I noted that Engine 72B had abnormal oil pressure. The pressure gauge indicated a reading higher than usual, at 90 psi, while the regular pressure is usually around 75 psi. There were no external signs of damage or leakage. Procedure S4.OP-EA.EB-0007 Engine Trouble Shooting was initiated. * * ACTIVITIES, PROCESSES, PROCEDURES INVOLVED: * S4.OP-EA.EB-0007, S4.OP-SO.EB-0003 * * WHY DID CONDITION HAPPEN? * The cause remains unknown, further investigation and inspection required. * * CONSEQUENCES: * The abnormal pressure may result in engine damage and reduced efficiency, leading to increased maintenance and operation costs. * * REQUIREMENTS IMPACTED: * Standard engine operation * * ADVERSE PHYSICAL CONDITIONS: * Elevated oil pressure in Engine 72B * * WHO WAS NOTIFIED: * Control Room, Maintenance Staff * * KNOWLEDGEABLE INDIVIDUALS: * Adams, Harris, Franco * * REPEAT OR SIMILAR CONDITION: * Yes, 3 prior notifications within the last 6 months on different engines * * IMMEDIATE ACTIONS AND RECOMMENDED ACTIONS: * Follow S4.OP-EA.EB-0007 for troubleshooting abnormal oil pressure. If necessary, enlist help of manufacturer service engineer. * 15/05/2017 10:32:51 KAREN LEE (INCIDENT) * Service engineer was called to investigate the root cause of the abnormal pressure. The engine was temporarily taken off line pending further investigation. | What was the immediate action taken when abnormal oil pressure was noted in Engine 72B? | Follow S4.OP-EA.EB-0007 for troubleshooting abnormal oil pressure. If necessary, enlist help of manufacturer service engineer. Service engineer was called to investigate the root cause of the abnormal pressure. The engine was temporarily taken off line pending further investigation.
38 | 2018-02-24 | 30980235 | 80573650 | Pump 18C abnormal vibration | S4CW -4CWE6 | * **************Incident Description************** * Notification 000030980235 Details * *********************************************************** * 02/24/2018 14:17:44 INCIDENT REPORT (INCIDENT REPORT) * Report submitted by: Patricia Walsh ENTITY\INCIDENT: * CONDITION DESCRIPTION/LOCATION (THE INAPPROPRIATE ACTION AND ITS NEGATIVE EFFECT/INCLUDE A DETAILED LOCATION DESCRIPTION): * During regular equipment survey, abnormal vibration was noticed on 18C Pump. The vibration was significantly higher than the usual operating condition. The pump was subsequently isolated and shut down for immediate inspection. * * ACTIVITIES, PROCESSES, PROCEDURES INVOLVED: * Regular Equipment Survey * WHY DID CONDITION HAPPEN? * The current analysis suggests a potential imbalance in the motor shaft or potential bearing failure. * * CONSEQUENCES: * Possible catastrophic failure of the pump. * * REQUIREMENTS IMPACTED: * Regular operation of the pump and possible downstream effects. * * ADVERSE PHYSICAL CONDITIONS: * High vibration level and potential equipment damage. * * WHO WAS NOTIFIED: * Maintenance Supervisor, Safety Officers * * KNOWLEDGEABLE INDIVIDUALS: * Maintenance Team, Safety Officers * * REPEAT OR SIMILAR CONDITION: * No, it's a first-time observation. * * IMMEDIATE ACTIONS AND RECOMMENDED ACTIONS: * Immediate isolation of the pump and scheduled investigation by the maintenance team. * 02/26/2018 13:15:26 PATRICIA WALSH (INCIDENT) * Pump motor has been inspected and the identified issue was due to a failure in the bearing which was then replaced. The motor has been placed back on service and the vibration levels are back to normal operation conditions. | What actions were taken after the abnormal vibration was noticed on the 18C Pump? | The pump was subsequently isolated and shut down for immediate inspection. Immediate isolation of the pump and scheduled investigation by the maintenance team. Pump motor has been inspected and the identified issue was due to a failure in the bearing which was then replaced. The motor has been placed back on service and the vibration levels are back to normal operation conditions.
39 | 2016-04-12 | 30756822 | 80233755 | 32B pumping motor vibration detection | S4CW -4CWE9 | * **************Incident Description************** * Notification 000030756822 Details * *********************************************************** * 04/12/2016 08:45:48 INCIDENT REPORT (INCIDENT REPORT) * Report submitted by: Susan Martin ENTITY\INCIDENT: * * CONDITION DESCRIPTION/LOCATION (THE INAPPROPRIATE ACTION AND ITS NEGATIVE EFFECT/INCLUDE A DETAILED LOCATION DESCRIPTION): * During morning routine inspection at 0830, high vibrations detected on 32B Pump motor. Inspection team was immediately notified. 32B Pump Motor was manually shut down to prevent further damage. Preliminary inspection revealed no external cause for the generated vibration. * * ACTIVITIES, PROCESSES, PROCEDURES INVOLVED: * S4.OP-SO.CW-0001, General Daily Inspection * * WHY DID CONDITION HAPPEN: * Unknown, further inspection needed. * * CONSEQUENCES: * Unexpected interruption of normal operation, potential internal damage to pump motor resulting in maintenance downtime. * * REQUIREMENTS IMPACTED: * Routine Operations, Efficiency. * * ADVERSE PHYSICAL CONDITIONS: * High Vibrations detected on 32B Pump motor * * WHO WAS NOTIFIED: * Control Room, Maintenance Team * * KNOWLEDGEABLE INDIVIDUALS: * Susan Martin, Maintenance Team, Head of Operations * * REPEAT OR SIMILAR CONDITION: * No, not previously recorded. * * IMMEDIATE ACTIONS AND RECOMMENDED ACTIONS: * Investigation and immediate maintenance to determine the root cause of the vibration. * 04/14/2016 09:23:15 SUSAN MARTIN (INCIDENT) * Maintenance inspection found an imbalance in the pump's motor rotor. The rotor has been balanced, and the motor no longer exhibits abnormal vibration. The system is now back to operational status. | What was found during the maintenance inspection of the pump motor after the incident? | Maintenance inspection found an imbalance in the pump's motor rotor. The rotor has been balanced, and the motor no longer exhibits abnormal vibration.
40 | 2018-05-17 | 30888121 | 90245153 | Unusual 10B Pump Vibration | S4CW -4CWE9 | * **************Incident Description************** * Notification 000030888121 Details * *********************************************************** * 05/17/2018 13:35:00 INCIDENT REPORT (INCIDENT REPORT) * Report submitted by: Tom Hardy 987-654-3210 ENTITY\INCIDENT: * CONDITION DESCRIPTION/LOCATION (THE INAPPROPRIATE ACTION AND ITS NEGATIVE EFFECT/INCLUDE A DETAILED LOCATION DESCRIPTION): * During a routine walkdown inspection today, unusual vibrations were noted in the 10B Pump. The vibrations appeared exaggerated compared to other pumps in service and the 10B pump itself prior to the most recent maintenance performed under work order 90235891. Kilowatt output was slightly elevated at 605 kW. * ACTIVITIES, PROCESSES, PROCEDURES INVOLVED: * Routine walkdown inspection * * WHY DID CONDITION HAPPEN? * Unknown. Possible internal damage affecting pump and motor operations or an imbalance in the pump. * * CONSEQUENCES: * Potential for early pump failure, unexpected loss of service, and possible maintenance team safety risk. * * REQUIREMENTS IMPACTED: * Predictive maintenance plan * * ADVERSE PHYSICAL CONDITIONS: * Increased vibration and kilowatt output from pump 10B * * WHO WAS NOTIFIED: * Supervisor, Maintenance Team * * KNOWLEDGEABLE INDIVIDUALS: * Supervisor, Tom Hardy, Incident Team * * REPEAT OR SIMILAR CONDITION: * No, this is the first indication of such an issue on the 10B pump. * * IMMEDIATE ACTIONS AND RECOMMENDED ACTIONS: * Organize an immediate pump shutdown, followed by an internal inspection. Detailed vibration analysis could be beneficial in diagnosing the issue. * 05/18/2018 09:51:45 TOM HARDY (INCIDENT) * Vibration analysis was performed and confirmed an imbalance in the impeller. Repairs have been scheduled, and the pump is expected to be back in service soon. | What was the immediate action recommended after noting the unusual vibrations in the pump? | Organize an immediate pump shutdown, followed by an internal inspection. Detailed vibration analysis could be beneficial in diagnosing the issue.
41 | 2017-09-15 | 30750321 | 80234567 | 10B Pump experiencing vibration issues | S4CW -4CWE1 | * **************Incident Description************** * Notification 000030750321 Details * *********************************************************** * 09/15/2017 14:42:00 INCIDENT REPORT (INCIDENT REPORT) * Report submitted by: Linda Green ENTITY\INCIDENT: * * CONDITION DESCRIPTION/LOCATION (THE INAPPROPRIATE ACTION AND ITS NEGATIVE EFFECT/INCLUDE A DETAILED LOCATION DESCRIPTION): * Operator reported the 10B Pump was experiencing vibrations during operations. The vibrations were felt at central monitoring station. Systems check revealed that pump validity parameters were within normal limits. However, unusual vibration levels could indicate internal wear or damage. * * ACTIVITIES, PROCESSES, PROCEDURES INVOLVED: * Operations monitoring system, Pump maintenance Procedures - S4.OP-S3.CW-0001 * * WHY DID CONDITION HAPPEN? * The cause is uncertain at this time. Potential underlying conditions include wear and tear, improper installation, or imbalance in pump. * * CONSEQUENCES: * If left unattended, the condition could escalate and lead to pump failure or damage. * * REQUIREMENTS IMPACTED: * Normal operation * * ADVERSE PHYSICAL CONDITIONS: * Severe vibrations from the pump * * WHO WAS NOTIFIED: * Operations Supervisor, Maintenance Team * * KNOWLEDGEABLE INDIVIDUALS: * Operations Supervisor, Pump Specialist, Maintenance Team Members * * REPEAT OR SIMILAR CONDITION: * No earlier issues registered involving severe vibrations but pumps have faced common maintenance issues. * * IMMEDIATE ACTIONS AND RECOMMENDED ACTIONS: * Maintenance team slated to inspect and repair any issues discovered. Follow Procedure S4.OP-S3.CW-0001 for pump maintenance. * 09/17/2017 09:52:20 LINDA GREEN (INCIDENT) * Maintenance team inspected and found imbalances in pump installation which were causing the vibrations. Adjustments were made and the pump is back in normal operation. Further monitoring is recommended to prevent recurrence. | What immediate and recommended actions were taken following the incident with the 10B Pump vibrations? | Maintenance team slated to inspect and repair any issues discovered. Follow Procedure S4.OP-S3.CW-0001 for pump maintenance.
42 | 2021-05-19 | 40051204 | 90221506 | Inconsistent water flow in Pump 7E | S4CW -4CWE5 | * **************Incident Description************** * Notification 000040051204 Details * *********************************************************** * 05/19/2021 13:42:56 INCIDENT REPORT (INCIDENT REPORT) * Report submitted by: Brian Scott 123-789-4561 ENTITY\INCIDENT: * * CONDITION DESCRIPTION/LOCATION (THE INAPPROPRIATE ACTION AND ITS NEGATIVE EFFECT/INCLUDE A DETAILED LOCATION DESCRIPTION): * During routine inspection, irregular water flow was noticed in the Pump 7E. * The flow was inconsistent compared to the normal flow rate, despite all operational parameters being within usual boundaries. * * ACTIVITIES, PROCESSES, PROCEDURES INVOLVED: * Routine inspection/S4.OP-AB.CW-0003 * * WHY DID CONDITION HAPPEN? * Unclear, potential pump motor or valve issue. * * CONSEQUENCES: * Potential disruption of water supply, further damage to the pump * * REQUIREMENTS IMPACTED: * Regular operation, water supply * * ADVERSE PHYSICAL CONDITIONS: * Inconsistent water flow from Pump 7E * * WHO WAS NOTIFIED: * Control Room/Immediate supervisor * * KNOWLEDGEABLE INDIVIDUALS: * Maintenance Team * * REPEAT OR SIMILAR CONDITION: * No * * IMMEDIATE ACTIONS AND RECOMMENDED ACTIONS: * Undergo further inspection and maintenance of Pump. Monitor closely and if issue persists, consider motor or valve replacement. * 05/19/2021 16:30:10 BRIAN SCOTT (INCIDENT) * Initial investigation suggests the issue is with the pump motor. Maintenance team has been alerted, and they will commence inspection and repair tasks tomorrow. The pump has been put on monitored status until resolved. | What were the immediate and recommended actions following the incident at Pump 7E? | Undergo further inspection and maintenance of Pump. Monitor closely and if issue persists, consider motor or valve replacement.
43 | 2020-09-29 | 30943043 | 80253435 | 7B pump irregular vibration | S4CW -4CWE2 | * **************Incident Description************** * Notification 000030943043 Details * *********************************************************** * 09/29/2020 14:05:15 INCIDENT REPORT (INCIDENT REPORT) * Report submitted by: William Fields ENTITY\INCIDENT: * * CONDITION DESCRIPTION/LOCATION (THE INAPPROPRIATE ACTION AND ITS NEGATIVE EFFECT/INCLUDE A DETAILED LOCATION DESCRIPTION): * During routine maintenance, an irregular vibration was detected on the 7B pump. There were no previous notifications of this condition. The pump was immediately removed from service and inspected. The vibration levels were high and could damage the pump if left unchecked. * * ACTIVITIES, PROCESSES, PROCEDURES INVOLVED: * Routine maintenance and inspection * * WHY DID CONDITION HAPPEN? * The cause is uncertain; could be due to worn bearings or internal misalignment. * * CONSEQUENCES: * Unchecked vibration could result in pump failure leading to unplanned downtime. * * REQUIREMENTS IMPACTED: * Unplanned maintenance and potential operational impacts. * * ADVERSE PHYSICAL CONDITIONS: * Irregular vibration at 7B pump motor * * WHO WAS NOTIFIED: * Maintenance Supervisor, Technical Services * * KNOWLEDGEABLE INDIVIDUALS: * William Fields, Maintenance Supervisor, Technical Services team * * REPEAT OR SIMILAR CONDITION: * No, this is the first occurrence of this issue. * * IMMEDIATE ACTIONS AND RECOMMENDED ACTIONS: * The pump is scheduled for an emergency teardown and investigation. Should the cause be determined to be a worn bearing, a replacement plan will be implemented. * 09/30/2020 10:14:20 WILLIAM FIELDS (INCIDENT) * The pump was inspected. The primary cause of the issue was a worn-out bearing. The pump has been serviced, and the bearing replaced. The pump is now operational. | What caused the irregular vibration on the 7B pump during routine maintenance? | The primary cause of the issue was a worn-out bearing.
44 | 2021-09-15 | 31234567 | 80923651 | Unusual vibration at 29B Pump | S5CW -5CWE7 | * **************Incident Description************** * Notification 000031234567 Details * *********************************************************** * 09/15/2021 10:12:16 INCIDENT REPORT (INCIDENT REPORT) * Report submitted by: Tom Hansen ENTITY\INCIDENT: * * CONDITION DESCRIPTION/LOCATION (THE INAPPROPRIATE ACTION AND ITS NEGATIVE EFFECT/INCLUDE A DETAILED LOCATION DESCRIPTION): * During a routine inspection at 0600 on 09/15/2021, unusual vibrations were noticed at 29B Pump. A possible bearing issue may be causing these vibrations. The pump was turned off and isolated immediately. An initial inspection shows no external damage. However, prolonged operation in this condition could result in a complete breakdown of the Pump. * * ACTIVITIES, PROCESSES, PROCEDURES INVOLVED: * S5.OP.AB-CW-0001, S5.OP-SO.CW-0001 * * WHY DID CONDITION HAPPEN? * Possible wear and tear or bearing damage. An investigation is necessary to confirm this. * * CONSEQUENCES: * Potential loss of operational efficiency, pump damage, and safety hazards. * * REQUIREMENTS IMPACTED: * Normal operations and safety protocols. * * ADVERSE PHYSICAL CONDITIONS: * Vibrations from the 29B pump, possible bearing damage. * * WHO WAS NOTIFIED: * Control Room, Maintenance Team. * * KNOWLEDGEABLE INDIVIDUALS: * Taylor, Jameson, Greene * * REPEAT OR SIMILAR CONDITION: * No, this is a new incident. * * IMMEDIATE ACTIONS AND RECOMMENDED ACTIONS: * Initiated S5.OP-AB.CW-0001 Pump Abnormality and notified Maintenance Team to initiate detailed pump inspection and potential repair or replacement. * 09/18/2021 13:35:47 TOM HANSEN (INCIDENT) * The Maintenance Team completed the investigation under work order 80923651. The cause was traced to a worn-out bearing. The bearing was replaced, and the pump tested. No unusual vibrations are noticed, post repair. Recommending | What was the immediate action taken after the detection of unusual vibrations in the 29B Pump? | Initiated S5.OP-AB.CW-0001 Pump Abnormality and notified Maintenance Team to initiate detailed pump inspection and potential repair or replacement.
45 | 2022-03-12 | 40930491 | 90123942 | High vibration detected in 3B pump | SC1W -1CWE2 | * **************Incident Description************** * Notification 000040930491 Details * *********************************************************** * 03/12/2022 10:38:32 INCIDENT REPORT (INCIDENT REPORT) * Report submitted by: Hannah Green * ENTITY\INCIDENT: * * CONDITION DESCRIPTION/LOCATION (THE INAPPROPRIATE ACTION AND ITS NEGATIVE EFFECT/INCLUDE A DETAILED LOCATION DESCRIPTION): * Routine monitoring identified high vibration in the 3B Pump. The pump operation was stopped, and a physical inspection was enacted. There was no visual damage, but the vibration was reconfirmed during a trial run. * * ACTIVITIES, PROCESSES, PROCEDURES INVOLVED: * Routine Monitoring, SC1.OP.C1.P-0004. * * WHY DID CONDITION HAPPEN? * At this time, the cause of the vibration is not clear. * * CONSEQUENCES: * The pump is out of operation until the cause is identified and fixed. This affects the efficiency of the whole system. * * REQUIREMENTS IMPACTED: * Pump availability, System Efficiency. * * ADVERSE PHYSICAL CONDITIONS: * High vibration levels with the unknown cause. * * WHO WAS NOTIFIED: * Supervisor, Maintenance Team, Incident Team. * * KNOWLEDGEABLE INDIVIDUALS: * Maintenance Team, Engineering Team. * * REPEAT OR SIMILAR CONDITION: * No, this is the first incident of this nature with this pump. * * IMMEDIATE ACTIONS AND RECOMMENDED ACTIONS: * Inspect and investigate the pump thoroughly to ascertain the cause for the high vibration. Possible overhaul may be considered. * 03/15/2022 14:17:28 JOHN DOE (INCIDENT) * Investigation underway with the full maintenance team. A detailed check of the components and systems involved is being conducted. Preliminary reports point out possible misalignment or bearing failure. The Maintenance Team will provide a detailed report once complete. | What immediate and recommended actions were taken following the discovery of the high vibration in the 3B Pump? | Inspect and investigate the pump thoroughly to ascertain the cause for the high vibration. Possible overhaul may be considered.
46 | 2018-11-24 | 30946175 | 80510623 | Excessive Vibration 16R Compressor | S1CM -1CPRE1OTR | * **************Incident Description************** * Notification 000030946175 Details * *********************************************************** * 11/24/2018 07:30:00 INCIDENT REPORT (INCIDENT REPORT) * Report submitted by: Rick Harrison ENTITY\INCIDENT: * * CONDITION DESCRIPTION/LOCATION (THE INAPPROPRIATE ACTION AND ITS NEGATIVE EFFECT/INCLUDE A DETAILED LOCATION DESCRIPTION): * During the quarterly maintenance activities, excessive vibration was recorded on 16R Compressor. The compression system was shut down immediately for safety. The vibration level recorded was above the limit defined in S1.OP-SO.CM-0002. The possibility of bearing failure or misalignment has been suggested. * * ACTIVITIES, PROCESSES, PROCEDURES INVOLVED: * Regular vibration check as per procedure S1.OP-SO.CM-0002. * * WHY DID CONDITION HAPPEN? * The cause is unknown at this time. A detailed inspection is scheduled for further investigation. * * CONSEQUENCES: * The compressor needs to be inspected and repaired, which may affect the plant operations if not resolved quickly. * * REQUIREMENTS IMPACTED: * Emergency shutdown of the compressor due to excessive vibration, impacting the plant operations. * * ADVERSE PHYSICAL CONDITIONS: * Excessive vibration from the 16R Compressor, potential internal damage. * * WHO WAS NOTIFIED: * Operation Control Room, Maintenance Department. * * KNOWLEDGEABLE INDIVIDUALS: * Rick Harrison, Sam Miller, Nancy Johnson. * * REPEAT OR SIMILAR CONDITION: * This is the first reported incident of this nature with this compressor. * * IMMEDIATE ACTIONS AND RECOMMENDED ACTIONS: * The compressor has been taken offline. Maintenance to conduct a detail inspection and necessary repairs on 16R Compressor. * 11/27/2018 13:14:59 RICK HARRISON (INCIDENT) * After comprehensive examination, it was found that the compressor bearing was defective. The faulty bearing was successfully replaced, and the system is now back in operation with normal vibration levels. | What was the immediate action taken after recording excessive vibration on the 16R Compressor? | The compression system was shut down immediately for safety. The compressor has been taken offline. Maintenance to conduct a detail inspection and necessary repairs on 16R Compressor.
47 | 2018-06-16 | 30971245 | 80283592 | Motor 9A abnormal vibration | S4CW -4CWE1 | * **************Incident Description************** * Notification 000030971245 Details * *********************************************************** * 06/16/2018 16:02:23 INCIDENT REPORT (INCIDENT REPORT) * Report submitted by: Thomas Gibson ENTITY\INCIDENT: * * CONDITION DESCRIPTION/LOCATION (THE INAPPROPRIATE ACTION AND ITS NEGATIVE EFFECT/INCLUDE A DETAILED LOCATION DESCRIPTION): * During the nightly check, Motor 9A was identified vibrating abnormally. Upon closer inspection, the vibration frequency was noted to be significantly higher than usual. Motor 9A is located in Unit 4. Normal routine monitoring procedures had been followed. * * ACTIVITIES, PROCESSES, PROCEDURES INVOLVED: * Routine checks & monitoring. * * WHY DID CONDITION HAPPEN? * The cause is yet to be identified. Might be due to bearing or balancing issue. * * CONSEQUENCES: * Could lead to potential equipment failure and loss in production. * * REQUIREMENTS IMPACTED: * Normal operation of Motor 9A. * * ADVERSE PHYSICAL CONDITIONS: * Excessive vibration at Motor 9A. The effect was immediately evident in the adverse vibrations. * * WHO WAS NOTIFIED: * Supervisor, Maintenance Team * * KNOWLEDGEABLE INDIVIDUALS: * Maintenance Team, Engineers * * REPEAT OR SIMILAR CONDITION: * No, this is a new finding * * IMMEDIATE ACTIONS AND RECOMMENDED ACTIONS: * Requesting detailed inspection of Motor 9A, possible balancing required. Machinery book procedure S4.MB-SO.MM-0005 must be followed for the detailed inspection. * 06/17/2018 09:12:41 THOMAS GIBSON (INCIDENT) * The maintenance team performed the inspection as directed, found misalignment in the motor rotor. It has been corrected as per standard protocol. Motor has been put back in operation and is now functioning normally. | What immediate actions were recommended due to abnormal vibration in Motor 9A? | Requesting detailed inspection of Motor 9A, possible balancing required. Machinery book procedure S4.MB-SO.MM-0005 must be followed for the detailed inspection.
48 | 2016-03-05 | 30845121 | 80255234 | High vibration from 16B cooling pump | S5CW -4CWE7 | * **************Incident Description************** * Notification 000030845121 Details * *********************************************************** * 03/05/2016 14:15:21 INCIDENT REPORT (INCIDENT REPORT) * Report submitted by: Richard Claus ENTITY\INCIDENT: * * CONDITION DESCRIPTION/LOCATION (THE INAPPROPRIATE ACTION AND ITS NEGATIVE EFFECT/INCLUDE A DETAILED LOCATION DESCRIPTION): * At 1405, during a regular round, engineer on shift noticed high vibration from 16B Cooling Pump. It was immediately reported to the Control Room and decision to emergency shutdown was made. A safety inspection was performed post shutdown. There were no external signs of damage but the vibration sensors recorded abnormally high levels which could be signs of internal mechanical imbalance or faults. * * ACTIVITIES, PROCESSES, PROCEDURES INVOLVED: * S5.OP.AB-CW-0002, S5.OP-SO.CW-0002 * * WHY DID CONDITION HAPPEN? * At this point, the exact cause is unclear, but possibilities include mechanical failure, misalignment, or potential debris caught in the pump. * * CONSEQUENCES: * Potential damage to the pump and nearby equipment, loss of efficiency and possible future unexpected shutdowns. * * REQUIREMENTS IMPACTED: * Cooling pump is currently out of service. * * ADVERSE PHYSICAL CONDITIONS: * High vibration level at 16B Cooling Pump, possible internal mechanical faults. * * WHO WAS NOTIFIED: * Control Room, Safety Team, Maintenance Department * * KNOWLEDGEABLE INDIVIDUALS: * Martin, Hughes, Rodriguez * * REPEAT OR SIMILAR CONDITION: * Not known at this time * * IMMEDIATE ACTIONS AND RECOMMENDED ACTIONS: * Safety inspection of area, immediate maintenance investigation into 16B Cooling Pump to ascertain exact cause of the abnormal vibration. * 03/05/2016 16:47:05 JANE DOE (INCIDENT) * The maintenance team has located the issue. Misalignment between the pump and motor was causing the vibration. Once realigned, normal operation resumed. Recommend a detailed alignment check within routine maintenance plan | What was the initial action taken after noticing high vibration in the 16B Cooling Pump? | It was immediately reported to the Control Room and decision to emergency shutdown was made. A safety inspection was performed post shutdown.
49 | 2020-12-01 | 31050923 | 81210354 | 7C Hydro motor high vibration | S4HY -4HYE5 | * **************Incident Description************** * Notification 000031050923 Details * *********************************************************** * 12/01/2020 16:27:15 INCIDENT REPORT (INCIDENT REPORT) * Report submitted by: Emily Williams ENTITY\INCIDENT: * * CONDITION DESCRIPTION/LOCATION (THE INAPPROPRIATE ACTION AND ITS NEGATIVE EFFECT/INCLUDE A DETAILED LOCATION DESCRIPTION): * During a regular check, it was discovered that 7C Hydro motor was experiencing abnormally high vibration. The increased vibration was detected on the motor bearings and pump housing. The operating parameters were within normal limits but the vibration levels were higher than the previous readings. * * ACTIVITIES, PROCESSES, PROCEDURES INVOLVED: * S4.OP.AB-HY-0002, S4.OP-SO.HY-0002 * * WHY DID CONDITION HAPPEN? * The reason is unknown, however, mechanical misalignment, imbalance, loose parts, or bearing wear could be potential causes. * * CONSEQUENCES: * Reduced motor life and potential for unexpected break down. * * REQUIREMENTS IMPACTED: * Motor functionality might be limited which can lead to an unexpected shutdown. * * ADVERSE PHYSICAL CONDITIONS: * High vibrations in the Hydro motor, possible bearing damage. * * WHO WAS NOTIFIED: * Plant Manager, Maintenance Team * * KNOWLEDGEABLE INDIVIDUALS: * Maintenance Team, Emily Williams * * REPEAT OR SIMILAR CONDITION: * No, first occurrence. * * IMMEDIATE ACTIONS AND RECOMMENDED ACTIONS: * Further investigation by maintenance department required. A detailed vibration analysis should be conducted to understand the causative factor of the high vibration. * 12/04/2020 14:50:12 JOHN DOE (INCIDENT) * 7C Hydro motor was examined by the maintenance team. Balance was checked and found to be within allowable limits. A misalignment was identified and corrected. Vibration levels reduced after realignment. Continuous monitoring will be done to ensure the issue does not recur. The motor is now back to normal operation. | What were the initial actions taken after discovering the high vibration in the 7C Hydro motor? | Further investigation by maintenance department required. A detailed vibration analysis should be conducted to understand the causative factor of the high vibration.
50 | 2017-04-16 | 30858274 | 80234862 | Increase in Vibrations from 36D Pump | S4CW -4CWE9 | * **************Incident Description************** * Notification 000030858274 Details * *********************************************************** * 04/16/2017 14:26:09 INCIDENT REPORT (INCIDENT REPORT) * Report submitted by: Sarah White 678-901-2345 * ENTITY\INCIDENT: * CONDITION DESCRIPTION/LOCATION (THE INAPPROPRIATE ACTION AND ITS NEGATIVE EFFECT/INCLUDE A DETAILED LOCATION DESCRIPTION): * During routine inspection, increased vibrations were detected from 36D Pump. Shut down the pump for emergency inspection. Upon initial assessment, no visible damage was detected. The pump was restarted, and the excessive vibration persisted. This is a potential safety concern and could lead to operational efficiency issues if not immediately addressed. * * ACTIVITIES, PROCESSES, PROCEDURES INVOLVED: * Routine inspection of pump, emergency shutdown and restart of pump. * * WHY DID CONDITION HAPPEN? * Unknown at this time. Possibility of internal parts failure or misalignment. * * CONSEQUENCES: * Decrease in operational efficiency, disruption of regular work flow, safety hazards * * REQUIREMENTS IMPACTED: * Safe and efficient pump operation * * ADVERSE PHYSICAL CONDITIONS: * Excessive vibration of 36D Pump * * WHO WAS NOTIFIED: * Control Room, Safety Team, Maintenance Department * * KNOWLEDGEABLE INDIVIDUALS: * Sarah White, Maintenance Team Lead * * REPEAT OR SIMILAR CONDITION: * No, this issue is newly reported * * IMMEDIATE ACTIONS AND RECOMMENDED ACTIONS: * Immediate shutdown of the problematic pump, request for detailed inspection by the maintenance team, and further investigative actions to be planned based on inspection results. * 04/16/2017 17:39:04 SARAH WHITE (INCIDENT) * Following the inspection and assessment of the vibration issue, the cause has been identified as a failing bearing. Detailed report and repair requisition submitted to the Maintenance Department. Expecting operations to return to normal following the repair and testing. Ensuring a close follow up. | What immediate actions were taken upon detection of the increased vibrations in Pump 36D? | Immediate shutdown of the problematic pump, request for detailed inspection by the maintenance team, and further investigative actions to be planned based on inspection results.
51 | 2017-05-18 | 30765219 | 80224759 | 33C Motor Overheating | S4CW -4CWE1 | * **************Incident Description************** * Notification 000030765219 Details * *********************************************************** * 05/18/2017 14:30:00 INCIDENT REPORT (INCIDENT REPORT) * Report submitted by: Frank Hardy ENTITY\INCIDENT: * CONDITION DESCRIPTION/LOCATION (THE INAPPROPRIATE ACTION AND ITS NEGATIVE EFFECT/INCLUDE A DETAILED LOCATION DESCRIPTION): * During a routine shift, a temperature increase was noticed in the 33C pump motor. An emergency stop was executed at 1530hrs and the matter was reported to the control room. Inspection by the engineering team and the shift supervisor revealed no damage on the exterior, but the scent of burnt insulation was detected. * ACTIVITIES, PROCESSES, PROCEDURES INVOLVED: * S4.OP.AP.CW-0012, S4.OP-SZ.CW-0009 * WHY DID CONDITION HAPPEN? * Uncertain. Past incidents involve the motor overheating due to blockages. * CONSEQUENCES: * If left unchecked, potential motor damage could lead to efficiency loss when the system is back in operation. * REQUIREMENTS IMPACTED: * Pump operation unavailability. * ADVERSE PHYSICAL CONDITIONS: * Overheating of the 33C pump motor with possible internal damage. * WHO WAS NOTIFIED: * Control Room, Engineering Team * KNOWLEDGEABLE INDIVIDUALS: * Clark, Wilson, Stokes * REPEAT OR SIMILAR CONDITION: * This is a recurring issue; similar incidents have occurred in the past. * IMMEDIATE ACTIONS AND RECOMMENDED ACTIONS: * Engineering team to check 33C Pump Motor * Updated: FRANK HARDY 05.18.2017 17:00:20 * ------------------------------------------------------------ * 06/01/2017 11:23:15 JOHN DOE (NUSER) * Investigation showed motor overheated due to an accumulation of debris. Cleaning the debris resolved the issue. The motor had been reassembled and is now operating normally. | What was the cause of the 33C pump motor overheating incident? | Investigation showed motor overheated due to an accumulation of debris.
52 | 2019-02-15 | 30984275 | 80245783 | Overheating of 29B Condenser | S4CW -4CWE2 | * **************Incident Description************** * Notification 000030984275 Details * *********************************************************** * 02/15/2019 14:24:32 INCIDENT REPORT (INCIDENT REPORT) * Report submitted by: George Fox ENTITY\INCIDENT: * * CONDITION DESCRIPTION/LOCATION (THE INAPPROPRIATE ACTION AND ITS NEGATIVE EFFECT/INCLUDE A DETAILED LOCATION DESCRIPTION): * During a routine inspection at 1400 hours on 15/02/19, Report noted 29B condenser was showing signs of overheating. The temperature and current readings were higher than normal range. Auxiliary units were immediately engaged to keep the system functional. * * ACTIVITIES, PROCESSES, PROCEDURES INVOLVED: * Routine inspection and observation of temperature and current parameters S4.OP-AB.CW-0002 and S4.OP-SO.CW-0001 * * WHY DID CONDITION HAPPEN? * Undetermined at the moment. Previous incidents point towards possible hardware malfunction or debris build-up. * * CONSEQUENCES: * Reduced efficiency due to auxiliary unit engagement. Possibility of unit damage if not resolved. * * REQUIREMENTS IMPACTED: * Regular operation of 29B condenser * * ADVERSE PHYSICAL CONDITIONS: * Overheating and excessive current at 29B condenser, potential internal damage * * WHO WAS NOTIFIED: * Control Room, Maintenance, Fire Department * * KNOWLEDGEABLE INDIVIDUALS: * Johnson, Smith, Lee, George * * REPEAT OR SIMILAR CONDITION: * Yes, similar incidents with other condensers have been reported in the past * * IMMEDIATE ACTIONS AND RECOMMENDED ACTIONS: * Immediate inspection required. If similar to previous incidents, hardware may need cleaning or replacement. * 02/16/2019 09:12:45 GEORGE FOX (INCIDENT) * On examination it was seen that debris build-up was causing the overheating. The unit was cleaned and returned to normal operation. Advised for more regular inspection to avoid future recurrences. | What was found to be the cause of the overheating in the 29B condenser? | On examination it was seen that debris build-up was causing the overheating. The unit was cleaned and returned to normal operation.
53 | 2020-04-22 | 40187055 | 90010653 | 7B Pump abnormal vibration | S4CW -4CWE7 | * **************Incident Description************** * Notification 000040187055 Details * *********************************************************** * 04/22/2020 14:20:43 INCIDENT REPORT (INCIDENT REPORT) * Report submitted by: Emily Green ENTITY\INCIDENT: * * CONDITION DESCRIPTION/LOCATION (THE INAPPROPRIATE ACTION AND ITS NEGATIVE EFFECT/INCLUDE A DETAILED LOCATION DESCRIPTION): * Continuous monitoring system reported that 7B pump has abnormal vibration at 7.8 mm/s RMS. This is higher than the alert level of 5 mm/s as per the guidelines. Operator at Unit 4 Control room confirmed the vibration. * * ACTIVITIES, PROCESSES, PROCEDURES INVOLVED: * Daily monitoring through Continuous monitoring system. S4.OP-AB.CW-0003, S4.OP-SO.CW-0003 * * WHY DID CONDITION HAPPEN? * Unknown, Arbitrary surges in vibration are unexplained. Further analysis might be required. * * CONSEQUENCES: * If left untreated, may result in Pump failure leading to operation shutdown. * * REQUIREMENTS IMPACTED: * Unit in operation - 7B Pump * * ADVERSE PHYSICAL CONDITIONS: * Abnormal vibration in 7B pump. * * WHO WAS NOTIFIED: * Supervisor, Maintenance Team * * KNOWLEDGEABLE INDIVIDUALS: * Jackson, Stuart, Carlos * * REPEAT OR SIMILAR CONDITION: * No, it is the first occurrence * * IMMEDIATE ACTIONS AND RECOMMENDED ACTIONS: * Conducting advanced analysis on 7B Pump, possible maintenance. * 04/26/2020 16:10:21 EMILY GREEN (INCIDENT) * Post detailed analysis it's found that the imbalances in the rotor caused the abnormal vibration. The pump rotor has been sent for maintenance and the plant is now operating normally. | What caused the abnormal vibration in the 7B pump? | The imbalances in the rotor caused the abnormal vibration.
54 | 2017-05-19 | 30817045 | 80241436 | 34B Pump leakage under new alignment | S4PW -4PWE3-MTRX | * **************Incident Description************** * Notification 000030817045 Details * *********************************************************** * 05/19/2017 07:32:00 INCIDENT REPORT (INCIDENT REPORT) * Report submitted by: Thomas Black ENTITY\INCIDENT: * * CONDITION DESCRIPTION/LOCATION (THE INAPPROPRIATE ACTION AND ITS NEGATIVE EFFECT/INCLUDE A DETAILED LOCATION DESCRIPTION): * During operation after maintenance work order 80231412, 34B pump was observed with a minor leak from the bottom housing seal. This pump was serviced and aligned under the new alignment protocol approved in early 2017 in procedure S4.OP-SO.PW-0007. However, it appears that the new alignment may have introduced a potential leakage pathway. * * ACTIVITIES, PROCESSES, PROCEDURES INVOLVED: * Working on the pump under procedure S4.OP-SO.PW-0007. * * WHY DID CONDITION HAPPEN? * Potentially due to new alignment procedure, further inspection required. * * CONSEQUENCES: * Potential for increased downtime, safety hazard due to slippery floor, potential impact on pump performance. * * REQUIREMENTS IMPACTED: * Environmental compliance, Workplace safety * * ADVERSE PHYSICAL CONDITIONS: * Leakage from 34B Pump * * WHO WAS NOTIFIED: * Supervisor, Health and Safety Officer * * KNOWLEDGEABLE INDIVIDUALS: * Thomas Black, Jane Doe, Michael Smith * * REPEAT OR SIMILAR CONDITION: * No. This is the first such incident after implementing new alignment protocol. * * IMMEDIATE ACTIONS AND RECOMMENDED ACTIONS: * Immediate containment of leaked fluid, scheduling a simpler checkup, Review of new alignment procedure with engineering team. * 05/20/2017 15:30:46 THOMAS BLACK (INCIDENT) * Containment actions were carried out effectively. Scheduled a simpler check for 34B. Conversation with engineers led to agreement on provisionally using the previous alignment procedure for other pumps and reviewing the new alignment approach based on results of the inspection. | What were the immediate actions taken after the incident involving pump 34B? | Immediate containment of leaked fluid, scheduling a simpler checkup, Review of new alignment procedure with engineering team.
55 | 2020-05-30 | 30778520 | 80245010 | Unexpected vibration in motor 5B Pump | S4CW -4CWE6 | * **************Incident Description************** * Notification 000030778520 Details * *********************************************************** * 05/30/2020 16:30:03 INCIDENT REPORT (INCIDENT REPORT) * Report submitted by: Laura Thompson ENTITY\INCIDENT: * * CONDITION DESCRIPTION/LOCATION (THE INAPPROPRIATE ACTION AND ITS NEGATIVE EFFECT/INCLUDE A DETAILED LOCATION DESCRIPTION): * On May 30th, 2020, during a periodic inspection, an unusual vibration was identified on the motor of the 5B Pump at the S4 Cooling Water System location. This is an atypical condition for this unit, which was recently serviced during the maintenance shutdown in April 2020. The vibration could be a sign of internal imbalance, damaged components, or misalignment. * * ACTIVITIES, PROCESSES, PROCEDURES INVOLVED: * Regular inspection and monitoring of equipment, namely S4.OP.SO.CW-0005. * * WHY DID CONDITION HAPPEN? * The exact cause of this vibration is yet unknown. It may be a result of overuse, difficult operation conditions or an issue during the last service procedure. * * CONSEQUENCES: * Risk of damage to the motor if issue is not addressed. This could lead to unplanned down-time and increased operating costs. * * REQUIREMENTS IMPACTED: * Regular operation and maintenance routine. * * ADVERSE PHYSICAL CONDITIONS: * Excessive vibration in the 5B pump motor. * * WHO WAS NOTIFIED: * Supervisor, Maintenance Team, Incident Investigator * * KNOWLEDGEABLE INDIVIDUALS: * Laura Thompson, John Green, Sam Roberts * * REPEAT OR SIMILAR CONDITION: * No previous instances reported for this specific unit. However, occasional excessive vibration issues have been noted fleet-wide on similar type motors. * * IMMEDIATE ACTIONS AND RECOMMENDED ACTIONS: * Recommended to halt use of the 5B Pump and carry out a thorough investigation, including vibration analysis and internal inspection. Ensure comprehensive reporting on the same, and revise maintenance procedures if necessary, specifically S4.OP | What immediate actions are recommended due to the vibration in the 5B pump motor? | Recommended to halt use of the 5B Pump and carry out a thorough investigation, including vibration analysis and internal inspection. Ensure comprehensive reporting on the same, and revise maintenance procedures if necessary, specifically S4.OP.
56 | 2018-11-19 | 30875201 | 80250093 | Unusual vibration in 30B Pump compressor | S3CW -3CWE4 | * **************Incident Description************** * Notification 000030875201 Details * *********************************************************** * 11/19/2018 17:38:00 INCIDENT REPORT (INCIDENT REPORT) * Report submitted by: Sarah Adams ENTITY\INCIDENT: * * CONDITION DESCRIPTION/LOCATION (THE INAPPROPRIATE ACTION AND ITS NEGATIVE EFFECT/INCLUDE A DETAILED LOCATION DESCRIPTION): * During the routine inspection, 30B coil compressor was noticed to have unusual vibration. The vibration was not normal and seemed to increase with increase in load. Comparatively, this pump does not show the same behavior at similar loads. The vibration was immediately reported and the pump was put on standby until further inspection. * * ACTIVITIES, PROCESSES, PROCEDURES INVOLVED: * Routine inspection and operations of S3.OP-SO.CW-0002. * * WHY DID CONDITION HAPPEN? * Unknown, possibly due to a mechanical issue or internal damage. * * CONSEQUENCES: * Risk of severe damaging the pump if left unaddressed. This could lead to operational downtime and cost implications. * * REQUIREMENTS IMPACTED: * Regular pump operations and maintenance schedule. * * ADVERSE PHYSICAL CONDITIONS: * Unusually high vibrational activity observed in the 30B pump compressor. * * WHO WAS NOTIFIED: * Supervisor, Maintenance Team. * * KNOWLEDGEABLE INDIVIDUALS: * John Smith, Emma Moore from the Maintenance Team. * * REPEAT OR SIMILAR CONDITION: * No, this is the first time such an issue has been reported with this pump model. * * IMMEDIATE ACTIONS AND RECOMMENDED ACTIONS: * The pump has been put on standby mode. Maintenance team to carry out a detailed inspection to identify the root cause of the unusual vibration. Necessary action will be taken based on the inspection report. * 11/22/2018 12:50:27 ALEX BROWN (INCIDENT) * Post a detailed inspection of the 30B pump compressor, it was found that the issue was due to misalignment of the motor and pump. The configuration has been adjusted and the pump is | What was the cause of the unusual vibration in the 30B pump compressor? | The issue was due to misalignment of the motor and pump.
57 | 2016-09-25 | 30766123 | 80237201 | Irregular vibrations in 4B Motor turbine | S1MT -1MT4B | * **************Incident Description************** * Notification 000030766123 Details * *********************************************************** * 09/25/2016 10:13:11 INCIDENT REPORT (INCIDENT REPORT) * Report submitted by: David Thompson 321-654-0987 ENTITY\INCIDENT: * CONDITION DESCRIPTION/LOCATION (THE INAPPROPRIATE ACTION AND ITS NEGATIVE EFFECT/INCLUDE A DETAILED LOCATION DESCRIPTION): * During the morning shift, the sensor attached to the 4B Motor Turbine recorded significant vibrations. Turbine speed was within the expected range, with around 3450 RPM. Ambient temperature and pressure readings were simultaneously noted to be normal. * * ACTIVITIES, PROCESSES, PROCEDURES INVOLVED: * Regular system monitoring * WHY DID CONDITION HAPPEN? * The cause is undetermined. However, misalignment or unbalance in the turbine can potentially cause such vibrations. * * CONSEQUENCES: * If not addressed, vibrations can lead to mechanical failure or a decrease in system efficiency. * * REQUIREMENTS IMPACTED: * System stability and turbine reliability. * * ADVERSE PHYSICAL CONDITIONS: * High-level vibrations in 4B Motor Turbine. * * WHO WAS NOTIFIED: * Operations Supervisor, Maintenance Division. * * KNOWLEDGEABLE INDIVIDUALS: * Operations Team, Engineering Unit. * * REPEAT OR SIMILAR CONDITION: * No, this is the first time such an incident has been recorded for this motor. * * IMMEDIATE ACTIONS AND RECOMMENDED ACTIONS: * Implement immediate inspection and diagnostic testing of the turbine. If required, carry out maintenance actions to rectify the issue. * 09/25/2016 14:15:00 DAVID THOMPSON (INCIDENT) * Inspections have begun, and carry out is being done collaboratively by the engineering unit and maintenance division. Proper diagnostics will be crucial to understanding the root cause of this condition. | What could be the potential cause of the significant vibrations in the 4B Motor Turbine? | The cause is undetermined. However, misalignment or unbalance in the turbine can potentially cause such vibrations.
58 | 2020-01-12 | 30764223 | 80239234 | Heat anomaly in Pump X10U | S4SE -4SES5 | * **************Incident Description************** * Notification 000030764223 Details * *********************************************************** * 01/12/2020 08:27:00 INCIDENT REPORT (INCIDENT REPORT) * Report submitted by: Mark Foster ENTITY\INCIDENT: * * CONDITION DESCRIPTION/LOCATION (THE INAPPROPRIATE ACTION AND ITS NEGATIVE EFFECT/INCLUDE A DETAILED LOCATION DESCRIPTION): * On Jan 12, 2020, the X10U pump showed an unusual heat surge on the monitoring unit. The subsequent thermal images confirmed that the motor possibly overheated. The pump was shut down temporarily, which curtailed the heat immediately. Visual inspection did not reveal any soot or smoke but a distinctive smell of heated insulation was present. X10U pump abnormality guideline S4.OP-AB.SE-0005 was exercised as a precautionary measure. * * ACTIVITIES, PROCESSES, PROCEDURES INVOLVED: * S4.OP-AB.SE-0005, S4.OP-SO.SE-0008 * * WHY DID CONDITION HAPPEN? * Not determined, this could be a sporadic event or due to a similar incident in the past. * * CONSEQUENCES: * Immediate unavailability of X10U pump, possible internal damage leading to efficiency loss when the unit comes back online. * * REQUIREMENTS IMPACTED: * Pump is inactive for now. * * ADVERSE PHYSICAL CONDITIONS: * Overheated X10U pump motor, possible internal damage. * * WHO WAS NOTIFIED: * Operations Room, Engineering Team. * * KNOWLEDGEABLE INDIVIDUALS: * Dawson, Fernandez, Gibbons * * REPEAT OR SIMILAR CONDITION: * Unknown * * IMMEDIATE ACTIONS AND RECOMMENDED ACTIONS: * Initiate the investigation of X10U Pump Motor, bring Maintenance team on board for thorough component diagnosis and repair, if required. * * Updated: MARK FOSTER 01.12.2020 11:03:12 * ---------------------------------------------------------- * 02/05/2020 07:14:51 JOHN BAKER (NUSER | What immediate actions were recommended after the X10U pump overheated? | Initiate the investigation of X10U Pump Motor, bring Maintenance team on board for thorough component diagnosis and repair, if required.
59 | 2018-09-01 | 31012452 | 90269224 | 33B heat exchanger erratic pressure | S5HE -5HWE1 | * **************Incident Description************** * Notification 000031012452 Details * *********************************************************** * 09/01/2018 15:20:10 INCIDENT REPORT (INCIDENT REPORT) * Report submitted by: Emily Rose 321-654-0987 * ENTITY\INCIDENT: * CONDITION DESCRIPTION/LOCATION (THE INAPPROPRIATE ACTION AND ITS NEGATIVE EFFECT/INCLUDE A DETAILED LOCATION DESCRIPTION): * During scheduled 33B Heat Exchanger inspection, erratic pressure readings were noted. Identified pressure variation from 27 to 57 psig, which is unusual as the device normally operates at steady 45 psig. No abnormal ambient conditions were noted that could account for the variation. * * ACTIVITIES, PROCESSES, PROCEDURES INVOLVED: * Regular inspection, S5.OP.SO.HE-0003 procedure * * WHY DID CONDITION HAPPEN? * Cause unknown, possibly due to malfunctioning pressure control or internal components damage * * CONSEQUENCES: * Inefficient operation, potential damage to the exchanger and adjoining pipelines due to pressure spikes * * REQUIREMENTS IMPACTED: * Stability of the heat exchanger operation * * ADVERSE PHYSICAL CONDITIONS: * Fluctuating pressure in 33B heat exchanger * * WHO WAS NOTIFIED: * Shift Supervisor, Maintenance Lead * * KNOWLEDGEABLE INDIVIDUALS: * Emily Rose, Maintenance Lead, Shift Supervisor * * REPEAT OR SIMILAR CONDITION: * No, first occurrence * * IMMEDIATE ACTIONS AND RECOMMENDED ACTIONS: * Carry out immediate shut down of the 33B heat exchanger, perform an internal inspection, and consider running diagnostic tests for malfunctioning components. * 09/02/2018 09:35:30 EMILY ROSE (INCIDENT) * After shutdown and inspection, damaged pressure relief valve was identified and replaced. The 33B heat exchanger is now back in service with stable operation. | What was the identified cause for the abnormal pressure fluctuations in the 33B heat exchanger? | Cause unknown, possibly due to malfunctioning pressure control or internal components damage.
60 | 2019-03-12 | 30837593 | 80230246 | LOW OUTPUT FROM 18B PUMP MOTOR | S3CW -3CWE5 | * **************Incident Description************** * Notification 000030837593 Details * *********************************************************** * 03/12/2019 15:39:46 INCIDENT REPORT (INCIDENT REPORT) * Report submitted by: William Ross ENTITY\INCIDENT: * * CONDITION DESCRIPTION/LOCATION (THE INAPPROPRIATE ACTION AND ITS NEGATIVE EFFECT/INCLUDE A DETAILED LOCATION DESCRIPTION): * During routine tests, observed under-performance from 18B Pump Motor. The output from the 18B Pump motor was significantly low compared to other pumps in operation. The output seemed inconsistent and fluctuated between high and low values. * ACTIVITIES, PROCESSES, PROCEDURES INVOLVED: * Routine testing, operating procedure S3.OP-AB.CW-0001 * * WHY DID CONDITION HAPPEN? * Unknown, possible faulty motor or wiring. * * CONSEQUENCES: * The low output could result in under-performance of the overall system. Potential for motor overheating or failure if continued to operate under these conditions. * * REQUIREMENTS IMPACTED: * Normal operation and efficiency are at risk due to faulty pump output. * * ADVERSE PHYSICAL CONDITIONS: * 18B pump performing with unusual output levels. * * WHO WAS NOTIFIED: * System Supervisor, Maintenance, Operations Team * * KNOWLEDGEABLE INDIVIDUALS: * Alan Watson, Mike Philips, Laura Reed * * REPEAT OR SIMILAR CONDITION: * No, this is the first instance * * IMMEDIATE ACTIONS AND RECOMMENDED ACTIONS: * Maintenance team to inspect 18B Pump Motor for potential issues. Exterior wiring to be checked and replaced if required. * If the issue persists after routine checks and maintenance, a full investigation and overhaul might be needed. * 03/13/2019 09:45:21 WILLIAM ROSS (INCIDENT) * The inspection was carried out, nothing wrong with the wiring. The motor is to be tested for internal faults. Further updates to follow. | What were the immediate actions taken after the under-performance of the 18B Pump Motor was observed? | Maintenance team to inspect 18B Pump Motor for potential issues. Exterior wiring to be checked and replaced if required. If the issue persists after routine checks and maintenance, a full investigation and overhaul might be needed.
61 | 2019-05-01 | 30850723 | 90241867 | Decreased pressure in 17B pump after overhaul | S1CW -1CWE7-PMPX | * **************Incident Description************** * Notification 000030850723 Details * *********************************************************** * 05/01/2019 14:41:33 INCIDENT REPORT (INCIDENT REPORT) * Report submitted by: Linda Evans 456-789-0123 * * ENTITY\INCIDENT: * CONDITION DESCRIPTION/LOCATION (THE INAPPROPRIATE ACTION AND ITS NEGATIVE EFFECT/INCLUDE A DETAILED LOCATION DESCRIPTION): * After pump 17B was serviced under work order 90232847 and put back into operation, a noticeable drop in pressure was observed. The pump's pressure was measured to be 10 psi below usual operating parameters.This was discovered during a routine operations check-up. Further observation indicates no external leaks or physical damages. * * ACTIVITIES, PROCESSES, PROCEDURES INVOLVED: * Routine operational checks post service, S1.OP.AB.CW-0002 * * WHY DID CONDITION HAPPEN: * The cause for the pressure drop is unknown. Potentially due to a discrepancy during the overhaul process. * * CONSEQUENCES: * Decreased pump efficiency and potential damage if run at lower pressure for extended periods. * * REQUIREMENTS IMPACTED: * Normal operational requirements of 17B pump * * ADVERSE PHYSICAL CONDITIONS: * Lower than normal pressure in the pump * * WHO WAS NOTIFIED: * Supervisor and Service Team * * KNOWLEDGEABLE INDIVIDUALS: * Linda Evans, Service Team, Operations Lead * * REPEAT OR SIMILAR CONDITION: * No identical previous incidents. However, similar pressure issues have been observed on different units. * * IMMEDIATE ACTIONS AND RECOMMENDED ACTIONS: * Investigations team to thoroughly inspect the pump and rectify any anomalies. Future overhauls should be closely monitored. * * 05/04/2019 10:05:40 LINDA EVANS (INCIDENT) * The immediate remedial action is being taken to inspect and rectify the pressure drop. Pump 17B will be closely monitored after reinstating to normal operations. | What was the observed issue with Pump 17B after it was put back into operation? | After pump 17B was serviced under work order 90232847 and put back into operation, a noticeable drop in pressure was observed. The pump's pressure was measured to be 10 psi below usual operating parameters.
62 | 2017-10-30 | 30888239 | 80218901 | Abnormal Temperature of Generator 16B | S4GH -4GHDE5 | * **************Incident Description************** * Notification 000030888239 Details * *********************************************************** * 10/30/2017 14:45:00 INCIDENT REPORT (INCIDENT REPORT) * Report submitted by: Laura Green ENTITY\INCIDENT: * * CONDITION DESCRIPTION/LOCATION (THE INAPPROPRIATE ACTION AND ITS NEGATIVE EFFECT/INCLUDE A DETAILED LOCATION DESCRIPTION): * During the regular inspection, abnormal temperature was identified on Generator 16B. The reading was 32% above the average temperature recorded during normal operation. Actions were taken immediately to shut down the generator and start a detailed examination. * * ACTIVITIES, PROCESSES, PROCEDURES INVOLVED: * Regular monitoring activities, normal operating procedure S4.OP-AB.GH-0002, routine maintenance. * * WHY DID CONDITION HAPPEN? * Preliminary assessment suggests possible internal mechanical issue or inadequate lubrication. Further examination is required to pinpoint the cause. * * CONSEQUENCES: * Risk of significant damage to the generator if continued to operate at abnormal temperature. * * REQUIREMENTS IMPACTED: * Potential disruption in power generation. * * ADVERSE PHYSICAL CONDITIONS: * Abnormal temperature reading from Generator 16B, potentially indicating an internal failure. * * WHO WAS NOTIFIED: * Operations Manager, Maintenance Team, Safety Officer * * KNOWLEDGEABLE INDIVIDUALS: * Maintenance Team, Safety Officer, Operations Manager * * REPEAT OR SIMILAR CONDITION: * No, this is the first occurrence. * * IMMEDIATE ACTIONS AND RECOMMENDED ACTIONS: * Shut down the generator to prevent any collateral damage and started the emergency inspection with priority. If the issue persists, may require maintenance or replacement of parts. * 11/01/2017 10:45:37 JOHN DOE (INSPECTION) * The abnormal temperature was due to a minor internal failure in the cooling system. The issue has been rectified and the generator is now back to normal operation with ongoing monitoring to prevent similar incidents. | What was the cause of the abnormal temperature in Generator 16B? | The abnormal temperature was due to a minor internal failure in the cooling system.
63 | 2016-09-17 | 30765431 | 80210456 | Unexpected low pressure in Pump 19A | S4CW -4CWE7 | * **************Incident Description************** * Notification 000030765431 Details * *********************************************************** * 09/17/2016 14:19:30 INCIDENT REPORT (INCIDENT REPORT) * Report submitted by: Emily Foster ENTITY\INCIDENT: * * CONDITION DESCRIPTION/LOCATION (THE INAPPROPRIATE ACTION AND ITS NEGATIVE EFFECT/INCLUDE A DETAILED LOCATION DESCRIPTION): * During necessary hourly checks, it was found that 19A Pump had unexpectedly lower pressure. The pressure measured was 10 psig below the standard value. No obvious external factors contributing to drop in pressure were identified. * * ACTIVITIES, PROCESSES, PROCEDURES INVOLVED: * Routine maintenance check, S4.OP-AB.CW-0002 * * WHY DID CONDITION HAPPEN? * Unclear, possible internal damage in the pump or issue with the control system. * * CONSEQUENCES: * Reduced efficiency and potential risk of shut down if the situation persists. * * REQUIREMENTS IMPACTED: * Normal operation of 19A Pump. * * ADVERSE PHYSICAL CONDITIONS: * Suppressed pressure level at Pump 19A * * WHO WAS NOTIFIED: * Plant Supervisor and Engineering department * * KNOWLEDGEABLE INDIVIDUALS: * Supervisor, Engineering department, and Maintenance team * * REPEAT OR SIMILAR CONDITION: * No, this is a first-time incident. * * IMMEDIATE ACTIONS AND RECOMMENDED ACTIONS: * Detailed inspection and diagnostic tests needed to determine the exact cause of the pressure drop. If necessary, engineering may need to revise procedures involving the pump. * 09/20/2016 08:43:52 EMILY FOSTER (INCIDENT) * Inspection determined an internal seal had broken causing the pressure drop. Replacement parts were ordered and the pump operation has normalized post-repair. We recommend reviewing routine checks to ensure this issue is spotted more quickly in future. | What immediate actions were taken following the incident with the 19A Pump? | Detailed inspection and diagnostic tests needed to determine the exact cause of the pressure drop. If necessary, engineering may need to revise procedures involving the pump.
64 | 2016-10-30 | 30750349 | 80210347 | Pressure Drop in 14B Pump | S4CW -4CWE5 | * **************Incident Description************** * Notification 000030750349 Details * *********************************************************** * 10/30/2016 13:45:00 INCIDENT REPORT (INCIDENT REPORT) * Report submitted by: William Howard 567-890-1234 * ENTITY\INCIDENT: * CONDITION DESCRIPTION/LOCATION (THE INAPPROPRIATE ACTION AND ITS NEGATIVE EFFECT/INCLUDE A DETAILED LOCATION DESCRIPTION): * During normal operation, 14B Pump showed an unexpected pressure drop. The pump pressure was checked and was seen to drop to 9 psig, lower than the normal operational values. This incident occurred in the early hours during the third shift. Pending further investigation, the 14B Pump was taken offline. * * ACTIVITIES, PROCESSES, PROCEDURES INVOLVED: * Normal operation, S4.OP-AB.PM-0003, S4.OP-SO.PM-0008 * * WHY DID CONDITION HAPPEN? * Unknown, possible blockage or mechanical fault within the pump. * * CONSEQUENCES: * Possible equipment damage and loss of efficiency due to low pressure. * * REQUIREMENTS IMPACTED: * Normal pump operation is compromised. * * ADVERSE PHYSICAL CONDITIONS: * Pressure lower than operation standard. * * WHO WAS NOTIFIED: * Shift Supervisor/ INCIDENT TEAM * * KNOWLEDGEABLE INDIVIDUALS: * Wilson, Cox, Rogers * * REPEAT OR SIMILAR CONDITION: * No previous records of similar incidents. * * IMMEDIATE ACTIONS AND RECOMMENDED ACTIONS: * Conduct thorough investigation of 14B Pump. If necessary, remove and replace. * 10/30/2016 16:23:42 WILLIAM HOWARD (INCIDENT) * In consultation with the supervisor, it was decided to undertake an immediate inspection of the 14B pump to determine the cause of the low pressure. Further action will be dependent upon the findings of this inspection. | What immediate action was recommended after the 14B pump showed an unexpected pressure drop? | Conduct thorough investigation of 14B Pump. If necessary, remove and replace.
65 | 2020-11-13 | 40720584 | 90189235 | 11B Pump High Vibration rate | S4CW -4CWE2 | * **************Incident Description************** * Notification 000040720584 Details * *********************************************************** * 11/13/2020 08:29:00 INCIDENT REPORT (INCIDENT REPORT) * Report Submitted by: Maxwell Edison 180-543-7869 * ENTITY\INCIDENT * * CONDITION DESCRIPTION/LOCATION (THE INAPPROPRIATE ACTION AND ITS NEGATIVE EFFECT/INCLUDE A DETAILED LOCATION DESCRIPTION): * During regular inspection, the operator noticed unusual high vibrations on 11B Pump. Vibration levels have been escalating slowly for past 4 days. This pump typically operates with much lower vibration. This could potentially mean internal wear or damage to the system. * * ACTIVITIES, PROCESSES, PROCEDURES INVOLVED: * Regular inspection, operational procedure S4.OP-SO.CW-0013 * * WHY DID CONDITION HAPPEN? * Unknown, potential internal wear or damage seems likely. * * CONSEQUENCES: * Increased risk of pump failure, potentially leading to an operational shutdown which could affect efficiency and output * * REQUIREMENTS IMPACTED: * Regular operation setup, potential output loss. * * ADVERSE PHYSICAL CONDITIONS: * High vibration rates observed on 11B pump * * WHO WAS NOTIFIED: * Plant Supervisor, Maintenance team * * KNOWLEDGEABLE INDIVIDUALS: * Maintenance Team * * REPEAT OR SIMILAR CONDITION: * No, this is the first such incident related to this. * * IMMEDIATE ACTIONS AND RECOMMENDED ACTIONS: * Engineering team to investigate 11B Pump vibrations. * 11/15/2020 13:55:18 MAXWELL EDISON (INCIDENT) * The investigation shows that the bearings were worn out, causing the unusual vibration. The pump was shut down, and the bearings were replaced. The pump is back in operation with normal vibration. We recommend regular monitoring to this case. | What was the cause of the high vibrations on the 11B pump and what immediate actions were taken? | The investigation shows that the bearings were worn out, causing the unusual vibration. The pump was shut down, and the bearings were replaced. The pump is back in operation with normal vibration.
66 | 2016-09-21 | 30785123 | 80193876 | 25B pump unusual vibration post repair | S3CW -3CWE8 | * **************Incident Description************** * Notification 000030785123 Details * *********************************************************** * 09/21/2016 11:15:14 INCIDENT REPORT (INCIDENT REPORT) * Report submitted by: Tyler Johnson ENTITY\INCIDENT: * * CONDITION DESCRIPTION/LOCATION (THE INAPPROPRIATE ACTION AND ITS NEGATIVE EFFECT/INCLUDE A DETAILED LOCATION DESCRIPTION): * Following a recent repair under work order 80193876, the 25B pump has been experiencing unusual vibrations during operation. This is a deviation from its normal operational characteristics and may indicate an issue with the pump alignment or imbalance in the rotor. * * ACTIVITIES, PROCESSES, PROCEDURES INVOLVED: * Equipment monitoring and evaluation of operational characteristics following a repair * * WHY DID CONDITION HAPPEN? * Possibly due to incorrect alignment or imbalance during repair process. * * CONSEQUENCES: * Potential damage to pump components, reduced efficiency, potential system failure. * * REQUIREMENTS IMPACTED: * Normal operation, system reliability. * * ADVERSE PHYSICAL CONDITIONS: * Unusual vibration at pump. * * WHO WAS NOTIFIED: * Supervisory staff and maintenance team. * * KNOWLEDGEABLE INDIVIDUALS: * Maintenance Team and operational staff familiar with 25B pump. * * REPEAT OR SIMILAR CONDITION: * No, this is the first occurrence post repair. * * IMMEDIATE ACTIONS AND RECOMMENDED ACTIONS: * Initiate a thorough inspection and realignment if necessary, and ensure the balance of the pump rotor is checked. If vibration persists, further detailed analysis may be required. * 09/23/2016 14:36:42 Tyler Johnson (INCIDENT) * Pump inspection conducted, minor misalignment detected. Subsequent adjustment appears to have resolved the issue. Continued monitoring has been recommended as a precaution. The issue will be further investigated to implement a more stable alignment process during future repairs. | What were the immediate and recommended actions after the issue with the pump was recognized? | Initiate a thorough inspection and realignment if necessary, and ensure the balance of the pump rotor is checked. If vibration persists, further detailed analysis may be required.
67 | 2017-09-18 | 30757891 | 80523456 | Irregular vibration from 11B pump | S4CW -4CWE2 | * **************Incident Description************** * Notification 000030757891 Details * *********************************************************** * 09/18/2017 13:37:00 INCIDENT REPORT (INCIDENT REPORT) * Report submitted by: Samantha Williams ENTITY\INCIDENT: * * CONDITION DESCRIPTION/LOCATION (THE INAPPROPRIATE ACTION AND ITS NEGATIVE EFFECT/INCLUDE A DETAILED LOCATION DESCRIPTION): * During a regular daily inspection, irregular vibrating movement was noticed from pump 11B. Pump operation was ceased and an investigation was initiated. Preliminary examination did not reveal any obvious issues. * * ACTIVITIES, PROCESSES, PROCEDURES INVOLVED: * S4.OP.AB-CW-0003, S4.MNT.AB.CW.0002 * * WHY DID CONDITION HAPPEN? * Unknown. A more detailed investigation, possibly involving partial disassembly, may be necessary. * * CONSEQUENCES: * Potential severe motor and pump damage if operation continued unnoticed. * * REQUIREMENTS IMPACTED: * Normal operation. * * ADVERSE PHYSICAL CONDITIONS: * Excessive vibration of 11B pump motor. * * WHO WAS NOTIFIED: * Supervisor, Maintenance Team. * * KNOWLEDGEABLE INDIVIDUALS: * Supervisor, Maintenance Team, Williams and Bradshaw. * * REPEAT OR SIMILAR CONDITION: * Not known at this time. * * IMMEDIATE ACTIONS AND RECOMMENDED ACTIONS: * Initiate S4.OP.AB.CW-0003 and if necessary, S4.MNT.AB.CW.0002 to determine the cause of irregular vibration. Consider preemptive inspection of similar pumps. * 09/20/2017 08:34:47 SAMANTHA WILLIAMS (MAINTENANCE) * A detailed investigation revealed a misalignment in the pump assembly post recent service work. This has been rectified and following tests showed normal operation. Therefore, the pump was put back online. | What was the adverse physical condition noticed in the 11B pump motor? | Excessive vibration of 11B pump motor.
68 | 2018-10-14 | 30890312 | 80234507 | Excessive vibration at PUMP MOTOR 16D | S4CW -4CWE7-MTRA | * **************Incident Description************** * Notification 000030890312 Details * *********************************************************** * SUMMARY: REVIEWING COMPLIANCE IN * ****PS-AA-120 "ISSUE IDENTIFICATION AND SCREENING PROCESS"***** * * 1) CONDITION DESCRIPTION/LOCATION: * At 1035 on 10/14/18, the technician noted excessive vibration coming from the 16D pump motor. The 16D pump was immediately turned off from Unit 4 Control Room. A follow-up inspection by the Maintenance Team did not show any visible damage but there was a noticeably high reading on the vibration meter. The pump in question was compared to others in operation and it showed a significantly higher vibration level. S4.OP-AB.CW-0001 Pump Abnormal Activity protocol was initiated due to this discovery. * * 2) ACTIVITIES, PROCESSES, PROCEDURES INVOLVED: * S4.OP.AB-CW-0003, S4.OP-SO.CW-0004 * * 3) WHY DID CONDITION HAPPEN: * As of now, it is unknown, although similar instances have been reported in the past. * * 4) CONSEQUENCES: * Vibration could result in premature wear and subsequent failure of the pump, resulting in costly repairs and potential operational downtime. * * 5) REQUIREMENTS IMPACTED: * Usability of pump * * 6) ADVERSE PHYSICAL CONDITION: * Excessive vibration at 16D Pump motor, potential internal damage. * * 7) WHO WAS NOTIFIED: * Maintenance Supervisor, Control Room * * 8) KNOWLEDGEABLE INDIVIDUALS: * Anderson, Miller, Thompson * * 9) REPEAT OR SIMILAR CONDITION: * Yes, multiple instances have been reported. * * 10) IMMEDIATE AND RECOMMENDED ACTIONS: * Maintenance team to further inspect 16D Pump Motor. * * Updated: JOHN DOE 10.14.2018 16:24:09 * ------------------------------------------------------------- * 11/19/2018 10:15 | What was the immediate response taken following the discovery of the excessively vibrating 16D pump motor? | The 16D pump was immediately turned off from Unit 4 Control Room. A follow-up inspection by the Maintenance Team did not show any visible damage but there was a noticeably high reading on the vibration meter. S4.OP-AB.CW-0001 Pump Abnormal Activity protocol was initiated due to this discovery.
69 | 2020-10-11 | 40011234 | 80246872 | Inconsistent pressure in 32B pump | S4CW -4CWE3 | * **************Incident Description************** * Notification 000040011234 Details * *********************************************************** * 10/11/2020 15:12:23 INCIDENT REPORT (INCIDENT REPORT) * Report submitted by: William Johnson ENTITY\INCIDENT: * * CONDITION DESCRIPTION/LOCATION (THE INAPPROPRIATE ACTION AND ITS NEGATIVE EFFECT/INCLUDE A DETAILED LOCATION DESCRIPTION): * During the evening operational shift, 32B pump exhibited inconsistent pressure readings. Despite calm weather conditions and standard operations, the pressure readings fluctuated outside of the usual thresholds. Previous reports have suggested this may indicate an approaching failure or malfunction. * * ACTIVITIES, PROCESSES, PROCEDURES INVOLVED: * Regular monitoring and operational procedures. * * WHY DID CONDITION HAPPEN? * Unknown, possible mechanical issues or sensor malfunctions. * * CONSEQUENCES: * It could potentially lead to unwanted shutdown, operational inefficiency, or undetected mechanical failure. * * REQUIREMENTS IMPACTED: * Regular monitoring and operations * * ADVERSE PHYSICAL CONDITIONS: * Inconsistent pressure readings in the 32B pump * * WHO WAS NOTIFIED: * Operation Supervisor, Maintenance Unit * * KNOWLEDGEABLE INDIVIDUALS: * Operators Team, Maintenance Unit, Engineering team * * REPEAT OR SIMILAR CONDITION: * No, It's the first issue of it's kind with the 32B pump * * IMMEDIATE ACTIONS AND RECOMMENDED ACTIONS: * Engineering and Maintenance to conduct an immediate investigation and detailed inspection of the 32B pump. Review of sensor readings should also be included. * 10/13/2020 08:21:34 JANE DOE (INCIDENT) * The detailed investigation revealed a software issue causing the erratic pressure reading. A software patch was applied that seems to have rectified the problem. The pump will be closely monitored during the upcoming operations to confirm the issue has been resolved. | What was the identified cause for inconsistent pressure readings in the 32B pump? | The detailed investigation revealed a software issue causing the erratic pressure reading.
70 | 2022-05-30 | 30978243 | 80359782 | 17B compressor system pressure drop | S4CW -4CWE9 | * **************Incident Description************** * Notification 000030978243 Details * *********************************************************** * 05/30/2022 15:32:00 INCIDENT REPORT (INCIDENT REPORT) * Report submitted by: Marty Thompson ENTITY\INCIDENT: * * CONDITION DESCRIPTION/LOCATION (THE INAPPROPRIATE ACTION AND ITS NEGATIVE EFFECT/INCLUDE A DETAILED LOCATION DESCRIPTION): * During the 05/29/22 shift, it was observed that the 17B Compressor system started displaying abnormal pressure readings. An unexpected pressure drop was noted in the compressor system. An immediate decision was made to shutdown the compressor for safety. There was no evident sign of external damage or leakage. * * ACTIVITIES, PROCESSES, PROCEDURES INVOLVED: * S4.OP.AB-CW-0008, S4.OP-SI.CW-0009 * * WHY DID CONDITION HAPPEN? * The reason remains uncertain and needs to be investigated. However, historical reports show such a condition can be caused by a blocked line or system failure. * * CONSEQUENCES: * The abrupt drop in pressure could potentially damage the whole compressor system and reduce the system efficiency. * * REQUIREMENTS IMPACTED: * Compressor system operation and runtime efficiency. * * ADVERSE PHYSICAL CONDITIONS: * Pressure drop in the compressor system with unknown cause. * * WHO WAS NOTIFIED: * The Control Room Operator, the maintenance team. * * KNOWLEDGEABLE INDIVIDUALS: * Patterson, Hill, Matthews. * * REPEAT OR SIMILAR CONDITION: * Not to the best of our knowledge. * * IMMEDIATE ACTIONS AND RECOMMENDED ACTIONS: * Immediate maintenance inspection is required to identify the issue. In the meantime, an alternate compressor should be employed. * 06/01/2022 08:45:18 MARTY THOMPSON (INCIDENT) * After a detailed inspection, it was found that a compressor inlet line was blocked leading to the pressure drop. The blockage has been cleared and the system has resumed normal operations with correct pressure readings. Monitoring will continue to ensure no further issues. | What was the immediate action taken after observing abnormal pressure readings in the 17B Compressor system? | An immediate decision was made to shutdown the compressor for safety.
71 | 2020-10-10 | 30982054 | 90088645 | Overheating of 18B cooling pump | S2CW -4CWE1 | * **************Incident Description************** * Notification 000030982054 Details * *********************************************************** * 10/10/2020 08:27:10 INCIDENT REPORT (INCIDENT REPORT) * Report submitted by: James Richardson ENTITY\INCIDENT: * * CONDITION DESCRIPTION/LOCATION (THE INAPPROPRIATE ACTION AND ITS NEGATIVE EFFECT/INCLUDE A DETAILED LOCATION DESCRIPTION): * At 0827 on 10/10/20, unusual heat was detected at the 18B cooling pump during routine maintenance inspection. The pump was immediately shut down to prevent further damage. No fire or smoke was detected but the heat signature exceeded normal operation parameters. Further inspection is needed to determine the cause. * * ACTIVITIES, PROCESSES, PROCEDURES INVOLVED: * Routine maintenance inspection. * * WHY DID CONDITION HAPPEN? * Undetermined at the moment, however, previous incidents suggest the possible cause could be equipment failure or blockage. * * CONSEQUENCES: * Potential damage to the pump, which could lead to production delay or issues related to cooling. * * REQUIREMENTS IMPACTED: * Normal operation of the pump is interrupted. * * ADVERSE PHYSICAL CONDITIONS: * Significant heat generation from 18B cooling pump. * * WHO WAS NOTIFIED: * Operations Engineer/ Incident Team * * KNOWLEDGEABLE INDIVIDUALS: * Incident Team, On-site technicians * * REPEAT OR SIMILAR CONDITION: * Yes, similar events have been reported previously. * * IMMEDIATE ACTIONS AND RECOMMENDED ACTIONS: *Immediate shut down of pump and notify Incident Team, technical analysis of the cause and replacement of the faulty part, if necessary. * 10/12/2020 10:45:20 JAMES RICHARDSON (INCIDENT) * Technicians have confirmed that the cause of the overheating was due to a faulty bearing in the pump. The part is being replaced and the pump is expected to be back to normal operation shortly. | What was the identified cause for the unusual heat detected at the 18B cooling pump? | Technicians have confirmed that the cause of the overheating was due to a faulty bearing in the pump.
72 | 2016-09-18 | 30873420 | 80256743 | Leak from 12C Pump | S2CW -3CWE5 | * **************Incident Description************** * Notification 000030873420 Details * *********************************************************** * 09/18/2016 13:35:44 INCIDENT REPORT (INCIDENT REPORT) * Report submitted by: George Foster ENTITY\INCIDENT: * CONDITION DESCRIPTION/LOCATION (THE INAPPROPRIATE ACTION AND ITS NEGATIVE EFFECT/INCLUDE A DETAILED LOCATION DESCRIPTION): * During the afternoon, around 1335, routine inspection revealed a leak from the 12C Pump. The leakage was steady and an adjacent puddle indicated it had been leaking for some time. There was no immediate danger, but if left unattended the problem could worsen. * * ACTIVITIES, PROCESSES, PROCEDURES INVOLVED: * Routine check * * WHY DID CONDITION HAPPEN? * Unknown, possibly due to a worn out seal or component failure. * * CONSEQUENCES: * Potential reduction in pump efficiency, water wastage, possible flooding * * REQUIREMENTS IMPACTED: * Normal operation * * ADVERSE PHYSICAL CONDITIONS: * Leak from 12C Pump * * WHO WAS NOTIFIED: * Maintenance Supervisor * * KNOWLEDGEABLE INDIVIDUALS: * Maintenance Team * * REPEAT OR SIMILAR CONDITION: * Yes, past leaks have occurred on other pumps. * * IMMEDIATE ACTIONS AND RECOMMENDED ACTIONS: * Stop the pump, drain, and investigate source of leak. Replace any faulty components. * 09/20/2016 10:10:30 SAMUEL TAYLOR (MAINTENANCE) * The leak has been fixed. A worn out seal was replaced and the motor is now operating within normal parameters. | What was the immediate and recommended action after discovering the leak in the 12C Pump? | Stop the pump, drain, and investigate source of leak. Replace any faulty components.
73 | 2017-09-15 | 30878135 | 80211723 | Overheating of the 44D Pump motor | S3CW -3CWE12 | * **************Incident Description************** * Notification 000030878135 Details * *********************************************************** * 09/15/2017 07:47:30 INCIDENT REPORT (INCIDENT REPORT) * Report submitted by: William Johnson ENTITY\INCIDENT: * * CONDITION DESCRIPTION/LOCATION (THE INAPPROPRIATE ACTION AND ITS NEGATIVE EFFECT/INCLUDE A DETAILED LOCATION DESCRIPTION): * At 0740 hours on 15/09/17, monitor alarms indicated an overheating incident with the 44D Pump motor, which was shut down for prevention from causing internal damage. Preliminary inspection didn't reveal a fire or visible external damage. However, a scent indicative of heated wiring insulation was registered by attending engineers. The overheating issue is similar to prior incidents involving other pump motors. * * ACTIVITIES, PROCESSES, PROCEDURES INVOLVED: * Monitoring system alert, immediate preventive shutdown - S3.OP.AB.CW-0008, S3.OP-SO.CW-0002 * * WHY DID CONDITION HAPPEN? * Uncertain. Similar incidents of motor overheating have been observed before. * * CONSEQUENCES: * The pump motor might experience future efficiency loss, plus the unavailability of the pump during the downtime. * * REQUIREMENTS IMPACTED: * Pump availability is compromised * * ADVERSE PHYSICAL CONDITIONS: * Potential internal damage to the motor due to overheating, odor indicative of heated insulation * * WHO WAS NOTIFIED: * Operations Unit, Fire Department * * KNOWLEDGEABLE INDIVIDUALS: * Rogers, Frank, Wilson * * REPEAT OR SIMILAR CONDITION: * Yes, past incidences with other pump motors. * * IMMEDIATE ACTIONS AND RECOMMENDED ACTIONS: * Assign a maintenance team for comprehensive inspection of 44D Pump Motor. * 09/20/2017 14:20:51 MARK ROGERS (MAINTENANCE) * Upon inspection, it was discovered that a faulty cooling fan was causing the overheating. The fan has been replaced, and the motor | What was discovered to be the cause of the 44D Pump motor overheating? | Upon inspection, it was discovered that a faulty cooling fan was causing the overheating.
74 | 2022-10-15 | 30732850 | 80204768 | Leaking from 15B pump post-repair | S4CW -4CWE3 | * **************Incident Description************** * Notification 000030732850 Details * *********************************************************** * 10/15/2022 08:15:00 INCIDENT REPORT (INCIDENT REPORT) * Report submitted by: Barbara Green ENTITY\INCIDENT: * * CONDITION DESCRIPTION/LOCATION (THE INAPPROPRIATE ACTION AND ITS NEGATIVE EFFECT/INCLUDE A DETAILED LOCATION DESCRIPTION): * Maintenance activities for 15B Pump under work order 80204768 were completed last night. This morning, it was noticed that the pump is leaking from a joint. Joint was tightened post-maintenance, but the issue persists. The maintenance team was alerted, and temporary containment measures were implemented. * * ACTIVITIES, PROCESSES, PROCEDURES INVOLVED: * Pump repair and joint tightening under work order 80204768. * * WHY DID CONDITION HAPPEN? * Possibly inadequate tightening or a faulty joint. * * CONSEQUENCES: * Risk of slip or fall, potential equipment damage, inefficiency in operation * * REQUIREMENTS IMPACTED: * Safe operation, environmental compliance * * ADVERSE PHYSICAL CONDITIONS: * Leaking fluid from 15B pump joint * * WHO WAS NOTIFIED: * Maintenance Supervisor, Site Safety Officer, Environmental Compliance * * KNOWLEDGEABLE INDIVIDUALS: * Maintenance Team, Safety Officer * * REPEAT OR SIMILAR CONDITION: * No, this is the first time this issue has been reported. * * IMMEDIATE ACTIONS AND RECOMMENDED ACTIONS: * Temporary containment measures implemented, notification to be issued to maintenance team for further investigation and repair. Procedure review is recommended. * 10/15/2022 10:43:09 BARBARA GREEN (INCIDENT) * The maintenance team is onsite and has started investigation. Immediate measures have been put in place to stop further leak. Updates to be provided as more information becomes available. | Why did the leakage issue occur with the 15B pump after maintenance activities? | Possibly inadequate tightening or a faulty joint.
75 | 2020-10-18 | 30991234 | 80262749 | Overpressure SAF32-HVC | P4HV -2SH-HVC | * *************Incident Description************** * Notification 000030991234 Details * *********************************************************** * 10/18/2020 15:40:23 INCIDENT REPORT (INCIDENT REPORT) * Report submitted by: John Harper ENTITY\ INCIDENT: * * CONDITION DESCRIPTION/LOCATION (THE INAPPROPRIATE ACTION AND ITS NEGATIVE EFFECT/ INCLUDE A DETAILED LOCATION DESCRIPTION): * Alarm received at 1510, overpressure condition on SAF32-HVC. Operators at site confirmed to be an overpressure condition and the system was manually shut down. Upon further inspection, initial suspicion indicating a stuck open control valve. Pump was isolated and the control valve will be serviced. * * ACTIVITIES, PROCESSES, PROCEDURES INVOLVED: * P4.OP.AB-HV-0002, P4.OP-AB.HV-0001 * * WHY DID CONDITION HAPPEN? * Preliminary inspection suggests a faulty control valve. However, a complete pump inspection will be initiated to conclusively determine. * * CONSEQUENCES: * Overpressure can lead to equipment damage, affecting system's normal operation. * * REQUIREMENTS IMPACTED: * System availability, functional status of control valve * * ADVERSE PHYSICAL CONDITIONS: * Stuck open control valve, pump shutdown, overpressure condition * * WHO WAS NOTIFIED: * Incident Team, Operations Supervisor. * * KNOWLEDGEABLE INDIVIDUALS: * Incident Team, Jillian Rodrigues, Steve Reynolds. * * REPEAT OR SIMILAR CONDITION: * Yes, was observed earlier this year. * * IMMEDIATE ACTIONS AND RECOMMENDED ACTIONS: * Investigate control valve: scheduled maintenance to verify whether the valve is the cause, or if the problem is originating from elsewhere. Update emergency shutdown procedure to incorporate a troubleshooting guide. * 10/19/2020 11:35:42 JILL RODRIGUES (INCIDENT) * The control valve was replaced, pump restarted and back at normal operating pressure. Recommended updating preventive maintenance program for control valves. | What immediate and recommended actions were taken following the incident? | Investigate control valve: scheduled maintenance to verify whether the valve is the cause, or if the problem is originating from elsewhere. Update emergency shutdown procedure to incorporate a troubleshooting guide. The control valve was replaced, pump restarted and back at normal operating pressure. Recommended updating preventive maintenance program for control valves.
76 | 2018-01-05 | 30815903 | 80236900 | 18B Pump Abnormal Vibration | S4CW -4CWE2 | * ************** Incident Description ************** * Notification 000030815903 Details * *********************************************************** * 01/05/2018 10:23:13 INCIDENT REPORT (INCIDENT REPORT) * Report submitted by: Mark Adams ENTITY\INCIDENT: * * CONDITION DESCRIPTION/LOCATION (THE INAPPROPRIATE ACTION AND ITS NEGATIVE EFFECT/INCLUDE A DETAILED LOCATION DESCRIPTION): * * During the morning shift, unusual vibration was detected at 18B Pump. Pump was immediately taken offline as a precautionary measure. No leak or temperature rise was observed. The pump was last serviced in December 2017 under work order number 80236900. * * ACTIVITIES, PROCESSES, PROCEDURES INVOLVED: * S4.OP-AB.CW-0002, S4.OP-SO.CW-0002 * * WHY DID CONDITION HAPPEN: * Still unknown. Investigation is in progress. It may be due to a mechanical failure or imbalance due to maintenance performed. * * CONSEQUENCES: * Potential pump failure and decreased efficiency. * * REQUIREMENTS IMPACTED: * Maintaining pump functionality, Cancelled schedule maintenance. * * ADVERSE PHYSICAL CONDITIONS: * Abnormal vibration of 18B Pump with unknown cause. * * WHO WAS NOTIFIED: * Maintenance Supervisor, Management * * KNOWLEDGEABLE INDIVIDUALS: * Maintenance Team * * REPEAT OR SIMILAR CONDITION: * No, first ever case reported of unusual vibration on this pump * * IMMEDIATE ACTIONS AND RECOMMENDED ACTIONS: * Maintenance team to investigate the cause and rectify it ASAP. The pump will stay offline until the issue is identified and corrected. * 01/05/2018 14:34:21 MARK ADAMS (INCIDENT) * Preliminary report from the maintenance team suggests possible imbalance of one of the pump components, detailed examination is required. | What immediate action was taken when the unusual vibration was detected at the 18B Pump? | Pump was immediately taken offline as a precautionary measure.
77 | 2020-10-19 | 30938507 | 80234512 | Unusual noise from compressor C6H | S4CW -4CWE8 | * **************Incident Description************** * Notification 000030938507 Details * *********************************************************** * 10/19/2020 07:15:00 INCIDENT REPORT (INCIDENT REPORT) * Report submitted by: Samuel Peterson ENTITY\INCIDENT: * * CONDITION DESCRIPTION/LOCATION (THE INAPPROPRIATE ACTION AND ITS NEGATIVE EFFECT/INCLUDE A DETAILED LOCATION DESCRIPTION): * During routine inspections on 10/19/2020, the maintenance team noticed an unusual, loud grinding noise coming from the compressor C6H. Initial investigations conducted by the maintenance team did not reveal any immediate signs of physical damage but considering the persistence of the noise, there are concerns about potential internal issues. * * ACTIVITIES, PROCESSES, PROCEDURES INVOLVED: * Routine inspections, S4.OP-AB.CW-0002, S4.OP-SO.CW-0002 Procedures * * WHY DID CONDITION HAPPEN? * Exact cause is presently unclear, potential for internal component deterioration, it needs an investigation. * * CONSEQUENCES: * If left unchecked, potential for serious compressor failure, forcing a stop in operations. * * REQUIREMENTS IMPACTED: * Normal operation * * ADVERSE PHYSICAL CONDITIONS: * Persistent unusual noise from compressor with no clear source. * * WHO WAS NOTIFIED: * Supervisor, Inspection Team * * KNOWLEDGEABLE INDIVIDUALS: * Inspection Team, Johnson, Lee * * REPEAT OR SIMILAR CONDITION: * Yes, minor occurrences in the past. * * IMMEDIATE ACTIONS AND RECOMMENDED ACTIONS: * Compressor should be scheduled for a comprehensive check-up. If required, replacement of parts to be planned post report of the check-up. * 10/19/2020 09:51:28 SAMUEL PETERSON (INCIDENT) * Update: Compressor C6H has been scheduled for a detailed inspection to better understand the cause of the noise. This will help avoid any unforeseen circumstances and ensure the smooth functioning of operations. | What immediate actions were recommended after the discovery of the noise in the compressor C6H? | Compressor should be scheduled for a comprehensive check-up. If required, replacement of parts to be planned post report of the check-up.
78 | 2020-05-27 | 30827063 | 80237456 | 30B Pump low fluid flow | S4CW -4CWE7 | * **************Incident Description************** * Notification 000030827063 Details * *********************************************************** * 05/27/2020 07:33:11 INCIDENT REPORT (INCIDENT REPORT) * Report submitted by: Dan Anderson ENTITY\INCIDENT: * * CONDITION DESCRIPTION/LOCATION (THE INAPPROPRIATE ACTION AND ITS NEGATIVE EFFECT/INCLUDE A DETAILED LOCATION DESCRIPTION): * During periodic monitoring, it was observed that the 30B Pump exhibited lower than normal fluid flow rates. The pump was working at only 70% of its capacity which is not typical for this unit. * * ACTIVITIES, PROCESSES, PROCEDURES INVOLVED: * Routine monitoring of pump performance. * * WHY DID CONDITION HAPPEN? * Cause of the condition is still unclear, possible factors might include component wear, blockage or improper calibration. * * CONSEQUENCES: * Reduced performance may lead to less efficient operation and increased operational stress on other units in the network. * * REQUIREMENTS IMPACTED: * The pump’s ability to maintain required fluid flow rates. * * ADVERSE PHYSICAL CONDITIONS: * Lower than usual fluid flow in 30B Pump. * * WHO WAS NOTIFIED: * Maintenance Supervisor, Engineer team. * * KNOWLEDGEABLE INDIVIDUALS: * Maintenance Supervisor, Engineer team. * * REPEAT OR SIMILAR CONDITION: * No, this is the first occurrence on this pump. * * IMMEDIATE ACTIONS AND RECOMMENDED ACTIONS: * Carry out immediate inspection and maintenance work on the 30B Pump as necessary. Check for signs of wear, blockage and verify calibration. * 05/30/2020 13:49:03 DAN ANDERSON (INCIDENT) * Upon maintenance check, we found that the drop in the fluid flow was due to obstruction in the pump. The object causing the obstruction was removed, and the pump is operating at full capacity. | What was the immediate action recommended when the lower than normal fluid flow rates in the 30B Pump were observed? | Carry out immediate inspection and maintenance work on the 30B Pump as necessary. Check for signs of wear, blockage and verify calibration.
79 | 2020-03-15 | 50040630 | 90568245 | Anomaly in hydraulic pressure S4 -4HPR2 |  | * **************Incident Description************** * Notification 000050040630 Details * *********************************************************** * 03/15/2020 14:25:30 INCIDENT REPORT (INCIDENT REPORT) * Report submitted by: Robert James 987-654-3210 ENTITY\INCIDENT: * * CONDITION DESCRIPTION/LOCATION (THE INAPPROPRIATE ACTION AND ITS NEGATIVE EFFECT/INCLUDE A DETAILED LOCATION DESCRIPTION): * At 1325 hours on 15/03/20, a hydraulic pressure anomaly was detected in the S4 system. The hydraulic pressure dropped from standard operating level of 98 bar to 89 bar. The pressure difference is unusual and is not typical based on historical data reviews. * * ACTIVITIES, PROCESSES, PROCEDURES INVOLVED: * S4.SP.AB-PH-0002, S4.SP-SO.PH-0002 * * WHY DID CONDITION HAPPEN: * The precise cause is not known. A potential reason could be a leak or a blockage in the pipeline. * * CONSEQUENCES: * Reduced pressure could lead to system inefficiency or potential system failure if not rectified. * * REQUIREMENTS IMPACTED: * Normal Hydraulic Operation * * ADVERSE PHYSICAL CONDITIONS: * Reduced hydraulic pressure * * WHO WAS NOTIFIED: * Control Room, Maintenance Team * * KNOWLEDGEABLE INDIVIDUALS: * Roberts, Martin, Ortega * * REPEAT OR SIMILAR CONDITION: * This is the first observed instance in the last two years. * * IMMEDIATE ACTIONS AND RECOMMENDED ACTIONS: * Immediate inspection and troubleshooting of the S4 system. * * Updated: ROBERT JAMES 03.15.2020 16:11:12 * ------------------------------------------------------------- * 03/18/2020 14:44:32 MARTIN JACOBS (NUSER) * Post inspection, it was discovered that the pressure drop was a consequence of a minor leak coupled with some obtrusive crud in the system. The system has been cleaned, sealed, and is now back to normal operation. | What was the initial problem detected in the S4 system? | At 1325 hours on 15/03/20, a hydraulic pressure anomaly was detected in the S4 system. The hydraulic pressure dropped from standard operating level of 98 bar to 89 bar. The pressure difference is unusual and is not typical based on historical data reviews.
80 | 2020-02-15 | 30976954 | 80251560 | Unusual Leakage from 18B Pump motor | S4CW -4CWE7 | * **************Incident Description************** * Notification 000030976954 Details * *********************************************************** * 02/15/2020 07:34:31 INCIDENT REPORT (INCIDENT REPORT) * Report submitted by: Emily Adams 321-654-0987 ENTITY\INCIDENT: * CONDITION DESCRIPTION/LOCATION (THE INAPPROPRIATE ACTION AND ITS NEGATIVE EFFECT/INCLUDE A DETAILED LOCATION DESCRIPTION): * At 0734 on 15/2/20 during the morning walkthrough, the operator identified unusual leakage from the 18B Pump motor. The 18B Pump was immediately shut down for inspection. Closer inspection revealed the leakage to be a clear liquid, possibly coolant escape from the motor. The area was cordoned off and the Engineering team was called to further investigate the source. * * ACTIVITIES, PROCESSES, PROCEDURES INVOLVED: * Daily equipment check, S4.OP.AB-CW-0003, S4.OP-SO.CW-0002 * WHY DID CONDITION HAPPEN? * Unknown, although past incidents of similar nature indicate seal failure or a loosen fixture * * CONSEQUENCES: * Potential internal damage to the pump motor, environmental concern due to leakage * * REQUIREMENTS IMPACTED: * Normal operation with potential extra downtime * * ADVERSE PHYSICAL CONDITIONS: * Seepage from 18B Pump Motor casing * * WHO WAS NOTIFIED: * Security, Supervisor, Engineering Team * * KNOWLEDGEABLE INDIVIDUALS: * Engineering Team * * REPEAT OR SIMILAR CONDITION: * No, this is the first report of this kind * * IMMEDIATE ACTIONS AND RECOMMENDED ACTIONS: * Engineering Team to diagnose and rectify the leakage, operator to monitor for any additional leakage. * 02/23/2020 12:15:44 EMILY ADAMS (INCIDENT) * Engineering reported the sealing fixture was loose which led to the leak. The fixture was tightened, and the motor was cleaned and tested. It's now back in operation. | What was the immediate action taken after identifying the unusual leakage from the pump motor? | The 18B Pump was immediately shut down for inspection. Closer inspection revealed the leakage to be a clear liquid, possibly coolant escape from the motor. The area was cordoned off and the Engineering team was called to further investigate the source.
81 | 2018-09-16 | 30875041 | 80246831 | Fluctuating current in 42B Pump | S4CW -4CWE8 | * **************Incident Description************** * Notification 000030875041 Details * *********************************************************** * 09/16/2018 16:52:00 INCIDENT REPORT (INCIDENT REPORT) * Report submitted by: Laura Johnson ENTITY\INCIDENT: * * CONDITION DESCRIPTION/LOCATION (THE INAPPROPRIATE ACTION AND ITS NEGATIVE EFFECT/INCLUDE A DETAILED LOCATION DESCRIPTION): * During routine inspection, 42B Pump showed fluctuating current which is not typical for this machinery. No fluctuations in pressure or temperature were noted. This pump is vital to maintain pressure in the cooling system and therefore it is critical to understand the cause of this fluctuation before it escalates to a more substantial issue. * * ACTIVITIES, PROCESSES, PROCEDURES INVOLVED: * Regular maintenance, S4.OP-RT.CW-0002 * * WHY DID CONDITION HAPPEN? * As of now, the cause is unknown. Further in-depth investigation is required. * * CONSEQUENCES: * Possible electrical or mechanical malfunction causing fluctuation, which could compromise cooling effectiveness. * * REQUIREMENTS IMPACTED: * Routine operation * * ADVERSE PHYSICAL CONDITIONS: * Electricity fluctuation in pump 42B * * WHO WAS NOTIFIED: * Operations Supervisor, Maintenance Department. * * KNOWLEDGEABLE INDIVIDUALS: * Technical Team * * REPEAT OR SIMILAR CONDITION: * No, it's the first report of such incident with this pump. * * IMMEDIATE ACTIONS AND RECOMMENDED ACTIONS: * Electrical team to investigate the cause and propose solution. * 09/20/2018 15:23:45 LAURA JOHNSON (INCIDENT) * The inspection revealed an aging wiring issue causing fluctuations. Rewiring and insulation repairs were performed on pump 42B. The pump's operation has returned to the normal range. | What was the immediate action taken for the incident involving Pump 42B's current fluctuation? | Electrical team to investigate the cause and propose solution.
82 | 2021-12-06 | 30945201 | 81652238 | Unexpected vibration from 34A Power Generator | S5PG -5PGN7 | * **************Incident Description************** * Notification 000030945201 Details * *********************************************************** * 12/06/2021 18:22:21 INCIDENT REPORT (INCIDENT REPORT) * Report submitted by: David Evans ENTITY\INCIDENT: * * CONDITION DESCRIPTION/LOCATION (THE INAPPROPRIATE ACTION AND ITS NEGATIVE EFFECT/INCLUDE A DETAILED LOCATION DESCRIPTION): * During standard operations, operator observed unexpected vibration emanating from the 34A Power Generator. Although no immediate effects in terms of power output were reported, the unexpected vibration may indicate underlying issues such as bearing wear or an imbalanced rotor. Immediate action was taken to initiate standard abnormality procedures. * * ACTIVITIES, PROCESSES, PROCEDURES INVOLVED: * Observation of sudden change in mechanical behavior as per procedure S5.OP.SO.PG-0023 * * WHY DID CONDITION HAPPEN? * The cause is yet to be determined. Possible reasons could be mechanical wear, rotor imbalance or underlying defect in the power generator components. * * CONSEQUENCES: * If left unchecked, this might lead to mechanical wear in generator components, unexpected shutdown or reduced efficiency in power output. * * REQUIREMENTS IMPACTED: * Operational safety and reliability of 34A Power Generator. * * ADVERSE PHYSICAL CONDITIONS: * Unexpected physical vibration from 34A Power Generator. * * WHO WAS NOTIFIED: * Shift Manager, Safety Department * * KNOWLEDGEABLE INDIVIDUALS: * Team Lead - David, Shift Supervisor - Allen, Safety Manager - Lisa * * REPEAT OR SIMILAR CONDITION: * No previous similar incidents reported. * * IMMEDIATE ACTIONS AND RECOMMENDED ACTIONS: * Initiated abnormality procedures as per S5.OP.SO.PG-0023. Also recommended immediate inspection of the 34A Power Generator by the Maintenance team. * 12/07/2021 07:56:56 DAVID EVANS (INCIDENT) * Maintenance inspection is currently underway. The inspection and subsequent report will provide more clarity on the issue. | What immediate action was taken when unexpected vibration was observed from the 34A Power Generator? | Immediate action was taken to initiate standard abnormality procedures.
83 | 2019-12-05 | 30985040 | 90001127 | Leaking coolant from 27B Pump | S4CW -4CWE9 | * **************Incident Description************** * Notification 000030985040 Details * *********************************************************** * 12/05/2019 10:23:44 INCIDENT REPORT (INCIDENT REPORT) * Report submitted by: Karen White ENTITY\INCIDENT: * * CONDITION DESCRIPTION/LOCATION (THE INAPPROPRIATE ACTION AND ITS NEGATIVE EFFECT/INCLUDE A DETAILED LOCATION DESCRIPTION): * During a routine check on 5/12/19, the 27B Pump was found to be leaking coolant. The situation was escalated to the emergency team who initiated shutdown procedures from the Unit 4 Control Room. The coolant spill was quickly managed with no apparent external damage. S4.OP-AB.CW-0001 Pump abnormality procedure was activated due to the incident. * * ACTIVITIES, PROCESSES, PROCEDURES INVOLVED: * S4.OP.AB-CW-0001, S4.OP-SO.CW-0001 * * WHY DID CONDITION HAPPEN? * Unknown, although there have been incidences of leaking pump coolant in the past. * * CONSEQUENCES: * Potential damage on the pump system which could reduce the efficiency of Unit 4. * * REQUIREMENTS IMPACTED: * Pumping system operations * * ADVERSE PHYSICAL CONDITIONS: * Coolant leakage from 27B pump, potential for motor failure. * * WHO WAS NOTIFIED: * Control Room, Emergency Team * * KNOWLEDGEABLE INDIVIDUALS: * Williams, Jones, Houston * * REPEAT OR SIMILAR CONDITION: * Yes, incidences of leaking pump coolant have been previously documented. * * IMMEDIATE ACTIONS AND RECOMMENDED ACTIONS: * Isolate the pump, perform initial diagnostics then liaise with maintenance to address the problem. * 12/10/2019 16:46:25 KAREN WHITE (INCIDENT) * Pump diagnostics have been performed. It was identified that the coolant leakage was due to worn-out seals which caused the system pressure to drop. Seals have been replaced, leakage stopped, system pressure restored to normal. I recommend regular maintenance checks and timely replacement of worn-out | What immediate and recommended actions were taken after the coolant leakage from the 27B Pump? | Isolate the pump, perform initial diagnostics then liaise with maintenance to address the problem. Pump diagnostics have been performed. It was identified that the coolant leakage was due to worn-out seals which caused the system pressure to drop. Seals have been replaced, leakage stopped, system pressure restored to normal. I recommend regular maintenance checks and timely replacement of worn-out.
84 | 2019-11-07 | 30750215 | 80221548 | 9A Pump motor vibration alarm | S4CW -4CWE1 | * **************Incident Description************** * Notification 000030750215 Details * *********************************************************** * 11/07/2019 10:27:20 INCIDENT REPORT (INCIDENT REPORT) * Report submitted by: Edward Green 555-123-4560 ENTITY\INCIDENT: * CONDITION DESCRIPTION/LOCATION (THE INAPPROPRIATE ACTION AND ITS NEGATIVE EFFECT/INCLUDE A DETAILED LOCATION DESCRIPTION): * The operator notified at 1000 hours on 11/7/19 that the 9A Pump's vibration alarm had been triggered. Vibration was confirmed on the pump motor and the pump was shut down per S4.OP-AB.CW-0002. An initial inspection did not reveal any external damage. * * ACTIVITIES, PROCESSES, PROCEDURES INVOLVED: * S4.OP.AB-CW-0002, S4.OP-SO.CW-0002 * * WHY DID CONDITION HAPPEN? * Unknown, though improper alignment or worn-out parts could be suspected. * * CONSEQUENCES: * Potential equipment damage if the cause of vibration is not identified and resolved. * * REQUIREMENTS IMPACTED: * Pump availability. Potential production impact. * * ADVERSE PHYSICAL CONDITIONS: * High vibration levels on 9A Pump motor. * * WHO WAS NOTIFIED: * Supervisor, Maintenance and Operations, Safety dept. * * KNOWLEDGEABLE INDIVIDUALS: * Maintenance Team Lead, Operations Supervisor. * * REPEAT OR SIMILAR CONDITION: * No, first occurrence. * * IMMEDIATE ACTIONS AND RECOMMENDED ACTIONS: * Investigation and diagnostic tests scheduled for 9A Pump Motor. * 11/07/2019 13:20:46 EDWARD GREEN (INCIDENT) * Diagnosis revealed that the motor’s bearings were worn out. Plan for motor bearing replacement has been initiated under a new work order. | What was the immediate action taken following the incident with the 9A Pump's vibration alarm? | Investigation and diagnostic tests scheduled for 9A Pump Motor.
85 | 2020-09-10 | 30912540 | 80231248 | Unplanned shutdown of 18B Pump | S4CW -4CWE7 | * **************Incident Description************** * Notification 000030912540 Details * *********************************************************** * 09/10/2020 14:50:21 INCIDENT REPORT (INCIDENT REPORT) * Report submitted by: Emily Thompson 987-654-3210 ENTITY\INCIDENT: * CONDITION DESCRIPTION/LOCATION (THE INAPPROPRIATE ACTION AND ITS NEGATIVE EFFECT/INCLUDE A DETAILED LOCATION DESCRIPTION): * At 1420 this afternoon, an unexpected shutdown of the 18B Pump was recorded. The pump's pressure was normal prior to the incident. Pump temperature was fluctuating more than usual, suggesting internal issues. * * ACTIVITIES, PROCESSES, PROCEDURES INVOLVED: * S4.OP.AB-CW-0015, S4.OP-SO.CW-0025 * * WHY DID CONDITION HAPPEN? * Unknown at this time. This could be due to natural wear and tear, or possibly a mechanical or electrical failure. * * CONSEQUENCES: * Potential impacts on operational efficiency, and risk to other equipment due to sudden pump shutdown. * * REQUIREMENTS IMPACTED: * Stable operation of 18B pump. * * ADVERSE PHYSICAL CONDITIONS: * Unplanned shutdown of a pump may have resulted in excessive mechanical stress on the components. * * WHO WAS NOTIFIED: * Supervisor, Maintenance Department, Incident Team * * KNOWLEDGEABLE INDIVIDUALS: * Maintenance Team, Incident Team, Pump Specialist * * REPEAT OR SIMILAR CONDITION: * No * * IMMEDIATE ACTIONS AND RECOMMENDED ACTIONS: * Launch a complete investigation of the 18B pump and the recording systems. If necessary, replace or repair affected parts. * 09/16/2020 11:28:38 EMILY THOMPSON (INCIDENT) * The investigation found faulty wiring in the control circuit that caused the unexpected shutdown. The wiring has been replaced and the pump is now functioning normally. | What caused the unexpected shutdown of the pump? | The investigation found faulty wiring in the control circuit that caused the unexpected shutdown.
86 | 2019-12-10 | 30965045 | 90235472 | Sudden Drop in 18D Pump Pressure | S4CW -4CWE1 | * **************Incident Description************** * Notification 000030965045 Details * *********************************************************** * 12/10/2019 14:12:36 INCIDENT REPORT (INCIDENT REPORT) * Report submitted by: David White ENTITY\INCIDENT: * * CONDITION DESCRIPTION/LOCATION (THE INAPPROPRIATE ACTION AND ITS NEGATIVE EFFECT/INCLUDE A DETAILED LOCATION DESCRIPTION): * During a routine check at 1400hrs, it was observed that the 18D Pump had a sudden drop in pressure. The pressure level reduced to 8 psig from 15 psig within three hours. Cooling water temperature remained within normal limits. No observable external damages were noted on the 18D pump. This sudden change in pressure is not typically expected and could cause reduced pump efficiency. * * ACTIVITIES, PROCESSES, PROCEDURES INVOLVED: * Routine pressure monitoring * * WHY DID CONDITION HAPPEN? * Unknown, potential internal pump damage or possible blockage * * CONSEQUENCES: * Potential reduced efficiency and performance hindrance, increase in maintenance needs. * * REQUIREMENTS IMPACTED: * Optimum pressure maintenance * * ADVERSE PHYSICAL CONDITIONS: * Unexpected low pressure at 18D Pump * * WHO WAS NOTIFIED: * Supervisor, Maintenance Team * * KNOWLEDGEABLE INDIVIDUALS: * Supervisor, Maintenance Team, Engineering Department * * REPEAT OR SIMILAR CONDITION: * No, this is the first occurrence. * * IMMEDIATE ACTIONS AND RECOMMENDED ACTIONS: * Technical team to investigate the cause for the drop in pressure of the 18D Pump. * If required, decommission and perform a complete system check. * 12/10/2019 18:22:41 DAVID WHITE (INCIDENT) * An internal investigation has been initiated to explore the reasons behind the unexpected pressure drop. | What immediate actions were recommended after the unexpected pressure drop at the 18D Pump? | Technical team to investigate the cause for the drop in pressure of the 18D Pump. If required, decommission and perform a complete system check.
87 | 2020-12-14 | 30998763 | 80245632 | 8B pump vibrating excessively | S4CW -4CWE7 | * **************Incident Description************** * Notification 000030998763 Details * *********************************************************** * 12/14/2020 16:10:23 INCIDENT REPORT (INCIDENT REPORT) * Report submitted by: Jessica Green ENTITY\INCIDENT: * * CONDITION DESCRIPTION/LOCATION (THE INAPPROPRIATE ACTION AND ITS NEGATIVE EFFECT/INCLUDE A DETAILED LOCATION DESCRIPTION): * Safety inspection team observed 8B pumps vibrating excessively, which is an unusual behaviour. This was discovered during a routine safety check of the Unit 4 cooling systems. Preliminary check showed no elevated temperature or overheating, but the motor casing's constant vibration poses a potential risk over time. * * ACTIVITIES, PROCESSES, PROCEDURES INVOLVED: * Safety inspection S4.OP-SO.CW-0003; routine analysis of cooling system * * WHY DID CONDITION HAPPEN? * Unknown. The pump underwent regular maintenance last year but this is the first such incident noted. * * CONSEQUENCES: * Long-term exposure to excessive vibration may lead to structural fatigue, resulting in potential equipment damage and downtime. * * REQUIREMENTS IMPACTED: * Reliable operation of 8B pump * * ADVERSE PHYSICAL CONDITIONS: * Excessive vibration of 8B pump casing; no increased temperature detected * * WHO WAS NOTIFIED: * Supervisor, Operations Team, Maintenance Team * * KNOWLEDGEABLE INDIVIDUALS: * Supervisor, Maintenance Team, Operations Team * * REPEAT OR SIMILAR CONDITION: * No, this is the first such occurrence noted. * * IMMEDIATE ACTIONS AND RECOMMENDED ACTIONS: * Carry out vibration analysis of 8B pump, and if symptoms persist, further inspection may be required. Review maintenance procedure to ensure proper fitting of components in pump assembly. * 12/16/2020 09:56:12 ROBERT BLACK (INCIDENT) * Vibration analysis carried out revealing wear and tear on the pump shafts due to unbalanced pressure. The team is planning to restore balance and replace parts of the pump shaft as necessary. This should solve the excessive vibration | What immediate and recommended actions were suggested following the excessive vibration of the 8B pump? | Carry out vibration analysis of 8B pump, and if symptoms persist, further inspection may be required. Review maintenance procedure to ensure proper fitting of components in pump assembly.
88 | 2017-09-13 | 30917439 | 80349230 | Oil Leakage in Pump 20B | S3CW -3CWE7 | * **************Incident Description************** * Notification 000030917439 Details * *********************************************************** * 09/13/2017 15:22:00 INCIDENT REPORT (INCIDENT REPORT) * Report submitted by: Madison Green ENTITY\INCIDENT: * * CONDITION DESCRIPTION/LOCATION (THE INAPPROPRIATE ACTION AND ITS NEGATIVE EFFECT/INCLUDE A DETAILED LOCATION DESCRIPTION): * During a routine inspection, our team observed an unusual oil leakage from 20B Pump. An immediate examination was conducted and a noticeable amount of oil deposited under the pump was detected. The pump was then shut off to avoid additional oil spillage and damage to pump machinery. * * ACTIVITIES, PROCESSES, PROCEDURES INVOLVED: * S3.OP.AB-CW-0012, S3.OP-SO.CW-0010 * * WHY DID CONDITION HAPPEN? * Preliminary check suggests worn out seals or gaskets, however detailed investigation required for confirmation. * * CONSEQUENCES: * Immediate cessation of the operation was necessary, leading to temporary loss of productivity. If left unaddressed, potential for severe machinery damage. * * REQUIREMENTS IMPACTED: * Required pump functionality and unit operations. * * ADVERSE PHYSICAL CONDITIONS: * Oil Leakage in 20B Pump. * * WHO WAS NOTIFIED: * Operations Supervisor, Maintenance Team * * KNOWLEDGEABLE INDIVIDUALS: * Williams, Maxwell, Stewart * * REPEAT OR SIMILAR CONDITION: * First reported instances of oil leakage from this unit. * * IMMEDIATE ACTIONS AND RECOMMENDED ACTIONS: * Maintenance Team to conduct thorough checkup & repair works involving the replacement of potential faulty seals or gaskets. * 09/14/2017 10:12:11 MADISON GREEN (INCIDENT) * Upon investigation, the maintenance team found the issue to be a faulty gasket that had worn out over time. The gasket was replaced and the pump is now back in operation. Extra precautions have been advised for future monitoring. | What was the cause of the oil leakage in the 20B pump? | Preliminary check suggests worn out seals or gaskets, however detailed investigation required for confirmation. Upon investigation, the maintenance team found the issue to be a faulty gasket that had worn out over time.
89 | 2018-10-10 | 30745638 | 80233490 | Surge in Processor 3A power consumption | P2PD -2PDE1 | * **************Incident Description************** * Notification 000030694282 Details * *********************************************************** * 10/10/2018 08:14:00 INCIDENT REPORT (INCIDENT REPORT) * Report submitted by: Sam Adams ENTITY\INCIDENT: * * CONDITION DESCRIPTION/LOCATION (THE INAPPROPRIATE ACTION AND ITS NEGATIVE EFFECT/INCLUDE A DETAILED LOCATION DESCRIPTION): * At 8 AM, while monitoring system logs, a power surge was noted on Processor 3A. Power usage was higher than average at all levels of operation. No external reasons can be attributed to the system surge. This incident has already been isolated, however, the cause of the maloperation is currently unspecified and there's potential risk to other processors. The processor was taken offline for safety procedures. No signs of physical damage was noted. * * ACTIVITIES, PROCESSES, PROCEDURES INVOLVED: * System Monitoring, Incident Isolation * * WHY DID CONDITION HAPPEN? * Unknown at this time. The surge may be a symptom of an internal fault in the processor, or an irregularity in the power supply unit. Needs further investigation. * * CONSEQUENCES: * Potential hardware failure. Extended downtime for affected equipment if the issue is not resolved immediately. * * REQUIREMENTS IMPACTED: * Temporary drop in processing capacity, affecting overall system performance. Investigations might require temporary decommissioning of similar units. * * ADVERSE PHYSICAL CONDITIONS: * Potential hardware failure noted. * * WHO WAS NOTIFIED: * Supervisor, Maintenance Team, System Admin * * KNOWLEDGEABLE INDIVIDUALS: * Systems Engineer, Hardware Technician * * REPEAT OR SIMILAR CONDITION: * No, this is the first incident of its nature. * * IMMEDIATE ACTIONS AND RECOMMENDED ACTIONS: * An immediate inspection of the affected processor unit is needed. Inspect power supply units for anomalies. If an internal fault is detected, other similar units should also be examined for potential defects. * 10/10/2018 12:25:12 SAM ADAMS (INCIDENT) * Post Inspection | What immediate actions are recommended following the incident? | An immediate inspection of the affected processor unit is needed. Inspect power supply units for anomalies. If an internal fault is detected, other similar units should also be examined for potential defects.
90 | 2022-01-14 | 40010547 | 90239876 | Faulty Valve at Unit 4A | S4CW -4CWE5-VALV | * **************Incident Description************** * Notification 000040010547 Details * *********************************************************** * 01/14/2022 15:23:46 INCIDENT REPORT (INCIDENT REPORT) * Report submitted by: Linda Green 987-654-3210 ENTITY\INCIDENT: * CONDITION DESCRIPTION/LOCATION (THE INAPPROPRIATE ACTION AND ITS NEGATIVE EFFECT/INCLUDE A DETAILED LOCATION DESCRIPTION): * During an inspection at 1520 on 1/14/22, a faulty valve was detected in Unit 4A. The valve was not closing fully, causing leakage. Immediate isolation of the valve was performed and normal flow was resumed through an alternative pipeline. The shutdown of the 4A valve and its consequences are under evaluation. * * ACTIVITIES, PROCESSES, PROCEDURES INVOLVED: * Routine inspection, S4.OP-AB.CW-0001 Valve Abnormality * WHY DID CONDITION HAPPEN? * Potential wear and tear of the valve or debris obstruction. * * CONSEQUENCES: * Possible increase in maintenance cost and pipeline inefficiency. * * REQUIREMENTS IMPACTED: * Valve function, pipeline efficiency * * ADVERSE PHYSICAL CONDITIONS: * Valve leakage * * WHO WAS NOTIFIED: * Maintenance Team, Control Room * * KNOWLEDGEABLE INDIVIDUALS: * Dawson, Johnson, Bradshaw * * REPEAT OR SIMILAR CONDITION: * No * * IMMEDIATE ACTIONS AND RECOMMENDED ACTIONS: * Valve replacement or repair and check for potential debris in the pipeline. * 01/15/2022 11:03:43 LARRY DOE (INCIDENT) * The valve was removed and inspected. It was found to be heavily worn out and it was replaced. The pipeline was also cleared of any potential debris. | What immediate actions were taken after the detection of the faulty valve? | Immediate isolation of the valve was performed and normal flow was resumed through an alternative pipeline. The valve was removed and inspected. It was found to be heavily worn out and it was replaced. The pipeline was also cleared of any potential debris.
91 | 2020-09-29 | 30978965 | 90241537 | HIGH VIBRATION FOUND IN 11A PUMP | S2CW -2CWE9 | * **************Incident Description************** * Notification 000030978965 Details * *********************************************************** * 09/29/2020 13:45:30 INCIDENT REPORT (INCIDENT REPORT) * Report submitted by: Thomas Watson 987-654-3210 ENTITY\INCIDENT: * CONDITION DESCRIPTION/LOCATION (THE INAPPROPRIATE ACTION AND ITS NEGATIVE EFFECT/INCLUDE A DETAILED LOCATION DESCRIPTION): * During a regular inspection routine at 1345 on 9/29/20, high vibrations were detected on the 11A Pump. The vibration was significantly higher than the standard operation. The pump was immediately shutdown, and the vibration subsided. Inspection did not reveal any loose parts or noticeable damage. The pump was operating at normal temperature and pressure before shutdown. * * ACTIVITIES, PROCESSES, PROCEDURES INVOLVED: * S2.OP.AB-CW-0009, S2.OP-SO.CW-0003 * WHY DID CONDITION HAPPEN? * Cause uncertain, further investigation is needed. High vibrations can be due to multiple reasons but primarily due to unbalanced or misaligned parts. * * CONSEQUENCES: * Potential for pump damage, if the pump continues to run in high vibration could lead to catastrophic failure. * * REQUIREMENTS IMPACTED: * Operational readiness of 11A Pump * * ADVERSE PHYSICAL CONDITIONS: * High Vibration on 11A Pump * * WHO WAS NOTIFIED: * Control Room, Maintenance Supervisor * * KNOWLEDGEABLE INDIVIDUALS: * Techs- Miller, Davis, Green * * REPEAT OR SIMILAR CONDITION: * No, not yet. * * IMMEDIATE ACTIONS AND RECOMMENDED ACTIONS: * Maintenance to carry out an in-depth examination of the 11A pump to ascertain the reason for the vibration. A detailed investigation should encompass the alignment and centralization of parts, pump foundation, and any damage to the bearing or seals. * Updated: THOMAS WATSON 09.29.2020 15:01:19 | What immediate actions were recommended after the detection of high vibrations on the 11A Pump? | Maintenance to carry out an in-depth examination of the 11A pump to ascertain the reason for the vibration. A detailed investigation should encompass the alignment and centralization of parts, pump foundation, and any damage to the bearing or seals.
92 | 2020-09-17 | 30985126 | 80264032 | Unexpected vibration in 16B Pump | S5CW -5CWE2 | * **************Incident Description************** * Notification 000030985126 Details * *********************************************************** * 09/17/2020 09:32:42 INCIDENT REPORT (INCIDENT REPORT) * Report submitted by: Emily Johnson ENTITY\INCIDENT: * * CONDITION DESCRIPTION/LOCATION (THE INAPPROPRIATE ACTION AND ITS NEGATIVE EFFECT/INCLUDE A DETAILED LOCATION DESCRIPTION): * During the regular maintenance on 09/17/2020, the technician reported unusual vibration in the 16B Pump. The pump was temporarily shut down for safety reasons and further inspection was initiated. The unusual vibration was believed to be emanating from the motor part of the pump, potentially indicating an internal mechanical issue. * * ACTIVITIES, PROCESSES, PROCEDURES INVOLVED: * S5.OP.AB-CW-0002, S5.OP-SO.CW-0003 * * WHY DID CONDITION HAPPEN? * Unknown at present, the source of the vibration needs to be identified. Possible causes could be worn-out components or mechanical faults. * * CONSEQUENCES: * Possible pump damage, reduced efficiency can potentially affect overall operation. * * REQUIREMENTS IMPACTED: * Normal Pump Operation, potential work schedule delays due to the shutdown. * * ADVERSE PHYSICAL CONDITIONS: * Unexpected vibration observed in the 16B Pump. * * WHO WAS NOTIFIED: * Maintenance Supervisor, Pump Team, Safety Officer * * KNOWLEDGEABLE INDIVIDUALS: * Technician Team, Safety Officer * * REPEAT OR SIMILAR CONDITION: * No, first occurrence. * * IMMEDIATE ACTIONS AND RECOMMENDED ACTIONS: * The vibration source to be identified. If necessary, a full pump inspection or replacement to be scheduled. Pump should remain off until deemed safe. * 09/18/2020 07:35:08 JOHN SMITH (INCIDENT) * The maintenance team investigated the pump and discovered a worn component causing the vibration. Component replaced, tests done to confirm the vibration was resolved. Recommending a review of maintenance schedule for similar components. | What immediate actions were recommended following the unusual vibration in the 16B Pump? | The vibration source to be identified. If necessary, a full pump inspection or replacement to be scheduled. Pump should remain off until deemed safe.
93 | 2019-04-05 | 30873651 | 80233547 | Abnormal vibration in 18B pump motor | S4CW -4CWE7 | * **************Incident Description************** * Notification 000030873651 Details * *********************************************************** * 04/05/2019 07:50:12 INCIDENT REPORT (INCIDENT REPORT) * Report submitted by: William Thompson ENTITY\INCIDENT: * * CONDITION DESCRIPTION/LOCATION (THE INAPPROPRIATE ACTION AND ITS NEGATIVE EFFECT/INCLUDE A DETAILED LOCATION DESCRIPTION): * At approximately 0700 on 4/5/19, it was reported that a recently maintained 18B Pump was exhibiting abnormal vibration. Several concerned operators noted the unusual behavior. S4.OP-AB.CW-0001 Pump Abnormality procedure was initiated due to the unusual vibration of 18B Pump Motor. * * ACTIVITIES, PROCESSES, PROCEDURES INVOLVED: * S4.OP.AB-CW-0001, S4.OP-SO.CW-0001 * * WHY DID CONDITION HAPPEN? * Unknown, though pump motors may vibrate excessively if the alignment or balancing is not done properly * * CONSEQUENCES: * Longer term, potential pump motor damage could occur, leading to reduced efficiency * * REQUIREMENTS IMPACTED: * Normal operation * * ADVERSE PHYSICAL CONDITIONS: * Excessive vibration from 18B Pump motor, potential internal damage * * WHO WAS NOTIFIED: * Control Room, Maintenance Team * * KNOWLEDGEABLE INDIVIDUALS: * Thompson, Lee, Davis * * REPEAT OR SIMILAR CONDITION: * No * * IMMEDIATE ACTIONS AND RECOMMENDED ACTIONS: * Investigation of 18B Pump Motor and rebalancing if necessary * * Updated: WILLIAM THOMPSON 04.05.2019 10:23:37 * ------------------------------------------------------------- * 04/06/2019 11:18:21 MARY JONES(INCIDENT) * Inspection conducted and found to be a misalignment problem. Motor was aligned properly under the same order. Currently, the 18B pump motor is working normally. | What was the initial problem with the 18B Pump Motor and what action was taken as a result? | At approximately 0700 on 4/5/19, it was reported that a recently maintained 18B Pump was exhibiting abnormal vibration. Several concerned operators noted the unusual behavior. S4.OP-AB.CW-0001 Pump Abnormality procedure was initiated due to the unusual vibration of 18B Pump Motor.
94 | 2020-09-11 | 30808176 | 80234026 | Unexpected vibration in 30B Pump | S4CW -4CWE1 | * **************Incident Description************** * Notification 000030808176 Details * *********************************************************** * 09/11/2020 13:50:01 INCIDENT REPORT (INCIDENT REPORT) * Report submitted by: Richard Adams 123-456-7895 ENTITY\INCIDENT: * * CONDITION DESCRIPTION/LOCATION (THE INAPPROPRIATE ACTION AND ITS NEGATIVE EFFECT/INCLUDE A DETAILED LOCATION DESCRIPTION): * On 09/11/2020, during the regular morning shift, operator observed high vibration levels on 30B pump at S4CW -4CWE1 location. The 30B pump was immediately shut down as per standby protocol. Initial check did not reveal any visible damage or leaks. Suspicion raised due to unusual vibrations that might indicate possible mechanical issues or impending failure. * * ACTIVITIES, PROCESSES, PROCEDURES INVOLVED: * Regular operation and surveillance activities. * * WHY DID CONDITION HAPPEN? * The exact cause is unknown at present. Likely causes could be misalignment, an imbalance, worn parts or mechanical looseness. * * CONSEQUENCES: * Without prompt corrective action, ongoing pump operation could lead to more severe mechanical damages or even catastrophic failure. * * REQUIREMENTS IMPACTED: * Equipment availability and reliability may be compromised if the pump fails. * * ADVERSE PHYSICAL CONDITIONS: * High level of vibration from 30B pump. * * WHO WAS NOTIFIED: * Supervisor, Maintenance team and Safety Department. * * KNOWLEDGEABLE INDIVIDUALS: * Richard Adams, Maintenance team. * * REPEAT OR SIMILAR CONDITION: * No, this is the first occurrence of such incident on this pump. * * IMMEDIATE ACTIONS AND RECOMMENDED ACTIONS: * Stop the pump and conduct detailed inspection. * 09/14/2020 15:43:26 RICHARD ADAMS (INCIDENT) * Inspection performed revealed misalignment of the pump and motor. Repairs were carried out and testing has been scheduled for later today to confirm the success of the maintenance. | What were the immediate actions taken after observing the high vibration levels on the 30B pump? | Stop the pump and conduct detailed inspection.
95 | 2020-11-30 | 30985231 | 80234567 | Odd vibration from 18A Pump | S4CW -4CWE3 | * **************Incident Description************** * Notification 000030985231 Details * *********************************************************** * 11/30/2020 09:15:45 INCIDENT REPORT (INCIDENT REPORT) * Report submitted by: Jack Thomas ENTITY\INCIDENT: * * CONDITION DESCRIPTION/LOCATION (THE INAPPROPRIATE ACTION AND ITS NEGATIVE EFFECT/INCLUDE A DETAILED LOCATION DESCRIPTION): * After regular monthly maintenance on 18A Pump, we are experiencing unusual vibrations when the pump is active. No irregularities were found during maintenance and all components were within normal parameters. However, after maintenance was completed, the pump began experiencing these odd vibrations, causing concern for potential hidden damage. * * ACTIVITIES, PROCESSES, PROCEDURES INVOLVED: * S4.OP.AB-CW-0003, S4.OP-SO.CW-0003 * * WHY DID CONDITION HAPPEN? * Unknown as all preventative maintenance was performed properly according to established procedures. * * CONSEQUENCES: * Possible failure of pump, leading to loss of function and efficiency. * * REQUIREMENTS IMPACTED: * Reliability of 18A Pump * * ADVERSE PHYSICAL CONDITIONS: * Unusual vibrations from 18A Pump post maintenance * * WHO WAS NOTIFIED: * On-Site Maintenance Manager * * KNOWLEDGEABLE INDIVIDUALS: * On-Site Maintenance Team * * REPEAT OR SIMILAR CONDITION: * No, first occurrence * * IMMEDIATE ACTIONS AND RECOMMENDED ACTIONS: * Suggest a thorough re-inspection of the 18A Pump and its components. Possible in depth vibration analysis for any potential hidden faults. * 12/01/2020 15:03:54 JACK THOMAS (INCIDENT) * Engineering team has been notified and a specialist team will be on site for a comprehensive investigation tomorrow. | What is the adverse physical condition reported after maintenance on a pump? | Unusual vibrations from 18A Pump post maintenance
96 | 2018-07-31 | 30773445 | 80232966 | Pressure drop in pump 7B | S4CW -4CWE5 | * **************Incident Description************** * Notification 000030773445 Details * *********************************************************** * 07/31/2018 09:33:14 INCIDENT REPORT (INCIDENT REPORT) * Report submitted by: Natalie Smith ENTITY\INCIDENT: * * CONDITION DESCRIPTION/LOCATION (THE INAPPROPRIATE ACTION AND ITS NEGATIVE EFFECT/INCLUDE A DETAILED LOCATION DESCRIPTION): * During routine inspection, 7B Pump exhibited sudden and unusual pressure drop. The pump pressure was monitored and found to fluctuate between 8 to 12 psi, lower than the normal pressure range of 15-18 psi. This indicates possible internal damage to either pump components or blockage impacting the proper functioning of the pump. * * ACTIVITIES, PROCESSES, PROCEDURES INVOLVED: * S4.OP.AB-CW-0002, S4.OP-SO.CW-0003 * * WHY DID CONDITION HAPPEN? * Preliminary analysis points towards possible internal damage or blockage. More detailed inspection is required to ascertain the cause. * * CONSEQUENCES: * Risk of pump failure and reduction of overall system efficiency. * * REQUIREMENTS IMPACTED: * Operating consistency, Equipment integrity * * ADVERSE PHYSICAL CONDITIONS: * Reduced pressure in 7B pump. * * WHO WAS NOTIFIED: * Equipment Oversight Committee, Maintenance Supervisor * * KNOWLEDGEABLE INDIVIDUALS: * Stuart Johnson, Maria Gonzalez, Adam Wong * * REPEAT OR SIMILAR CONDITION: * No, first instance * * IMMEDIATE ACTIONS AND RECOMMENDED ACTIONS: * Initiate immediate inspection of 7B Pump for potential damage or blockage. Subsequently, if necessary, facilitate repairs or part replacements. * 07/31/2018 16:31:47 NATALIE SMITH (INCIDENT) * Inspection conducted found a blockage in the pump's input valve. The blockage was removed, pump parameters tested and are now within normal range. Monitoring will continue to ensure stable operation. | What immediate actions were suggested after observing the unusual pressure drop in the 7B Pump? | Initiate immediate inspection of 7B Pump for potential damage or blockage. Subsequently, if necessary, facilitate repairs or part replacements.
97 | 2018-12-04 | 30781215 | 80239671 | Distorted sound from transformer T5F | S4TR -4TRE5 | * **************Incident Description************** * Notification 000030781215 Details * *********************************************************** * 12/04/2018 13:48:12 INCIDENT REPORT (INCIDENT REPORT) * Report submitted by: Mark Hill * ENTITY\INCIDENT: * * CONDITION DESCRIPTION/LOCATION (THE INAPPROPRIATE ACTION AND ITS NEGATIVE EFFECT/INCLUDE A DETAILED LOCATION DESCRIPTION): * At 13:05 on 12/04/18, the technician noticed distorted sound from the T5F Transformer. Isolated and inspected the transformer. Disconnect switches on the H side are very hot to touch. Observations indicate a possible problem with the bushings. Also, a strong smell of overheating was identified. S4.OP-AB.TR-0002 Transformer Abnormality was initiated due to this unusual observation. * * ACTIVITIES, PROCESSES, PROCEDURES INVOLVED: * S4.OP-AB.TR-0002, S4.OP-SO.TR-0002 * * WHY DID CONDITION HAPPEN? * Unknown. Past incidents indicate a possibility of bushing breakdown or short circuits inside the transformer. * * CONSEQUENCES: * Possible transformer damage, which might lead to efficiency loss and interruption in power supply. * * REQUIREMENTS IMPACTED: * Transformer relaying and voltage regulation. * * ADVERSE PHYSICAL CONDITIONS: * Distorted sound and heat from T5F Transformer, possible internal damage. * * WHO WAS NOTIFIED: * Control Room, Maintenance Team. * * KNOWLEDGEABLE INDIVIDUALS: * Brown, Johnson, Smith. * * REPEAT OR SIMILAR CONDITION: * No, this is a new issue. * * IMMEDIATE AND RECOMMENDED ACTIONS: * Investigate T5F transformer and examine bushings and disconnect switches. * * Updated: MARK HILL 12.04.2018 14:23:27 * ------------------------------------------------------------ * 12/05/2018 08:46:04 JANE ROE (NUSER) * Thermal imaging showed high temperature concentration around the bushings. Transformer was taken out of service, inspected, and cleaned. | What immediate actions were recommended after the abnormality was discovered in the T5F Transformer? | Investigate T5F transformer and examine bushings and disconnect switches.
98 | 2017-07-27 | 30918764 | 80342652 | Unusual vibration in 18C Valve Gasket | S3CW -3CWE8 | * **************Incident Description************** * Notification 000030918764 Details * *********************************************************** * 07/27/2017 13:47:05 INCIDENT REPORT (INCIDENT REPORT) * Report submitted by: Dylan Thompson 321-762-8901 ENTITY\INCIDENT: * CONDITION DESCRIPTION/LOCATION (THE INAPPROPRIATE ACTION AND ITS NEGATIVE EFFECT/INCLUDE A DETAILED LOCATION DESCRIPTION): * During the bi-weekly inspection of the treatment facility, an unusual vibration was detected in the 18C Valve Gasket. This condition presents potential hazards of compromised integrity and failure of the gasket. The system was immediately placed in safe mode pending further investigation. * * ACTIVITIES, PROCESSES, PROCEDURES INVOLVED: * Routine inspection activity * * WHY DID CONDITION HAPPEN? * The underlying cause of the condition is yet to be determined pending a detailed investigation. * * CONSEQUENCES: * A failure of the gasket could lead to potential leaks and disruption of the system * * REQUIREMENTS IMPACTED: * Maintaining the integrity of the treatment facility and operating at optimal efficiency * * ADVERSE PHYSICAL CONDITIONS: * High vibration and potential of gasket failure * * WHO WAS NOTIFIED: * Shift Supervisor, Incident Response Team * * KNOWLEDGEABLE INDIVIDUALS: * Facility Manager, Engineering Team * * REPEAT OR SIMILAR CONDITION: * No, this is the first reported case of such a condition * * IMMEDIATE ACTIONS AND RECOMMENDED ACTIONS: * The facility has been placed in safe mode. An investigation plan has been initiated, involving a comprehensive inspection of the gasket design, maintenance history, and vibration analysis. Maintenance team will perform a detailed assessment and initiate corrective measures. * 07/30/2017 15:17:44 DYLAN THOMPSON (INCIDENT) * Post detailed assessment, it has been determined that the vibration was due to a loosened bolt holding the gasket. The bolt has been tightened and the gasket is now functioning in normal parameters. | What immediate actions were taken following the detection of unusual vibration in the 18C Valve Gasket? | The facility has been placed in safe mode. An investigation plan has been initiated, involving a comprehensive inspection of the gasket design, maintenance history, and vibration analysis. Maintenance team will perform a detailed assessment and initiate corrective measures.
99 | 2018-10-16 | 30754320 | 80245811 | Cooling tank leak in 7A | S4CW -4CWE2 | * **************Incident Description************** * Notification 000030754320 Details * *********************************************************** * 10/16/2018 14:25:22 INCIDENT REPORT (INCIDENT REPORT) * Report submitted by: James White ENTITY\INCIDENT: * * CONDITION DESCRIPTION/LOCATION (THE INAPPROPRIATE ACTION AND ITS NEGATIVE EFFECT/INCLUDE A DETAILED LOCATION DESCRIPTION): * During morning rounds, an engineer reported that coolant was leaking from 7A Cooling Tank. The engineer immediately activated the containment protocol and isolated the area, ensuring minimal exposure to personnel and equipment. The leak rate was low but consistently dripping. * * ACTIVITIES, PROCESSES, PROCEDURES INVOLVED: * Regular equipment inspection and containment processes. * * WHY DID CONDITION HAPPEN? * Pending investigation, but preliminary analysis indicates potential material fatigue or corrosive damage. FLOC: S4CW -4CWE2 * * CONSEQUENCES: * Potential system overheating, temporary shutdown for repair, environmental concerns, and personal safety issues. * * REQUIREMENTS IMPACTED: * System reliability, safety protocols, maintenance schedule. * * ADVERSE PHYSICAL CONDITIONS: * Constant coolant leak from 7A Cooling Tank. * * WHO WAS NOTIFIED: * Site Director, Maintenance Crew, Environmental and Safety Officer. * * KNOWLEDGEABLE INDIVIDUALS: * Maintenance Crew, Site Engineers, James White * * REPEAT OR SIMILAR CONDITION: * No previous incidents with this cooling tank. However, instances from other tanks exist in the site's history. * * IMMEDIATE ACTIONS AND RECOMMENDED ACTIONS: * Initiate emergency maintenance procedure, remove the faulty tank and inspect for causes of the leak. Check surrounding equipment for potential secondary damage. * 10/17/2018 16:55:34 JAMES WHITE (INCIDENT) * Upon a detailed inspection, the cause of the leak was identified as corroded welding seam. Due to the nature of the defect, the tank could not be repaired on-site and subsequently replaced. Preventative maintenance schedule will be updated, including a more thorough inspection of welding seams | What immediate actions were recommended after the coolant leak was discovered from 7A Cooling Tank? | Initiate emergency maintenance procedure, remove the faulty tank and inspect for causes of the leak. Check surrounding equipment for potential secondary damage.
100 | 2018-11-28 | 30895370 | 80538457 | Unexpected vibration on 29B pump | S5CW -5CWE1 | * **************Incident Description************** * Notification 000030895370 Details * *********************************************************** * 11/28/2018 04:49:13 INCIDENT REPORT (INCIDENT REPORT) * Report submitted by: Lisa Green 123-986-4587 ENTITY\INCIDENT: * CONDITION DESCRIPTION/LOCATION (THE INAPPROPRIATE ACTION AND ITS NEGATIVE EFFECT/INCLUDE A DETAILED LOCATION DESCRIPTION): * 29B Pump was observed with unusual vibrations during a routine inspection. The vibration level was 20% higher than normal. 29B Pump has been taken offline for inspection. * * ACTIVITIES, PROCESSES, PROCEDURES INVOLVED: * S5.OP.AB-CW-0001, S5.OP-SO.CW-0001 * * WHY DID CONDITION HAPPEN? * It is currently unknown, but may likely be due to mechanical failure or an imbalance. * * CONSEQUENCES: * Could result in pump failure or decreased efficiency. If left unchecked, this could lead to a major system breakdown. * * REQUIREMENTS IMPACTED: * Emergency shutdown of 29B Pump. Standby pump has been activated. * * ADVERSE PHYSICAL CONDITIONS: * High vibration level on 29B pump * * WHO WAS NOTIFIED: * Control Room, Maintenance Team * * KNOWLEDGEABLE INDIVIDUALS: * Richard Johnson, Jason Smith, Kim Lee * * REPEAT OR SIMILAR CONDITION: * No, this is the first occurrence * * IMMEDIATE ACTIONS AND RECOMMENDED ACTIONS: * Maintenance to inspect 29B pump and identify the cause of vibration * * Updated: LISA GREEN 11.28.2018 06:58:22 * ------------------------------------------------------------- * 12/03/2018 15:09:49 JASON DOE (NUSER) * The inspection revealed that the mother was out of balance due to worn out bearings. The bearings have been replaced and the pump was rebalanced. The pump has been returned to service with normal vibration levels. | What immediate action was recommended upon observing the unusual vibrations of the 29B pump? | Maintenance to inspect 29B pump and identify the cause of vibration.
101 | 2022-03-08 | 30956924 | 90045732 | POWER OUTAGE ON DRIVER ENGINE 11 | S1PE -1PEN3 | * **************Incident Description************** * Notification 000030956924 Details * *********************************************************** * 03/08/2022 16:15:02 INCIDENT REPORT (INCIDENT REPORT) * Report submitted by: Lisa Green ENTITY\INCIDENT: * * CONDITION DESCRIPTION/LOCATION (THE INAPPROPRIATE ACTION AND ITS NEGATIVE EFFECT/INCLUDE A DETAILED LOCATION DESCRIPTION): * At 14:50 on 3/08/22, the driver engine 11 experienced an unexpected power outage during operation. The Work Management Center was notified and a maintenance team was dispatched. The outage caused the system to enter a fail-safe state with no apparent damage. An odor of electrical burn was noted. The investigation into the outage is ongoing. * * ACTIVITIES, PROCESURES, PROCESSES INVOLVED: * S1.OP.PE.EN-0010, S1.OP-EM.PE-0002 * * WHY DID CONDITION HAPPEN? * Unknown, initial analysis suspect a possible electrical failure. * * CONSEQUENCES: * A prolonged outage could lead to overall system instability and unscheduled downtime. * * REQUIREMENTS IMPACTED: * Ongoing operation of Driver Engine 11. * * ADVERSE PHYSICAL CONDITIONS: * Power outage on Driver Engine 11, smell of electrical burn. * * WHO WAS NOTIFIED: * Supervisor, Work Management Center * * KNOWLEDGEABLE INDIVIDUALS: * Williams, Robinson, Garcia * * REPEAT OR SIMILAR CONDITION: * No, not a regular occurrence. * * IMMEDIATE ACTIONS AND RECOMMENDED ACTIONS: * Maintenance team to investigate the outage and repair any identified issues. If necessary, replacement parts should be ordered. * 03/09/2022 11:23:28 LISA GREEN (INCIDENT) * Preliminary examination did not show any signs of substantial electrical damage. A more thorough investigation is ongoing. Proper maintenance procedures have been initiated and the system will be carefully monitored upon restoration. | What are the consequences of a prolonged outage of the affected system? | A prolonged outage could lead to overall system instability and unscheduled downtime.
102 | 2019-04-12 | 30917455 | 80540027 | Overheat detected in Pump 8C | S3CW -3CWE5 | * **************Incident Description************** * Notification 000030917455 Details * *********************************************************** * 04/12/2019 07:21:14 INCIDENT REPORT (INCIDENT REPORT) * Report submitted by: Sydney Black ENTITY\INCIDENT: * * CONDITION DESCRIPTION/LOCATION (THE INAPPROPRIATE ACTION AND ITS NEGATIVE EFFECT/INCLUDE A DETAILED LOCATION DESCRIPTION): * During the morning inspection, Pump 8C installed at Unit 3 showed signs of overheat. The thermal sensors detected the unusual surge immediately. Immediate shutdown was ordered, and upon manual inspection, signs of discoloration in the motor casing, odd smell traces, and high temperatures were noted. Suspected potential insulation melt and subsequent issues. * * ACTIVITIES, PROCESSES, PROCEDURES INVOLVED: * Morning Inspection, Emergency Shutdown, Manual Inspection * * WHY DID CONDITION HAPPEN? * Possible failure in cooling system of the motor or overstress due to load. * * CONSEQUENCES: * Risk of motor failure and corresponding operations disruption. * * REQUIREMENTS IMPACTED: * Availability of Pump 8C * * ADVERSE PHYSICAL CONDITIONS: * Overheat in motor casing * * WHO WAS NOTIFIED: * Operations Supervisor, Safety Team * * KNOWLEDGEABLE INDIVIDUALS: * Maintenance Manager, Operations Supervisor * * REPEAT OR SIMILAR CONDITION: * Not known, new instance * * IMMEDIATE AND RECOMMENDED ACTIONS: * Comprehensive inspection of pump and testing of cooling system. Potential replacement of motor if damage is found. * 04/12/2019 12:45:10 SYDNEY BLACK (INCIDENT) * Inspection found issue with coolant flow, potential blockage resulted in overheating. Cooling system is being cleaned and tested before re-installation. Motor is sent for further diagnosis. | What immediate action was taken when the overheat of Pump 8C was detected? | Immediate shutdown was ordered, and upon manual inspection, signs of discoloration in the motor casing, odd smell traces, and high temperatures were noted.
103 | 2020-03-15 | 30987456 | 80234561 | Failure of 34C Heat Exchanger | S5CW -5CWE7 | * **************Incident Description************** * Notification 000030987456 Details * *********************************************************** * 03/15/2020 08:24:18 INCIDENT REPORT (INCIDENT REPORT) * Report submitted by: Daniel Radcliffe ENTITY\INCIDENT: * * CONDITION DESCRIPTION/LOCATION (THE INAPPROPRIATE ACTION AND ITS NEGATIVE EFFECT/INCLUDE A DETAILED LOCATION DESCRIPTION): * At 0745 on 3/15/20, the operator detected a failure in the 34C Heat Exchanger. An immediate inspection revealed a substantial loss of coolant and elevated temperatures in the system. A quick shutdown was initiated from the Unit 5 Control Room to prevent further damages. * * ACTIVITIES, PROCESSES, PROCEDURES INVOLVED: * S5.OP.HX-CD-0003, S5.OP-SO.HX-0001 * * WHY DID CONDITION HAPPEN? * Unknown at this moment. This type of failure generally occurs due to component fatigue or physical damage. * * CONSEQUENCES: * Severe thermal stress on the 34C Heat Exchanger, and potential failure of other components due to a system-wide heating. * * REQUIREMENTS IMPACTED: * Heat Exchange System * * ADVERSE PHYSICAL CONDITION: * Loss of coolant and elevated temperature readings. * * WHO WAS NOTIFIED: * Control Room, Maintenance team * * KNOWLEDGEABLE INDIVIDUALS: * Peterson, Williams, Thompson * * REPEAT OR SIMILAR CONDITION: * No * * IMMEDIATE AND RECOMMENDED ACTIONS: * Maintenance to investigate the 34C Heat Exchanger for potential component fatigue or physical damage. * Update: DANIEL RADCLIFFE 03.15.2020 10:33:19 * ------------------------------------------------------------ * 03/20/2020 14:32:45 JAMES DOE (NUSER) * After a detailed investigation, it was determined that failure was due to a physical damage. A small piece of debris lodged into the exchanger caused the breakdown. * Once the debris was removed, repairs were made, and the system is now functional | What was the cause of the failure in the 34C Heat Exchanger? | After a detailed investigation, it was determined that failure was due to a physical damage. A small piece of debris lodged into the exchanger caused the breakdown.
104 | 2019-12-05 | 40917236 | 90283746 | Unexpected shutdown of 5A Generator | S1PB -1PBE5-EGEN | * **************Incident Description************** * Notification 000040917236 Details * *********************************************************** * 12/05/2019 15:20:09 INCIDENT REPORT (INCIDENT REPORT) * Report submitted by: David Phillips 456-789-0123 ENTITY\INCIDENT: * CONDITION DESCRIPTION/LOCATION (THE INAPPROPRIATE ACTION AND ITS NEGATIVE EFFECT/INCLUDE A DETAILED LOCATION DESCRIPTION): * While monitoring the system, there was an abrupt shutdown of the 5A Generator. Diagnostic check showed a significant rise in internal temperatures seconds before the shutdown. No apparent external damage; however, critical operations were impacted. 5A Generator was unavailable for approximately 2 hours. Back-up systems initiated as expected. * * ACTIVITIES, PROCESSES, PROCEDURES INVOLVED: * System monitoring, S1.OP.AB-PB-0002, S1.OP-SO.PB-0011 * * WHY DID CONDITION HAPPEN? * Unknown. An in-depth investigation has been initiated. * * CONSEQUENCES: * Loss of a critical system, potential internal damage to 5A Generator * * REQUIREMENTS IMPACTED: * Critical operation, back-up system engagement * * ADVERSE PHYSICAL CONDITIONS: * High internal temperatures in 5A Generator, abrupt shutdown * * WHO WAS NOTIFIED: * Supervisor, Engineering Team, Maintenance Team, Safety Team * * KNOWLEDGEABLE INDIVIDUALS: * Engineering Team, Maintenance Team * * REPEAT OR SIMILAR CONDITION: * No * * IMMEDIATE ACTIONS AND RECOMMENDED ACTIONS: * Execute Emergency Procedure S1.OP.AB-PB-0013, Initiated thorough investigation, Arrange for component inspection * 12/05/2019 17:48:00 DAVID PHILLIPS (INCIDENT) * In-depth investigation is underway. Arrangements have been made for a specialist to inspect the generator. | What immediate actions were taken following the incident with the 5A Generator? | Execute Emergency Procedure S1.OP.AB-PB-0013, Initiated thorough investigation, Arrange for component inspection
105 | 2018-09-25 | 30841432 | 80235467 | 8C Pump abnormal vibration | S1CW -1CWE8 | * **************Incident Description************** * Notification 000030841432 Details * *********************************************************** * 09/25/2018 10:34:11 INCIDENT REPORT (INCIDENT REPORT) * Report submitted by: David Miller Entity\Incident: * * CONDITION DESCRIPTION/LOCATION (THE INAPPROPRIATE ACTION AND ITS NEGATIVE EFFECT/INCLUDE A DETAILED LOCATION DESCRIPTION): * During routine operations, an abnormal vibration was detected on the 8C Pump. Along with the unusual vibrations, the pump motor's current was fluctuating. Despite this fluctuation, no immediate failure occurred. However, the abnormal vibration can result in potential pump damage if not properly addressed. * * ACTIVITIES, PROCESSES, PROCEDURES INVOLVED: * Normal Pump Operation, Initial Vibration check. * * WHY DID CONDITION HAPPEN: * Unclear, possible underlying mechanical issue or foreign object within the pump system. * * CONSEQUENCES: * Potential mechanical damage or pump failure, leading to operational inefficiency or total loss of pump function. * * REQUIREMENTS IMPACTED: * Regular Pump Operation * * ADVERSE PHYSICAL CONDITIONS: * Abnormal vibration of 8C Pump, current fluctuation. * * WHO WAS NOTIFIED: * Operations Supervisor, Maintenance Team * * KNOWLEDGEABLE INDIVIDUALS: * Operations Supervisor, Maintenance Team, Engineering Team * * REPEAT OR SIMILAR CONDITION: * No, this is the first reported incident of abnormal vibration for this equipment. * * IMMEDIATE ACTIONS AND RECOMMENDED ACTIONS: * Operations have been advised to monitor the pump closely, while the maintenance team is planning a conditional assessment and potential maintenance work on the 8C Pump. * 09/26/2018 14:52:09 DAVID MILLER (INCIDENT) * Maintenance has scheduled a shutdown for 8C Pump to perform a thorough inspection and possible repair. The pump will be out of service till further notification. Will update the report once the issue gets resolved. | What immediate action has been taken following the detection of abnormal vibration in the pump? | Operations have been advised to monitor the pump closely, while the maintenance team is planning a conditional assessment and potential maintenance work on the 8C Pump.
106 | 2018-03-22 | 30754290 | 80235791 | Motor 18B high temperature | S1CW -1CWE2-MTRD | * **************Incident Description************** * Notification 000030754290 Details * *********************************************************** * SUMMARY: VALIDATE CURRENT GUIDELINES CONTAINED IN * ****PS-AB-110 "ISSUE ANALYSIS AND MANAGING PROCESS"***** * * 1) Condition Description/Location (The inappropriate action and its negative effect/Include a detailed location description): * At 1345 on 22/03/18 the operator noted high temperature in the 18B Motor. Immediate shut down from Unit 1 Control Room was performed and the temperature declined. Fire Department and Operations inspection found no fire, but smell of burnt wires was detected. Motor temperatures were higher than others currently in operation and no external signs of damage were seen. S1.OP-BA.CW-0002 Motor Abnormality was initiated due to the immediate shutdown of 18B Motor. * * 2) ACTIVITIES, PROCESSES, PROCEDURES INVOLVED: * S1.OP.AB-CW-0002, S1.OP-BO.CW-0002 * * 3) WHY DID CONDITION HAPPEN: * Uncertain, albeit motors have overheated previously * * 4) CONSEQUENCES: * No immediate consequences, but possible motor damage could result in loss of efficiency when the unit is back online. * * 5) REQUIREMENTS IMPACTED: * Non-functional motor * * 6) ADVERSE PHYSICAL CONDITION: * High temperature from 18B Motor, potential interior damage * * 7) WHO WAS NOTIFIED: * Control Room, Fire Department * * 8) KNOWLEDGEABLE INDIVIDUALS: * Adams, Stewart, Li * * 9) REPEAT OR SIMILAR CONDITION: * Inconclusive * * 10) IMMEDIATE AND RECOMMENDED ACTIONS: * Let Maintenance examine 18B Motor * * Updated: JASON DOE 22.03.2018 15:40:19 * ------------------------------------------------------------ * 27/03/2018 09:51:31 LUCY DOE ( | Who were the individuals knowledgeable about the incident with the 18B Motor? | Adams, Stewart, Li
107 | 2018-04-29 | 40914856 | 92286501 | IC coolant leaks on Motor 25B | S3CW -3CWE5 | * **************Incident Description************** * Notification 000040914856 Details * *********************************************************** * 04/29/2018 08:33:22 INCIDENT REPORT (INCIDENT REPORT) * Report submitted by: David Thomas ENTITY\INCIDENT: * * 1) CONDITION DESCRIPTION/LOCATION (THE INAPPROPRIATE ACTION AND ITS NEGATIVE EFFECT/INCLUDE A DETAILED LOCATION DESCRIPTION): * At 0822 on 04/29/2018, a coolant leak was noted on Motor 25B. This has caused pooling of coolant at the base of the motor. The motor temperature and pressures are normal with no signs of damage. However, due to the coolant leak, standard shutdown and repair procedures for Motor 25B have been instigated. * * 2) ACTIVITIES, PROCESSES, PROCEDURES INVOLVED: * S3.OP.AB-CW-0003, S3.OP-SO.CW-0003 * * 3) WHY DID CONDITION HAPPEN: * Possible leakage due to seal faults or damage to the cooling system. * * 4) CONSEQUENCES: * If unchecked, could result in overheating and motor failure. * * 5) REQUIREMENTS IMPACTED: * Potential downtime for repair. * * 6) ADVERSE PHYSICAL CONDITION: * Coolant leak on and around Motor 25B. * * 7) WHO WAS NOTIFIED: * Supervisor, Maintenance Team * * 8) KNOWLEDGEABLE INDIVIDUALS: * Watson, Harris, Thompson * * 9) REPEAT OR SIMILAR CONDITION: * No, unique issue. * * 10) IMMEDIATE AND RECOMMENDED ACTIONS: * Initiate shutdown of Motor 25B, engineer inspection, and repair. * * Updated: DAVID THOMAS 04.29.2018 09:01:34 * ------------------------------------------------------------ * 05/02/2018 07:42:53 KATE SMITH (ENGINEERING) * Inspection determined that the coolant leak was due to a faulty seal. Seal has been replaced, and the motor | What was the cause of the coolant leak on Motor 25B? | Inspection determined that the coolant leak was due to a faulty seal.
108 | 2019-11-12 | 30987512 | 80231507 | 24P Pump oil leak identification | S4CW -3CWE5 | * **************Incident Description************** * Notification 000030987512 Details * *********************************************************** * 11/12/2019 10:05:22 INCIDENT REPORT (INCIDENT REPORT) * Report submitted by: Steven Black 891-654-3210 ENTITY\INCIDENT: * CONDITION DESCRIPTION/LOCATION (THE INAPPROPRIATE ACTION AND ITS NEGATIVE EFFECT/INCLUDE A DETAILED LOCATION DESCRIPTION): * While carrying out the scheduled inspection, spotted 24P Pump oil leak. The oil leak was reported but the pump was still operational, however, the oil pressure was low and this could lead to further complications if not rectified. * * ACTIVITIES, PROCESSES, PROCEDURES INVOLVED: * Scheduled inspection and regular monitoring * WHY DID CONDITION HAPPEN? * Unknown, possible reasons may be corroded oil pipe, loose fittings, or failing pump seal. * * CONSEQUENCES: * Potential pump failure, oil pressure too low * * REQUIREMENTS IMPACTED: * Normal operation and maintenance schedule * * ADVERSE PHYSICAL CONDITIONS: * Oil leakage observed from pump * * WHO WAS NOTIFIED: * Control Room, Maintenance Team * * KNOWLEDGEABLE INDIVIDUALS: * Control Room Team, Maintenance Team, Anderson * * REPEAT OR SIMILAR CONDITION: * No, first-time observation * * IMMEDIATE ACTIONS AND RECOMMENDED ACTIONS: * Initiate oil pump repair or replacement as necessary, tighten up loose fittings and inspect the entire pumping system for similar issues. * 11/12/2019 14:35:50 STEVEN BLACK (INCIDENT) * Maintenance Team was immediately called in. Post inspection, the faulty oil pipe was replaced and fittings were properly tightened. Further inspection is required for ensuring system integrity. | What immediate actions were taken after the oil leak from the 24P Pump was reported? | Maintenance Team was immediately called in. Post inspection, the faulty oil pipe was replaced and fittings were properly tightened.
109 | 2018-05-23 | 30865893 | 90213490 | Low pressure from 7B Pump | S4CW -4CWE9 | * **************Incident Description************** * Notification 000030865893 Details * *********************************************************** * 05/23/2018 14:32:30 INCIDENT REPORT (INCIDENT REPORT) * Report submitted by: Sarah Johnson * * ENTITY\INCIDENT: * CONDITION DESCRIPTION/LOCATION (THE INAPPROPRIATE ACTION AND ITS NEGATIVE EFFECT/INCLUDE A DETAILED LOCATION DESCRIPTION): * During a standard operation, low pressure was detected on the 7B Pump. Outlet pressure was 35 bar, significantly lower than other similar pumps. No initial signs of leakage were visible. Based on pump behaviour, it does not typically operate with such low pressure. * * ACTIVITIES, PROCESSES, PROCEDURES INVOLVED: * Standard operational check * * WHY DID CONDITION HAPPEN? * Unclear, potential pump wear or damage. * * CONSEQUENCES: * Possible disruption in operations, damage to pump * * REQUIREMENTS IMPACTED: * Normal operation flow * * ADVERSE PHYSICAL CONDITIONS: * Low pressure at pump outlet with unknown cause * * WHO WAS NOTIFIED: * Operations Supervisor, Maintenance Team * * KNOWLEDGEABLE INDIVIDUALS: * Maintenance Manager, Operations Supervisor * * REPEAT OR SIMILAR CONDITION: * No, first occurrence * * IMMEDIATE ACTIONS AND RECOMMENDED ACTIONS: * Planning for immediate inspection and possible repair. If the problem persists, pump replacement may be required. * 05/24/2018 09:23:37 SARAH JOHNSON (INCIDENT REPORT) * The inspection revealed some internal wear of the pump components causing the low pressure. Parts were ordered and pump repair is scheduled for next maintenance window. | What was the immediate action taken when low pressure was detected on the 7B Pump? | Planning for immediate inspection and possible repair. If the problem persists, pump replacement may be required.
110 | 2018-04-10 | 30785612 | 80199145 | Unusual vibration in Motor 26B | S4CW -4CWE2 | * **************Incident Description************** * Notification 000030785612 Details * *********************************************************** * 04/10/2018 14:35:21 INCIDENT REPORT (INCIDENT REPORT) * Report submitted by: Robert Adams ENTITY\INCIDENT: * * CONDITION DESCRIPTION/LOCATION (THE INAPPROPRIATE ACTION AND ITS NEGATIVE EFFECT/INCLUDE A DETAILED LOCATION DESCRIPTION): * During routine inspection, abnormal vibration was noted from Motor 26B. All other parameters were in range but the vibration could potentially lead to damage if not addressed. * * ACTIVITIES, PROCESSES, PROCEDURES INVOLVED: * Routine inspection * WHY DID CONDITION HAPPEN? * Unknown, possibly due to unbalanced load or bearing failure. * * CONSEQUENCES: * If left unchecked, could result in damage to motor resulting in downtime and repair costs. * * REQUIREMENTS IMPACTED: * Regular Operation and maintenance. * * ADVERSE PHYSICAL CONDITIONS: * High vibration levels observed in motor. * * WHO WAS NOTIFIED: * Maintenance Supervisor and Operations Manager. * * KNOWLEDGEABLE INDIVIDUALS: * Maintenance Team. * * REPEAT OR SIMILAR CONDITION: * Similar conditions have been identified but not with this motor. * * IMMEDIATE ACTIONS AND RECOMMENDED ACTIONS: * Isolate and inspect motor for causes of vibration. Possible examination of rotor and bearings. * 04/12/2018 10:23:56 ROBERT ADAMS (INCIDENT) * Upon further investigation, a misalignment issue was found. Misalignment has been rectified and motor is now running smoothly. | What immediate actions were recommended when abnormal vibration was found in Motor 26B? | Isolate and inspect motor for causes of vibration. Possible examination of rotor and bearings.
111 | 2020-05-01 | 30980212 | 80962215 | Unusual heat increase in 28B Motor | S4CW -4CWE5 | * **************Incident Description************** * Notification 000030980212 Details * *********************************************************** * 05/01/2020 13:47:20 INCIDENT REPORT (INCIDENT REPORT) * Report submitted by: Tom Green ENTITY\INCIDENT: * * CONDITION DESCRIPTION/LOCATION (THE INAPPROPRIATE ACTION AND ITS NEGATIVE EFFECT/INCLUDE A DETAILED LOCATION DESCRIPTION): * On 5/1/20 at 1300, the 28B Motor was reported to have overheating issues. The motor was immediately shut down from the Unit Control Room and the heat subsided. On inspecting the unit, a faint smell of charred insulation was noted. A temperature comparison with other motors did not reveal any anomalies, exterior motor damage was not detected. Abnormality procedure for 28B Motor, S4.OP-AB.CW-0003 was enforced. * * ACTIVITIES, PROCESSES, PROCEDURES INVOLVED: * S4.OP.AB-CW-0003, S4.OP-SO.CW-0002 * * WHY DID CONDITION HAPPEN: * The cause remains unidentified but similar overheating issues have been observed earlier * * CONSEQUENCES: * No immediate damage, but potential wear could lead to decreased effectiveness when the machine is operated again. * * REQUIREMENTS IMPACTED: * Loss of a functional motor * * ADVERSE PHYSICAL CONDITION: * High heat levels in 28B Motor; potential internal damage * * WHO WAS NOTIFIED: * Control Room and Maintenance Team * * KNOWLEDGEABLE INDIVIDUALS: * Daniels, Robinson, Miller * * REPEAT OR SIMILAR CONDITION: * Not known * * IMMEDIATE AND RECOMMENDED ACTIONS: * Immediate assessment of 28B Motor * * Updated: TOM GREEN 05.01.2020 14:45:27 * ------------------------------------------------------------ * 05/12/2020 09:35:51 JULIE DOE (NUSER) * It was discovered after a thorough investigation, the failure was not electrical. The heat | What was the reported issue with the 28B Motor on 5/1/20? | The 28B Motor was reported to have overheating issues. The motor was immediately shut down from the Unit Control Room and the heat subsided.
112 | 2021-02-14 | 31020780 | 90232071 | Heat Above Average on 34B Transformer | S1T -1TRF6 | * **************Incident Description************** * Notification 000031020780 Details * *********************************************************** * 02/14/2021 08:34:47 INCIDENT REPORT (INCIDENT REPORT) * Report submitted by: Mark Wilson * * 1) CONDITION DESCRIPTION/LOCATION (THE INAPPROPRIATE ACTION AND ITS NEGATIVE EFFECT/INCLUDE A DETAILED LOCATION DESCRIPTION): * During the regular check, 34B Transformer was reported to exhibit noticeably higher temperature than normal, though within operational limits. To prevent overheating, Transformer 34B was shut down and moved to the cooling stage. Initial inspections did not note any abnormal condition or external damage. Transformer temperatures are now normal; however, it's functioning will be carefully supervised to ensure safe operation. S1.OP-AB.TF-0002 Transformer Abnormality was triggered because of this event. * * 2) ACTIVITIES, PROCESSES, PROCEDURES INVOLVED: * S1.OP.AB-TF-0002, S1.OP-SO.TF-0001 * * 3) WHY DID CONDITION HAPPEN: * Unknown, although transformers have faced overheating issues before. * * 4) CONSEQUENCES: * Potential transformer damage, reducing efficiency upon escalation. * * 5) REQUIREMENTS IMPACTED: * Transformer downtime * * 6) ADVERSE PHYSICAL CONDITION: * High Heat from 34B Transformer; possible internal malfunction. * * 7) WHO WAS NOTIFIED: * Control Room, Maintenance Team * * 8) KNOWLEDGEABLE INDIVIDUALS: * Peterson, Gomez, Clark * * 9) REPEAT OR SIMILAR CONDITION: * Yes, in different equipment. * * 10) IMMEDIATE AND RECOMMENDED ACTIONS: * Further investigation and constant monitoring of 34B Transformer * * Updated: MARK WILSON 2.14.2021 10:03:19 * ------------------------------------------------------------ * 02/14/2021 18:15:45 JOHN DOE (MAINTAINANCE TEAM) * After a deeper inspection, | What immediate action was taken when an abnormality was detected in the 34B Transformer? | To prevent overheating, Transformer 34B was shut down and moved to the cooling stage.
113 | 2020-03-05 | 31022562 | 90233023 | Leakage in 17B Condensate Pump | S4CW -4CWE8 | * **************Incident Description************** * Notification 000031022562 Details * *********************************************************** * 03/05/2020 11:35:56 INCIDENT REPORT (INCIDENT REPORT) * Report submitted by: Laura Hayes ENTITY\INCIDENT: * * CONDITION DESCRIPTION/LOCATION (THE INAPPROPRIATE ACTION AND ITS NEGATIVE EFFECT/INCLUDE A DETAILED LOCATION DESCRIPTION): * In morning rounds, a small leak was observed in 17B Condensate Pump, specifically at the rotary seal region, contributing to water wastage and potential long-term damage. Rotary seal of the pump is suspected to be faulty, requiring immediate replacement to ensure continued safe and efficient operation. * * ACTIVITIES, PROCESSES, PROCEDURES INVOLVED: * Morning rounds, normal pump operation * * WHY DID CONDITION HAPPEN? * Expected seal wear and tear or possible damage during the last maintenance, this is currently unknown and would require further investigation. * * CONSEQUENCES: * Loss of water, possible damage to the pump and surroundings, potential operational disruption if unchecked. * * REQUIREMENTS IMPACTED: * Operational efficiency, resource management * * ADVERSE PHYSICAL CONDITIONS: * Water leakage from pump, possible flooding * * WHO WAS NOTIFIED: * Shift Supervisor, Maintenance Department * * KNOWLEDGEABLE INDIVIDUALS: * Shift Supervisor, Maintenance Team, Senior Engineers * * REPEAT OR SIMILAR CONDITION: * No, this is the first occurrence * * IMMEDIATE ACTIONS AND RECOMMENDED ACTIONS: * Initiate S4.OP-AB.CW-0003, the leakage response procedure. Maintenance Department to inspect and replace the faulty seal promptly. * 03/05/2020 15:00:42 LAURA HAYES (INCIDENT) * The rotary seal has been replaced and the pump is now operating normally, without any detected leakage. A review of maintenance operations is recommended to prevent similar incidents in the future. | What immediate actions were taken and recommended when the leak was observed in the pump? | Initiate S4.OP-AB.CW-0003, the leakage response procedure. Maintenance Department to inspect and replace the faulty seal promptly.
114 | 2019-02-25 | 30895219 | 90235678 | 7B Pump excessive vibration | S4CW -4CWE2 | * **************Incident Description************** * Notification 000030895219 Details * *********************************************************** * 02/25/2019 16:23:00 INCIDENT REPORT (INCIDENT REPORT) * Report submitted by: Daniel Green ENTITY\INCIDENT: * * CONDITION DESCRIPTION/LOCATION (THE INAPPROPRIATE ACTION AND ITS NEGATIVE EFFECT/INCLUDE A DETAILED LOCATION DESCRIPTION): * During a regular inspection, operator noted excessive vibration from the 7B Pump. The vibrations caused the emergency shutdown of the pump from Unit 4 control room. Post-shutdown, an inspection was carried out and no visible external damage was found on the pump. Cross-checks with other pumps currently in operation revealed that the temperature and pressure parameters were normal. * * ACTIVITIES, PROCESSES, PROCEDURES INVOLVED: * Regular inspection, S2.OP.AB-CW-0003, S2.OP-SO.CW-0021 * * WHY DID CONDITION HAPPEN? * The cause is uncertain at this moment. Excessive vibrations could be due to misalignment, imbalance or bearing failure in the pump. * * CONSEQUENCES: * Potential premature wear and damage to pump components which can lead to operational downtime if not addressed quickly. * * REQUIREMENTS IMPACTED: * Regular operation. * * ADVERSE PHYSICAL CONDITIONS: * Excessive vibration on 7B Pump, likely internal issue. * * WHO WAS NOTIFIED: * Supervisor, Maintenance Team * * KNOWLEDGEABLE INDIVIDUALS: * Anderson, Robinson, Clark * * REPEAT OR SIMILAR CONDITION: * No, this is the first incident of this kind. * * IMMEDIATE ACTIONS AND RECOMMENDED ACTIONS: * Maintenance to thoroughly inspect 7B Pump, investigate vibration source, and repair as necessary. * 02/27/2019 18:00:10 DANIEL GREEN (INCIDENT) * After a comprehensive inspection of the 7B Pump, it was concluded that the damage was due to a broken bearing. The bearing has been replaced and the pump is back in operation. | What was the cause of the excessive vibration in the 7B Pump? | The damage was due to a broken bearing.
115 | 2020-09-25 | 31700239 | 80213049 | Leaking observed in 7A CW pump | S4CW -4CWE7 | * **************Incident Description************** * Notification 000031700239 Details * *********************************************************** * 09/25/2020 10:21:27 INCIDENT REPORT (INCIDENT REPORT) * Report submitted by: Samuel Johnson ENTITY\INCIDENT: * * CONDITION DESCRIPTION/LOCATION (THE INAPPROPRIATE ACTION AND ITS NEGATIVE EFFECT/INCLUDE A DETAILED LOCATION DESCRIPTION): * At 1021 on 9/25/20, during periodic checkup, the team noticed a slow leak from the 7A CW Pump. 7A Pump was immediately isolated and shut-down from Unit 4 Control Room to prevent possible damage. Inspection did not reveal any immediate signs of damage, however, the leak could result in long term inefficiencies or catastrophic pump failure if not addressed promptly. An abnormality was initiated due to this incident. * * ACTIVITIES, PROCESSES, PROCEDURES INVOLVED: * S4.OP.AB-CW-0007, S4.OP-SO.CW-0001 * * WHY DID CONDITION HAPPEN: * Possible wear and tear or material failure. * * CONSEQUENCES: * Potential pump failure, resultant downtime, and system inefficiency. * * REQUIREMENTS IMPACTED: * Normal operation of CW system * * ADVERSE PHYSICAL CONDITIONS: * Leak from 7A CW pump * * WHO WAS NOTIFIED: * Supervisor, Maintenance team * * KNOWLEDGEABLE INDIVIDUALS: * Supervisor, Johnson, Smith * * REPEAT OR SIMILAR CONDITION: * Not Known * * IMMEDIATE ACTIONS AND RECOMMENDED ACTIONS: * Maintenance to inspect and repair 7A Pump * * 09/30/2020 14:33:15 EMILY ROSE (MAINTENANCE) * The investigation revealed the leakage was due to a faulty seal. The seal has been replaced and after re-testing, the pump is back in operation with no signs of leakage. Barring any unforeseen problems, the pump should remain operational. | What was the cause of the leak in the 7A CW Pump? | The investigation revealed the leakage was due to a faulty seal.
116 | 2019-05-15 | 30876842 | 90135214 | Vibration in Pump 17B | S4CW -4CWE7 | * **************Incident Description************** * Notification 000030876842 Details * *********************************************************** * 05/15/2019 16:07:34 INCIDENT REPORT (INCIDENT REPORT) * Report submitted by: Robert Wilson 321-654-0987 ENTITY\INCIDENT: * CONDITION DESCRIPTION/LOCATION (THE INAPPROPRIATE ACTION AND ITS NEGATIVE EFFECT/INCLUDE A DETAILED LOCATION DESCRIPTION): * During daily equipment inspection, it was reported that Pump 17B exhibited an abnormal vibration. Pump operating pressure and temperature were within the permissible range. The sudden vibration during operation can lead to potential damage to the pump or its connections. * * ACTIVITIES, PROCESSES, PROCEDURES INVOLVED: * Daily equipment check * WHY DID CONDITION HAPPEN? * Unknown, possible mechanical failure or imbalance in pump * * CONSEQUENCES: * Potential for pump failure, might lead to production loss if not addressed * * REQUIREMENTS IMPACTED: * Smooth operation * * ADVERSE PHYSICAL CONDITIONS: * High vibration level at pump with no known cause * * WHO WAS NOTIFIED: * Supervisor/ INCIDENT TEAM * * KNOWLEDGEABLE INDIVIDUALS: * Incident Team, Maintenance Engineer * * REPEAT OR SIMILAR CONDITION: * No, first time * * IMMEDIATE ACTIONS AND RECOMMENDED ACTIONS: * Stop pump operation, perform immediate full inspection * 05/15/2019 19:24:48 ROBERT WILSON (INCIDENT) * An inspection revealed that the pump's impeller was out of balance causing the vibration and it was replaced immediately, restoring the pump's normal operation. | What immediate action was recommended following the abnormal vibration of Pump 17B? | Stop pump operation, perform immediate full inspection
117 | 2016-09-18 | 30781509 | 80266975 | Sudden Pressure Rise in 18B Valve | S4CW -4CWE7-VLV | * **************Incident Description************** * Notification 000030781509 Details * *********************************************************** * 09/18/2016 14:08:32 INCIDENT REPORT (INCIDENT REPORT) * Report submitted by: Daniel Thompson ENTITY\INCIDENT: * * CONDITION DESCRIPTION/LOCATION (THE INAPPROPRIATE ACTION AND ITS NEGATIVE EFFECT/INCLUDE A DETAILED LOCATION DESCRIPTION): * At approximately 1325 hours, a sudden pressure rise was detected on 18B Valve. Following emergency protocols, the valve network was shut down from the Unit 4 Control Room. A subsequent inspection revealed a potential breach in the valve gasket. No injuries reported but operation halted temporarily due to the incident. * * ACTIVITIES, PROCESSES, PROCEDURES INVOLVED: * S4.OP.AB-VL-0002 involved and S4.OP-SO.VL-0011 * * WHY DID CONDITION HAPPEN? * The specific cause is unverified at this time. Possible reasons include gasket wear or tightening issue during maintenance. * * CONSEQUENCES: * Temporary halt in operations and potential valve damage * * REQUIREMENTS IMPACTED: * Operational continuity * * ADVERSE PHYSICAL CONDITIONS: * Overpressurization of 18B Valve, possible damage to gasket * * WHO WAS NOTIFIED: * Control Room, Incident Response Team * * KNOWLEDGEABLE INDIVIDUALS: * Miller, Garcia, Wong * * REPEAT OR SIMILAR CONDITION: * Not known, needs checking * * IMMEDIATE ACTIONS AND RECOMMENDED ACTIONS: * Investigation by Maintenance & Engineering Team to finalize cause and to verify the integrity of other valves in the system. * 09/20/2016 11:55:41 DAVID JOHN (INCIDENT) * Investigation confirmed the gasket failure causing the pressure rise. The damaged gasket has been replaced and safety checks performed successfully. System is now operational. Further analysis needed to define the cause and possible prevention mechanisms. | What immediate actions were recommended after the incident? | Investigation by Maintenance & Engineering Team to finalize cause and to verify the integrity of other valves in the system.
118 | 2022-01-06 | 30872390 | 80245490 | 33B Pump irregular vibration | S4CW -4CWE2 | * **************Incident Description************** * Notification 000030872390 Details * *********************************************************** * 01/06/2022 14:15:46 INCIDENT REPORT (INCIDENT REPORT) * Report submitted by: David Taylor ENTITY\INCIDENT: * * CONDITION DESCRIPTION/LOCATION (THE INAPPROPRIATE ACTION AND ITS NEGATIVE EFFECT/INCLUDE A DETAILED LOCATION DESCRIPTION): * During routine maintenance inspection, it was observed that the 33B Pump exhibited an irregular vibration. Initial measurements revealed vibrations beyond standard values. No immediate threats were detected however prolonged operation under such conditions could lead to catastrophic failure. * * ACTIVITIES, PROCESSES, PROCEDURES INVOLVED: * Routine maintenance inspection involving S4.OP-AB.CW-0003 and S4.OP-SO.CW-0003 * * WHY DID CONDITION HAPPEN? * Unknown at present time, potential misalignment or bearing issue. * * CONSEQUENCES: * Potential pump failure leading to safety risks and process downtime. * * REQUIREMENTS IMPACTED: * Routine operation check process and operational safety. * * ADVERSE PHYSICAL CONDITIONS: * Irregular vibrations originating from 33B Pump motor. * * WHO WAS NOTIFIED: * Maintenance Supervisor, Safety Department * * KNOWLEDGEABLE INDIVIDUALS: * David Taylor, Maintenance Supervisor, Lead Technician * * REPEAT OR SIMILAR CONDITION: * No similar incidents pertaining to this machine have been recorded. * * IMMEDIATE ACTIONS AND RECOMMENDED ACTIONS: * Cease operation of 33B Pump, execute detail inspection and necessary repair work. * 01/10/2022 08:35:17 DAVID TAYLOR (INCIDENT) * Repair work on 33B completed and the pump is back in service post successful test run. The root cause was misalignment which has been corrected. Procedure S4.OP-SO.CW-0003 to be revised to incorporate additional inspection steps. | What immediate action was recommended when irregular vibrations were noticed in the 33B Pump? | Cease operation of 33B Pump, execute detail inspection and necessary repair work.
119 | 2018-03-19 | 30801245 | 80245678 | 12D Pump abnormal vibrations | S1CW -1CWE9-PMP | * **************Incident Description************** * Notification 000030801245 Details * *********************************************************** * 19/03/2018 14:35:42 INCIDENT REPORT (INCIDENT REPORT) * Report submitted by: Luke Thompson 987-654-3210 ENTITY\INCIDENT: * CONDITION DESCRIPTION/LOCATION (THE INAPPROPRIATE ACTION AND ITS NEGATIVE EFFECT/INCLUDE A DETAILED LOCATION DESCRIPTION): * During a routine pass, notice was taken of the 12D Pump, where it was generating abnormal vibrations. As a part of unit 1, the 12D Pump is supposed to function seamlessly, but it hasn't been the case lately. The pump has been isolated pending further investigation. * * ACTIVITIES, PROCESSES, PROCEDURES INVOLVED: * Routine monitoring, S1.OP.AB-CW-0009, S1.OP-SO.CW-0011 * * WHY DID CONDITION HAPPEN? * Uncertain. Possible wear and tear or alignment issues. * * CONSEQUENCES: * Could result to possible damage to the pump or loss of efficiency in pump operation. * * REQUIREMENTS IMPACTED: * Essential operation of 12D pump * * ADVERSE PHYSICAL CONDITIONS: * Abnormal vibrations from pump * * WHO WAS NOTIFIED: * Maintenance Team, Department Supervisor * * KNOWLEDGEABLE INDIVIDUALS: * Anderson, Taylor, Taylor * * REPEAT OR SIMILAR CONDITION: * Yes, few past instances * * IMMEDIATE ACTIONS AND RECOMMENDED ACTIONS: * Initiated vibration analysis, consider realignment or replacement if necessary. * 19/03/2018 17:47:23 LUKE THOMPSON (INCIDENT) * Maintenance team is performing a thorough vibration analysis. If the vibrations continue, a recommendation for replacement will be made. | What immediate and recommended actions were taken in response to the noticed abnormal vibrations from the 12D Pump? | Initiated vibration analysis, consider realignment or replacement if necessary.
120 | 2020-12-01 | 30985074 | 90236540 | Overheating of motor 18A | S4CW -4CWE8 | * **************Incident Description************** * Notification 000030985074 Details * *********************************************************** * 12/01/2020 10:30:02 INCIDENT REPORT (INCIDENT REPORT) * Report submitted by: Richard Johnson ENTITY\INCIDENT: * * CONDITION DESCRIPTION/LOCATION (THE INAPPROPRIATE ACTION AND ITS NEGATIVE EFFECT/INCLUDE A DETAILED LOCATION DESCRIPTION): * At 10:00 on 12/1/20, an abnormal heat reading was detected from the motor of 18A Pump. The Pump was immediately shut down from the main Control Room. * Further inspection revealed no visible damage, but a higher than average temperature for an inactive motor. This could potentially indicate internal damage. Subsequent procedures were initiated in accordance with S4.OP-AB.CW-0002 Motor Damaging Heat Issue. * * ACTIVITIES, PROCESSES, PROCEDURES INVOLVED: * S4.OP-AB.CW-0002, S4.OP-SO.CW-0002 * * WHY DID CONDITION HAPPEN: * The exact cause is unknown, however previous instances of motor heat issues have been attributed to worn-out parts or debris in the motor. * * CONSEQUENCES: * Potential complete motor failure, leading to longer downtime and higher maintenance costs. * * REQUIREMENTS IMPACTED: * Expected pump availability, potential delay in operations. * * ADVERSE PHYSICAL CONDITIONS: * Excessive heat from motor 18A, potential internal damage. * * WHO WAS NOTIFIED: * Engineering team, Control Room, Maintenance Team. * * KNOWLEDGEABLE INDIVIDUALS: * Richard Johnson, Tom Davidson, Lisa White * * REPEAT OR SIMILAR CONDITION: * Yes, has happened before but each incident was isolated. * * IMMEDIATE ACTIONS AND RECOMMENDED ACTIONS: * Engineering team to inspect and evaluate the root cause of the overheating. If necessary, maintenance will have to replace the motor or appropriate components. * 12/05/2020 16:45:58 RICHARD JOHNSON (INCIDENT) * The motor overheating was due to worn-out parts | What caused the overheating of the motor of pump 18A? | The motor overheating was due to worn-out parts.
121 | 2014-02-25 | 30743406 | 80218225 | Odd behavior from 3B pump | S1RW -1RWE1-LBDN | * **************Incident Description************** * Notification 000030743406 Details * *********************************************************** * 02/25/2014 07:44:10 INCIDENT REPORT (INCIDENT REPORT) * Report submitted by: Peter Thomas ENTITY\INCIDENT: * * CONDITION DESCRIPTION/LOCATION (THE INAPPROPRIATE ACTION AND ITS NEGATIVE EFFECT/INCLUDE A DETAILED LOCATION DESCRIPTION): * At 0744 on 2/25/14, the operator reported that 3B Pump demonstrated abnormal behavior - alternating between high and low pressure. No external physical damage was observed. Anomalies persisted even after resetting the system. * * ACTIVITIES, PROCESSES, PROCEDURES INVOLVED: * S1.OP.RW.PP-0003, S1.OP.PH.PP-0004 * * WHY DID CONDITION HAPPEN? * Basis for this condition is indeterminate although fluctuations in the power supply or a faulty internal component could be possible causes. * * CONSEQUENCES: * Possible degradation of pump efficiency, premature wear of internal components, potential system malfunction. * * REQUIREMENTS IMPACTED: * Normal operation of the pump under stable conditions. * * ADVERSE PHYSICAL CONDITIONS: * Inconsistent pressure readings from 3B pump. * * WHO WAS NOTIFIED: * Plant Supervisor, Maintenance Team * * KNOWLEDGEABLE INDIVIDUALS: * Peters, Johnson, Santos * * REPEAT OR SIMILAR CONDITION: * No * * IMMEDIATE ACTIONS AND RECOMMENDED ACTIONS: * System reset was performed. Recommended actions include deeper investigation to identify the root cause, and potential component replacement if fault found internally. * 02/27/2014 14:18:08 PETER THOMAS (INCIDENT) * Post evaluation, it was identified that the inconsistent pressure readings resulted from a faulty pressure sensor. The sensor was replaced and the pump is functioning normally thereafter. Ensure preventative maintenance for the sensors is conducted timely to avoid occurrence of similar incidents. | What was the identified cause of the abnormal behavior in the 3B Pump? | Post evaluation, it was identified that the inconsistent pressure readings resulted from a faulty pressure sensor.
122 | 2022-04-30 | 30982130 | 80670982 | Fluctuations in 10B Pump speed | S4CW -4CWE5 | * ************** Incident Description ************** * Notification 000030982130 Details * *********************************************************** * 04/30/2022 14:37:00 INCIDENT REPORT (INCIDENT REPORT) * Report submitted by: David Wilson ENTITY\INCIDENT: * * CONDITION DESCRIPTION/LOCATION (THE INAPPROPRIATE ACTION AND ITS NEGATIVE EFFECT/INCLUDE A DETAILED LOCATION DESCRIPTION): * Upon routine checks, the 10B Pump was observed to have sudden variations in its operating speed, with speed surges and drops occurring intermittently. The erratic activity was noticed in the Control Room where the 10B Pump control speed is monitored. * * ACTIVITIES, PROCESSES, PROCEDURES INVOLVED: * S4.OP.AB-CW-0001, S4.OP-SO.CW-0001 * * WHY DID CONDITION HAPPEN? * Unknown. This has not been reported for the pump in its current service. * * CONSEQUENCES: * Fluctuations could potentially harm the pump's motor and affect the pump's operational efficiency. * * REQUIREMENTS IMPACTED: * Unexpected pump behavior * * ADVERSE PHYSICAL CONDITIONS: * Fluctuating speeds in the 10B Pump motor * * WHO WAS NOTIFIED: * Control Room, Maintenance Division * * KNOWLEDGEABLE INDIVIDUALS: * Peterson, Clark, Roberts * * REPEAT OR SIMILAR CONDITION: * No, first of such occurrence * * IMMEDIATE ACTIONS AND RECOMMENDED ACTIONS: * Immediate action to diagnose and troubleshoot the 10B Pump System. * 04/30/2022 16:59:20 DAVID WILSON (INCIDENT) * Diagnosis process ongoing. Further updates to follow upon complete understanding of the underlying issue. | What was the observed problem with the 10B Pump and what could potentially be its consequences? | Upon routine checks, the 10B Pump was observed to have sudden variations in its operating speed, with speed surges and drops occurring intermittently. The erratic activity was noticed in the Control Room where the 10B Pump control speed is monitored. Fluctuations could potentially harm the pump's motor and affect the pump's operational efficiency.
123 | 2020-12-11 | 30812746 | 80394521 | 14B Generator has an oil leak | S1G -1GWE7-GENR | * **************Incident Description************** * Notification 000030812746 Details * *********************************************************** * 12/11/2020 10:23:07 INCIDENT REPORT (INCIDENT REPORT) * Report submitted by: Peter Wilson 321-654-0987 ENTITY\INCIDENT: * * CONDITION DESCRIPTION/LOCATION (THE INAPPROPRIATE ACTION AND ITS NEGATIVE EFFECT/INCLUDE A DETAILED LOCATION DESCRIPTION): * On 12/11/2020, during routine maintenance work, the team noticed an oil leak on 14B Generator. The oil leak was observed at the bottom of the motor. Work was immediately stopped and 14B Generator was shut down. An emergency cleanup was carried out to contain the oil spill and prevent any environmental damage. * * ACTIVITIES, PROCESSES, PROCEDURES INVOLVED: * S1.OP.AB-GW-0001, S1.OP-SO.GW-0001 * * WHY DID CONDITION HAPPEN? * Now it's unknown - possible causes could be wear and tear over time or a potential failure in a component part. * * CONSEQUENCES: * Possible environmental damage, equipment damage, costs related to cleanup and repair. * * REQUIREMENTS IMPACTED: * Environmental requirements, equipment operation * * ADVERSE PHYSICAL CONDITIONS: * Oil leak under the 14B Generator * * WHO WAS NOTIFIED: * Maintenance Supervisor, Environmental Safety Officer * * KNOWLEDGEABLE INDIVIDUALS: * Operations Team, Maintenance Team * * REPEAT OR SIMILAR CONDITION: * No * * IMMEDIATE ACTIONS AND RECOMMENDED ACTIONS: * Maintenance Team to further inspect and repair 14B Generator. Environmental safety to verify the area is clear and safe post cleanup. * 12/11/2020 12:17:34 PETER WILSON (INCIDENT) * Notified maintenance. Immediate inspection and repair scheduled. Environmental safety confirmed the area is now clear and safe. | What immediate actions were taken following the oil leak incident on 14B Generator? | Work was immediately stopped and 14B Generator was shut down. An emergency cleanup was carried out to contain the oil spill and prevent any environmental damage. Maintenance Team to further inspect and repair 14B Generator. Environmental safety to verify the area is clear and safe post cleanup. Immediate inspection and repair scheduled. Environmental safety confirmed the area is now clear and safe.
124 | 2021-11-03 | 30894523 | 82234521 | Unusual Vibrations from turbine T3A | S4TR -4TRL6 | * ****************Incident Description******************** * Notification 000030894523 Details * ************************************************************** * 11/03/2021 13:45:56 INCIDENT REPORT (INCIDENT REPORT) * Report submitted by: Emily Harris ENTITY\INCIDENT: * * CONDITION DESCRIPTION/LOCATION (THE INAPPROPRIATE ACTION AND ITS NEGATIVE EFFECT/INCLUDE A DETAILED LOCATION DESCRIPTION): * At 1300 on the 3rd of November, unusual vibrations were detected from the T3A Turbine. An emergency shutdown was initiated. Turbine T3A was taken off the unit 4 operational grid and the vibration ceased. Engineering team inspection was not able to pinpoint the root cause, but noticed signs of wear and tear on the turbine blades. * * ACTIVITIES, PROCESSES, PROCEDURES INVOLVED: * S4.OP.TR-0001, S4.OP-SO.TR-0002 * * WHY DID CONDITION HAPPEN: * Unclear, although overuse could be a contributor. * * CONSEQUENCES: * Potential turbine damage and loss of efficiency when the unit returns online. * * REQUIREMENTS IMPACTED: * Normal operation * * ADVERSE PHYSICAL CONDITION: * Unusual vibration from T3A Turbine, possible internal damage * * WHO WAS NOTIFIED: * Unit 4 Control Room, Engineering team * * KNOWLEDGEABLE INDIVIDUALS: * Michaels, Jacobs, Bronte * * REPEAT OR SIMILAR CONDITION: * No * * IMMEDIATE AND RECOMMENDED ACTIONS: * Engineering team to further investigate the issue with T3A Turbine * * Updated: EMILY HARRIS 11.03.2021 14:50:23 * ----------------------------------------------------------- * 11/09/2021 10:19:32 JOHN DOE (NUSER) * The further investigation revealed that an increased build-up of debris had resulted in causing the friction that consequently led to the unusual vibrations. The official report outlined that the debris was successfully cleared and the worn-out blades replaced. The Turbine is now back in operation. | What caused the unusual vibrations in the T3A Turbine? | The further investigation revealed that an increased build-up of debris had resulted in causing the friction that consequently led to the unusual vibrations.
125 | 2019-03-26 | 30888293 | 80222356 | Unexpected power surge in 23A Pump | S3CW -3CWE4 | * **************Incident Description************** * Notification 000030888293 Details * *********************************************************** * 03/26/2019 17:22:16 INCIDENT REPORT (INCIDENT REPORT) * Report submitted by: Fredrick Winston ENTITY\INCIDENT: * * CONDITION DESCRIPTION/LOCATION (THE INAPPROPRIATE ACTION AND ITS NEGATIVE EFFECT/INCLUDE A DETAILED LOCATION DESCRIPTION): * At 1715 on 3/26/19 the operator noted an unexpected increase in power usage on the 23A Pump. Emergency shutdown was performed from Unit 3 Control Room. Post-shutdown inspection revealed signs of stress on the motor and abnormal readings. Investigations into the nature of the power surge are ongoing. * * ACTIVITIES, PROCESSES, PROCEDURES INVOLVED: * S3.OP.AB-CW-0002, S3.OP-SO.CW-0003 * * WHY DID CONDITION HAPPEN? * Unknown, although some indications suggest possible internal electrical fault. * * CONSEQUENCES: * Potential for significant damage to the pump motor, which would impact operations when the unit is brought back online. * * REQUIREMENTS IMPACTED: * Regular operations, power consumption normalization * * ADVERSE PHYSICAL CONDITIONS: * High power usage from 23A pump, potential internal damage to pump motor * * WHO WAS NOTIFIED: * Control Room, Maintenance Team * * KNOWLEDGEABLE INDIVIDUALS: * Peterson, Clark, Watson * * REPEAT OR SIMILAR CONDITION: * No * * IMMEDIATE ACTIONS AND RECOMMENDED ACTIONS: * Further inspection of 23A Pump motor, verify power supply integrity * * Updated: FREDRICK WINSTON 03.26.2019 19:49:22 * ------------------------------------------------------------ * 04/02/2019 13:30:45 HENRY TAYLOR (NUSER) * Inspection completed. It was found that there was an internal fault in the motor windings leading to an abnormal current flow. The motor was reconditioned, and the pump is now | What immediate action was taken when the unexpected power usage increase on the 23A Pump was noted? | Emergency shutdown was performed from Unit 3 Control Room.
126 | 2018-03-13 | 30842115 | 80236524 | Overheating observed in 30A pump | S4CW -4CWE1 | * **************Incident Description************** * Notification 000030842115 Details * *********************************************************** * 03/13/2018 15:20:23 INCIDENT REPORT (INCIDENT REPORT) * Report submitted by: Simon Johnson ENTITY\INCIDENT: * * CONDITION DESCRIPTION/LOCATION (THE INAPPROPRIATE ACTION AND ITS NEGATIVE EFFECT/INCLUDE A DETAILED LOCATION DESCRIPTION): * At approximately 1520 hours on 13/03/18, the operator observed an overheating condition in the 30A Pump motor during the routine inspection. Despite no abnormal load conditions, the motor temperature was 20% higher than other similar pumps. The motor was immediately isolated and the system shifted to its secondary channel for normal operations. A faint smell of overheated insulation was noted, however, no smoke or fire was observed. * * ACTIVITIES, PROCESSES, PROCEDURES INVOLVED: * S4.OP.AB-CW-0001, S4.OP-SO.CW-0001 * * WHY DID CONDITION HAPPEN: * The cause of the overheating is not yet known. There have been previous instances of similar conditions resulting from inbuilt anomalies within the pump system * * CONSEQUENCES: * Temporary loss of primary pumping system. Potential risk of pump failure or fire in case of severe overheating. * * REQUIREMENTS IMPACTED: * Regular operations and safety procedures * * ADVERSE PHYSICAL CONDITIONS: * Overheating of 30A Pump motor, risk of internal damage or fire * * WHO WAS NOTIFIED: * Control Room, Plant Manager, Maintenance team * * KNOWLEDGEABLE INDIVIDUALS: * Assistant Plant Manager, Shift Supervisor * * REPEAT OR SIMILAR CONDITION: * Overheating incidents noted before, alpha pump infrared inspection. * * IMMEDIATE ACTIONS AND RECOMMENDED ACTIONS: * Full service investigation required for 30A Pump Motor. Until cause is identified and rectified, operations to run through secondary channel. All other pumps to be thermally scanned and checked for similar conditions * 03/15/ | What immediate actions were taken following the overheating incident of the 30A Pump motor? | The motor was immediately isolated and the system shifted to its secondary channel for normal operations.
127 | 2017-05-25 | 30981275 | 82135892 | Strong vibration from Motor 18B | S3CW -3CWE5 | * **************Incident Description************** * Notification 000030981275 Details * *********************************************************** * 05/25/2017 16:29:05 INCIDENT REPORT (INCIDENT REPORT) * Report submitted by: William Rodriguez ENTITY\INCIDENT: * * CONDITION DESCRIPTION/LOCATION (THE INAPPROPRIATE ACTION AND ITS NEGATIVE EFFECT/INCLUDE A DETAILED LOCATION DESCRIPTION): * During the scheduled shift, around 1501, the control room personnel detected a strong vibration from the Motor 18B. Inspection team responded immediately to the site and confirmed excessive vibration from Motor 18B. The vibration level was found to be dangerous for the motor. They initiated an emergency shutdown from Unit 3 Control room and vibration ceased. Investigation revealed that the coupling alignment was out from the normal range. The 18B Motor was put offline for further evaluation. * * ACTIVITIES, PROCESSES, PROCEDURES INVOLVED: * S3.OP.AB-CW-0002, S3.OP-SO.CW-0006 * * WHY DID CONDITION HAPPEN: * Preliminary speculation is that the misalignment of the motor-shaft coupling caused the vibration. A deeper investigation is needed to verify. * * CONSEQUENCES: * Over-vibration could have led to potential motor damage which would result in a decrease in operational efficiency, and an extended shutdown period. * * REQUIREMENTS IMPACTED: * Machine normal operation was hampered due to the shutdown. * * ADVERSE PHYSICAL CONDITION: * Excessive vibration of the 18B Motor, possible shaft damage. * * WHO WAS NOTIFIED: * Unit Supervisor, Maintenance Department. * * KNOWLEDGEABLE INDIVIDUALS: * Maintenance Team, Unit Supervisor, Johnson, Terry. * * REPEAT OR SIMILAR CONDITION: * Yes, observed previously in other units but not in the 18B Motor. * * IMMEDIATE AND RECOMMENDED ACTIONS: * Re-align the motor-shaft coupling, and run vibration analysis to see if any internal damage occurred. Initiate procedure S3.OP.AB-CW-0002 for abnormality correction | What was the immediate action taken after the detection of excessive vibration from the Motor 18B? | They initiated an emergency shutdown from Unit 3 Control room and vibration ceased. Investigation revealed that the coupling alignment was out from the normal range. The 18B Motor was put offline for further evaluation.
128 | 2019-08-30 | 30720229 | 80309210 | Overload on Circuit Breaker 9C | S2PW -2PWE7-CKR | * **************Incident Description************** * Notification 000030720229 Details * *********************************************************** * 08/30/2019 10:10:12 INCIDENT REPORT (INCIDENT REPORT) * Report submitted by: Peter Thompson ENTITY\INCIDENT: * CONDITION DESCRIPTION/LOCATION (THE INAPPROPRIATE ACTION AND ITS NEGATIVE EFFECT/INCLUDE A DETAILED LOCATION DESCRIPTION): * An overload warning was noticed on Circuit Breaker 9C during routine inspection. The overload limit was indicated at 120% of the rate, significantly higher than the other operating Circuit Breakers. As a precautionary measure, the circuit breaker was switched off to prevent possible fire or damage to connected equipment. * * ACTIVITIES, PROCESSES, PROCEDURES INVOLVED: * Routine inspection * * WHY DID CONDITION HAPPEN? * The overload could be due to a faulty equipment connected to the circuit or an internal problem with the circuit breaker itself. * * CONSEQUENCES: * Possible electrical fire, damage to connected equipment, and disruption of power supply. * * REQUIREMENTS IMPACTED: * Fire safety and equipment reliability * * ADVERSE PHYSICAL CONDITIONS: * Overload condition on Circuit Breaker * * WHO WAS NOTIFIED: * Supervisor, Electrical Maintenance Team * * KNOWLEDGEABLE INDIVIDUALS: * Electrical Maintenance Team * * REPEAT OR SIMILAR CONDITION: * No, this is the first occurrence * * IMMEDIATE ACTIONS AND RECOMMENDED ACTIONS: * Isolate and inspect the faulty circuit breaker and connected equipment. A replacement may be necessary if internal issues are identified in the circuit breaker. * 08/30/2019 15:50:24 JOHN MILLER (INCIDENT) * Inspection completed. Overload condition was due to faulty wiring in the connected equipment. The equipment has been disconnected and sent for repair. The circuit breaker was tested again and is now operating within normal parameters. | What was the cause of the overload condition on Circuit Breaker 9C? | Overload condition was due to faulty wiring in the connected equipment.
129 | 2020-12-12 | 30763251 | 80201294 | 35B pump showing unstable pressure output | S4CW -4CWE7 | * **************Incident Description************** * Notification 000030763251 Details * *********************************************************** * 12/12/2020 14:10:45 INCIDENT REPORT (INCIDENT REPORT) * Report submitted by: Emma White ENTITY\INCIDENT: * * CONDITION DESCRIPTION/LOCATION (THE INAPPROPRIATE ACTION AND ITS NEGATIVE EFFECT/INCLUDE A DETAILED LOCATION DESCRIPTION): * On 12/12/2020, during the morning inspection, inconsistent pressure output was observed in 35B pump. The pressure readings fluctuated within an unacceptable range, indicative of potential internal issues with the pump. * * ACTIVITIES, PROCESSES, PROCEDURES INVOLVED: * S4.OP-AB-CW-0002, S4.OP-SO.CW-0003 * * WHY DID CONDITION HAPPEN? * The reason for the inconsistent output pressure is unknown at this time. However, internal wear or blockage could be contributing factors. * * CONSEQUENCES: * If not rectified, unstable pressure output could lead to pump failure and impact the overall system performance. * * REQUIREMENTS IMPACTED: * Standard operating conditions * * ADVERSE PHYSICAL CONDITIONS: * Abnormal pressure output in 35B pump * * WHO WAS NOTIFIED: * On-Site Operator, Team Supervisor * * KNOWLEDGEABLE INDIVIDUALS: * Emma White, Team Supervisor, Maintenance Specialist * * REPEAT OR SIMILAR CONDITION: * No previous incidents of this nature * * IMMEDIATE ACTIONS AND RECOMMENDED ACTIONS: * Inspect 35B pump for possible internal wear and blockage. Conduct full maintenance check if necessary. * 12/14/2020 11:25:39 EMMA WHITE (INCIDENT) * Share maintenance updates and findings with the technical team for preventive measures to mitigate future occurrences. | What immediate and recommended actions have been suggested following the incident with the inconsistent pressure output in 35B pump? | Inspect 35B pump for possible internal wear and blockage. Conduct full maintenance check if necessary.
130 | 2018-10-12 | 30890562 | 90145678 | Unusual vibrations from 30B motor pump | S4CW -4CWE5 | * **************Incident Description************** * Notification 000030890562 Details * *********************************************************** * 10/12/2018 19:50:45 INCIDENT REPORT (INCIDENT REPORT) * Report submitted by: Robert Blue ENTITY\INCIDENT: * * CONDITION DESCRIPTION/LOCATION (THE INAPPROPRIATE ACTION AND ITS NEGATIVE EFFECT/INCLUDE A DETAILED LOCATION DESCRIPTION): * During the night shift on 10/12/2018, notification came from S4 Control Room about a 30B motor pump exhibiting unusual vibrations exceeding the acceptable limit as per S4.OP-SO.CW-0002. All other parameters such as pressure, current and temperature are within normal range. Emergency shutdown procedure was implemented as per standard protocol. * * ACTIVITIES, PROCESSES, PROCEDURES INVOLVED: * Observing and responding to abnormal pump conditions as per S4.OP-SO.CW-0002 * * WHY DID CONDITION HAPPEN? * The exact cause is unknown. Possible reasons could be mechanical faults or internal blockage. * * CONSEQUENCES: * If left undiagnosed and untreated, the continuous vibrations could lead to pump failure, affecting the system's efficiency and performance. * * REQUIREMENTS IMPACTED: * Operational reliability and efficiency. * * ADVERSE PHYSICAL CONDITIONS: * Excess vibrations coming from the 30B motor pump. * * WHO WAS NOTIFIED: * Supervisor, Maintenance Team, Control Room * * KNOWLEDGEABLE INDIVIDUALS: * Supervisor, Maintenance Team, Engineers * * REPEAT OR SIMILAR CONDITION: * No, this is the first incident of its kind. * * IMMEDIATE ACTIONS AND RECOMMENDED ACTIONS: * An immediate diagnosis followed by an adequate solution in compliance with the S4.OP-AB.CW-0001 Procedure. If necessary, replacement parts should be used for restoring the pump's normal operation. * 10/12/2018 22:28:15 JANE DOE (INCIDENT) * The Maintenance Team identified an imbalance in the pump due to wear and tear on the rotor blades. | What was the detected problem in the 30B motor pump that provoked an incident? | A 30B motor pump exhibiting unusual vibrations exceeding the acceptable limit as per S4.OP-SO.CW-0002.
131 | 2018-09-12 | 30990134 | 80587601 | Water leakage 19X Pump | S1FW -1FWE5-PMP | * **************Incident Description************** * Notification 000030990134 Details * *********************************************************** * 09/12/2018 09:09:07 INCIDENT REPORT (INCIDENT REPORT) * Report submitted by: William Graham 321-654-9870 ENTITY\INCIDENT: * * CONDITION DESCRIPTION/LOCATION (THE INAPPROPRIATE ACTION AND ITS NEGATIVE EFFECT/INCLUDE A DETAILED LOCATION DESCRIPTION): * During scheduled maintenance, technician noticed water dripping from the 19X Pump base. No prior leak was in evidence before the pump shutdown. The leak seemed minor, but could escalate if unchecked. * * ACTIVITIES, PROCESSES, PROCEDURES INVOLVED: * Scheduled maintenance. * * WHY DID CONDITION HAPPEN? * Likely seal failure. Could due to wear and tear or misalignment. * * CONSEQUENCES: * Potential pump damage, Slip hazards for workers, Unavailability of 19X pump. * * REQUIREMENTS IMPACTED: * Safe workplace, Efficient pump operation. * * ADVERSE PHYSICAL CONDITIONS: * Water pooling around the pump base. * * WHO WAS NOTIFIED: * Maintenance Manager, Safety Officer. * * KNOWLEDGEABLE INDIVIDUALS: * Maintenance Manager, Safety Officer. * * REPEAT OR SIMILAR CONDITION: * Minor leaks have been reported before for other pumps. * * IMMEDIATE ACTIONS AND RECOMMENDED ACTIONS: * The area has been cordoned off and suitable slip hazard warning signage has been placed. Immediate inspection and repair of seal and re-evaluation of pump alignment is recommended. Include this incident in the next safety meeting. * 09/12/2018 14:25:00 WILLIAM GRAHAM (INCIDENT) * Repair order placed. Safety Officer informed. The leak is temporarily managed by containment. This will be reviewed at the next Safety meeting. | What immediate actions were taken and what was recommended after finding the water leak from the 19X Pump base? | The area has been cordoned off and suitable slip hazard warning signage has been placed. Immediate inspection and repair of seal and re-evaluation of pump alignment is recommended. Include this incident in the next safety meeting.
132 | 2018-04-24 | 30781265 | 80245719 | R8D MOTOR TEMP ABOVE NORMAL | S4RL -4RLD8 | * **************Incident Description************** * Notification 000030781265 Details * *********************************************************** * 04/24/2018 07:15:29 INCIDENT REPORT (INCIDENT REPORT) * Report submitted by: Mark Taylor ENTITY\INCIDENT: * * CONDITION DESCRIPTION/LOCATION (THE INAPPROPRIATE ACTION AND ITS NEGATIVE EFFECT/INCLUDE A DETAILED LOCATION DESCRIPTION): * Following routine maintenance on 24/04/18 at R8D motor, the system indicators showed higher than normal temperature readings. Immediate visual and sensory checks confirmed the increased in temperature, but no other abnormal signs were observed. * * ACTIVITIES, PROCESSES, PROCEDURES INVOLVED: * Routine maintenance, procedure S4.OP-SO.RL-0001 followed, standardising operational controls and temperature settings. * * WHY DID CONDITION HAPPEN? * Current cause is unknown. Possibility of flawed maintenance, faulty sensors, or intrinsic motor damage being investigated. * * CONSEQUENCES: * Potential equipment failure, increase in system downtime, compromised safety, and efficiency. * * REQUIREMENTS IMPACTED: * Business continuity, safety guidelines * * ADVERSE PHYSICAL CONDITIONS: * Increased motor temperature, no other observed physical condition. * * WHO WAS NOTIFIED: * Maintenance Supervisor, Safety Department, Operations Manager * * KNOWLEDGEABLE INDIVIDUALS: * Maintenance Supervisor, Safety Expert, Smith, Joe, Johnson * * REPEAT OR SIMILAR CONDITION: * No, this is a new incident. * * IMMEDIATE ACTIONS AND RECOMMENDED ACTIONS: * Investigation initiated by Maintenance Team to determine root cause. Pending results, potential equipment replacement or overhaul may be considered. * 04/25/2018 16:55:42 MARK TAYLOR (INCIDENT) * Preliminary findings suggest a possible alignment issue during maintenance. Further investigations are ongoing. | What were the possible causes for the increased temperature readings on the R8D motor? | Current cause is unknown. Possibility of flawed maintenance, faulty sensors, or intrinsic motor damage being investigated.
133 | 2021-03-12 | 30927541 | 80212345 | Bearing vibration monitoring abnormality in 32B Pump | S4CW -4CWE7 | * **************Incident Description************** * Notification 000030927541 Details * *********************************************************** * 03/12/2021 08:20:24 INCIDENT REPORT (INCIDENT REPORT) * Report submitted by: Jacob White ENTITY\INCIDENT: * * CONDITION DESCRIPTION/LOCATION (THE INAPPROPRIATE ACTION AND ITS NEGATIVE EFFECT/INCLUDE A DETAILED LOCATION DESCRIPTION): * This morning during the routine vibration monitoring check, an abnormality was recognized in the 32B pump. The bearing lateral vibration was unusually above the set limits. Temperature on the pump housing was close to normal, which makes the high vibration an alarming anomaly. * * ACTIVITIES, PROCESSES, PROCEDURES INVOLVED: * Routine vibration monitoring check. * WHY DID CONDITION HAPPEN? * Unknown, but wear and tear or possible misalignment of the pump could be a factor. * * CONSEQUENCES: * Potential bearing damage leading to unexpected failure. * * REQUIREMENTS IMPACTED: * Normal operation and predictive maintenance. * * ADVERSE PHYSICAL CONDITIONS: * High vibration level. * * WHO WAS NOTIFIED: * Supervisor, Maintenance Manager * * KNOWLEDGEABLE INDIVIDUALS: * Maintenance Team Members, Vibration Analyst * * REPEAT OR SIMILAR CONDITION: * No, this is the first instance. * * IMMEDIATE AND RECOMMENDED ACTIONS: * Isolate and perform detailed inspection of the pump. Record observed conditions and abnormalities for further assessment. * 03/12/2021 16:30:47 JACOB WHITE (INCIDENT) * The pump has been inspected. Misalignment found and has been corrected. Vibration level is within normal limits. Continue monitoring. | What was the abnormality noticed during the routine vibration monitoring check? | The bearing lateral vibration was unusually above the set limits.
134 | 2016-11-12 | 30753880 | 80238542 | 60V PUMP HIGH VIBRATION | S4CW -4CWE7 | * **************Incident Description************** * Notification 000030753880 Details * *********************************************************** * 11/12/2016 14:20:25 INCIDENT REPORT (INCIDENT REPORT) * Report submitted by: William Cox ENTITY\INCIDENT: * * CONDITION DESCRIPTION/LOCATION (THE INAPPROPRIATE ACTION AND ITS NEGATIVE EFFECT/INCLUDE A DETAILED LOCATION DESCRIPTION): * During routine operation, it was noted that the 60V Pump exhibited a sudden spike in vibration readings. Vibration level had risen to 9 mils (peak to peak) which is significant since the pump typically operates at 2 mils. In the interest of safety and equipment preservation, 60V pump was remotely shut down from Unit 4 Control Room. * * ACTIVITIES, PROCESSES, PROCEDURES INVOLVED: * S4.OP.AB-CW-0003, S4.OP-SO.CW-0002 * * WHY DID CONDITION HAPPEN? * Unknown, requires further investigation. * * CONSEQUENCES: * Potential for pump failure if it remained in operation, possible collateral damage. * * REQUIREMENTS IMPACTED: * Pump availability. * * ADVERSE PHYSICAL CONDITIONS: * High vibration on 60V Pump. * * WHO WAS NOTIFIED: * Control Room, Maintenance Team. * * KNOWLEDGEABLE INDIVIDUALS: * Williams, Jackson, Reed. * * REPEAT OR SIMILAR CONDITION: * No. * * IMMEDIATE ACTIONS AND RECOMMENDED ACTIONS: * Check and log vibration prior to startup and after pump has reached normal operating temperature and speed, while the system is manually balanced. Inspection and Maintenance team to investigate the cause of high vibration. * 11/13/2016 10:43:05 WILLIAM COX (INCIDENT) * Upon inspection, a minor imbalance in the impeller was found. The pump has been serviced, balanced and is now back in operation with normal vibration levels. | What was the observed problem with the 60V Pump during its routine operation? | During routine operation, it was noted that the 60V Pump exhibited a sudden spike in vibration readings. Vibration level had risen to 9 mils (peak to peak) which is significant since the pump typically operates at 2 mils. In the interest of safety and equipment preservation, 60V pump was remotely shut down from Unit 4 Control Room.
135 | 2018-05-24 | 30745893 | 80245609 | Unexpected pressure drop in 17B Pump | S2CW -2CWE7 | * **************Incident Description************** * Notification 000030745893 Details * *********************************************************** * 05/24/2018 15:14:56 INCIDENT REPORT (INCIDENT REPORT) * Report submitted by: Brad Johnson ENTITY\INCIDENT: * * CONDITION DESCRIPTION/LOCATION (THE INAPPROPRIATE ACTION AND ITS NEGATIVE EFFECT/INCLUDE A DETAILED LOCATION DESCRIPTION): * Noticed an unexpected pressure drop in 17B Pump at 2314 hours. Normal operation was disrupted and 17B pump was shut down from Control Room. No visible signs of external damage. The Course of action taken as per S2.OP-AA.120 Pump Abnormality in similar situations. * * ACTIVITIES, PROCESSES, PROCEDURES INVOLVED: * S2.OP-AA.120 * * WHY DID CONDITION HAPPEN: * Cause is unknown at the moment - requires further investigation. * * CONSEQUENCES: * Potential reduced efficiency of the unit once it is restarted, pump damage. * * REQUIREMENTS IMPACTED: * Normal Operation * * ADVERSE PHYSICAL CONDITIONS: * Unexpected pressure drop in 17B Pump * * WHO WAS NOTIFIED: * Control Room, Supervisor, Maintenance Team * * KNOWLEDGEABLE INDIVIDUALS: * Peterson, O'Reilly, James * * REPEAT OR SIMILAR CONDITION: * No, this is the first occurrence with this pump * * IMMEDIATE ACTIONS AND RECOMMENDED ACTIONS: * Inspection and maintenance tasks are required to investigate the pressure drop situation with the 17B Pump. * * Updated: BRAD JOHNSON 05.24.2018 16:25:32 * ------------------------------------------------------------ * 06/04/2018 09:41:35 LISA ROGERS (NUSER) * An extensive investigation showed the issue was due to some internal blockage in the pump. The blockage was removed and the pump is now functioning normally. Further observation is recommended to prevent recurrence. | What was the cause behind the unexpected pressure drop in the 17B Pump? | The issue was due to some internal blockage in the pump.
136 | 2019-11-05 | 30979362 | 80281645 | High vibration observed in 16B Pump Motor | S4CW -4CWE5 | * **************Incident Description************** * Notification 000030979362 Details * *********************************************************** * 11/05/2019 13:15:45 INCIDENT REPORT (INCIDENT REPORT) * Report submitted by: Emily Thomas ENTITY\INCIDENT: * * CONDITION DESCRIPTION/LOCATION (THE INAPPROPRIATE ACTION AND ITS NEGATIVE EFFECT/INCLUDE A DETAILED LOCATION DESCRIPTION): * During the inspection, 16B Pump Motor demonstrated high vibration. Vibration level is 4.2mm/s, beyond the acceptable limit of 3.5mm/s. Post-maintenance return incident similar to 16A pump earlier this year. The condition needs an immediate investigation and solution to prevent potential damage. * * ACTIVITIES, PROCESSES, PROCEDURES INVOLVED: * Regular inspection and monitoring, S4.OP-AB.CW-0002 * * WHY DID CONDITION HAPPEN? * The exact cause of the issue is not clear at this point; factors like worn-out parts, improper alignment, or other mechanical problems might be involved. * * CONSEQUENCES: * If not addressed, the increased vibration could lead to more serious mechanical issues and could disrupt normal operation. * * REQUIREMENTS IMPACTED: * Regular operation, safety regulations adhering to vibration limits * * ADVERSE PHYSICAL CONDITIONS: * Increased vibration in 16B Pump Motor * * WHO WAS NOTIFIED: * Supervisor, Engineering Team * * KNOWLEDGEABLE INDIVIDUALS: * Engineering Team, Maintenance Team * * REPEAT OR SIMILAR CONDITION: * Yes, similar to 16A Pump Motor * * IMMEDIATE ACTIONS AND RECOMMENDED ACTIONS: * The maintenance team needs to investigate the vibration and implement corrective actions as necessary. The engineering team should review historical data of previous issues with similar conditions. * * 11/07/2019 16:52:12 EMILY THOMAS (INCIDENT) * Inspection revealed misaligned parts causing the high vibrations. Corrections have been made and vibration levels are monitoring within acceptable limits now. | What was the immediate action taken when high vibration was observed in the 16B Pump Motor? | The maintenance team needs to investigate the vibration and implement corrective actions as necessary. The engineering team should review historical data of previous issues with similar conditions.
137 | 2019-11-25 | 30881056 | 80259874 | Abnormal Vibration in Pump Motor 28B | S4CW -4CWE5 | * **************Incident Description************** * Notification 000030881056 Details * *********************************************************** * 11/25/2019 09:32:00 INCIDENT REPORT (INCIDENT REPORT) * Report submitted by: David Thompson ENTITY\INCIDENT: * * CONDITION DESCRIPTION/LOCATION (THE INAPPROPRIATE ACTION AND ITS NEGATIVE EFFECT/INCLUDE A DETAILED LOCATION DESCRIPTION): * At 0730 on 11/25/19, abnormal vibrations were detected on the 28B Pump motor during routine inspection. Pump was not shut down but was placed on cautionary observation. Vibrations were within acceptable limits but higher than typical levels for this equipment. No immediate signs of damage or degradation were observed externally. S4.OP-AB.CW-0003 Pump Abnormality procedure was initiated due to the observed vibrations. * * ACTIVITIES, PROCESSES, PROCEDURES INVOLVED: * S4.OP.AB-CW-0003, S4.OP-SO.CW-0004 * * WHY DID CONDITION HAPPEN: * Unknown currently, investigation underway * * CONSEQUENCES: * Extended operation under the current condition may lead to damage in the motor resulting in system inefficiency. * * REQUIREMENTS IMPACTED: * Potential motor maintenance and repair * * ADVERSE PHYSICAL CONDITION: * Abnormal Vibrations in 28B Pump motor * * WHO WAS NOTIFIED: * Control Room, Maintenance Team * * KNOWLEDGEABLE INDIVIDUALS: * Adams, Baker, Wilson * * REPEAT OR SIMILAR CONDITION: * No, this is the first incident of this nature * * IMMEDIATE AND RECOMMENDED ACTIONS: * Reduce the operational load of 28B Pump and schedule maintenance * * Updated: DAVID THOMPSON 11.25.2019 11:45:19 * ------------------------------------------------------------ * 12/03/2019 08:33:51 MARK HENRY (MAINTENANCE) * Inspection revealed misalignment of the pump causing the abnormal vibrations. After realigning the pump and | What was the immediate recommended action following the detection of abnormal vibrations in the 28B Pump Motor? | Reduce the operational load of 28B Pump and schedule maintenance
138 | 2018-10-19 | 30750139 | 80239817 | R3A Pump experienced pressure fluctuations | M4CW -4CWE1 | * **************Incident Description************** * Notification 000030750139 Details * *********************************************************** * 10/19/2018 14:13:00 INCIDENT REPORT (INCIDENT REPORT) * Report submitted by: Robert Johnson ENTITY\INCIDENT: * * CONDITION DESCRIPTION/LOCATION (THE INAPPROPRIATE ACTION AND ITS NEGATIVE EFFECT/INCLUDE A DETAILED LOCATION DESCRIPTION): * During the regular maintenance cycle, R3A Pump was observed to experience pressure fluctuations beyond the normally expected variation. The subsequent inspection revealed indications of wear on pump impellers. All associated pressures and temperatures were recorded and logged for analysis. * * ACTIVITIES, PROCESSES, PROCEDURES INVOLVED: * Regular maintenance check and inspection of R3A Pump * * WHY DID CONDITION HAPPEN? * Suspected wear on impellers due to prolonged operation could be a possible cause. Further examination is necessary. * * CONSEQUENCES: * Risk of pump failure or reduced efficiency, possible impact on associated processes and flow rates * * REQUIREMENTS IMPACTED: * Ability to maintain constant flow rate * * ADVERSE PHYSICAL CONDITIONS: * Fluctuating pressure in the pump system * * WHO WAS NOTIFIED: * Operations Team, Maintenance Supervisor * * KNOWLEDGEABLE INDIVIDUALS: * Robert Johnson, Operations Team, Maintenance Supervisor * * REPEAT OR SIMILAR CONDITION: * No * * IMMEDIATE ACTIONS AND RECOMMENDED ACTIONS: * Initiate a detailed inspection and if necessary, replacement of worn components should be scheduled. Further monitoring of the pump system is needed to determine if the issue persists. * 10/23/2018 08:15:51 JOHN DOE (INCIDENT) * Inspection concluded wear on impellers as primary cause. Replacement is scheduled for the next maintenance window. Temporary measures have been put in place to mitigate effect on flow rate and prevent potential pump failure. Further monitoring and reporting have been established. | What were the immediate actions and recommended actions after noticing fluctuating pressure in the R3A Pump? | Initiate a detailed inspection and if necessary, replacement of worn components should be scheduled. Further monitoring of the pump system is needed to determine if the issue persists.
139 | 2019-04-12 | 30845720 | 80217690 | Leakage from 18A Cooling Tower | S4CW -4CWE7 | * **************Incident Description************** * Notification 000030845720 Details * *********************************************************** * 04/12/2019 10:07:21 INCIDENT REPORT (INCIDENT REPORT) * Report submitted by: Emily Barnes ENTITY\INCIDENT: * * CONDITION DESCRIPTION/LOCATION (THE INAPPROPRIATE ACTION AND ITS NEGATIVE EFFECT/INCLUDE A DETAILED LOCATION DESCRIPTION): * During a periodic on-site inspection on 04/12/19, it was noted that there was a leakage from the 18A Cooling Tower. The leakage was continuous and caused water spillage around the area. Operations team initiated Swift leak containment and cleanup measures. * * ACTIVITIES, PROCESSES, PROCEDURES INVOLVED: * Regular site inspection and S4.OP.AB.CT-0002, S4.OP.SO.CT-0001 * * WHY DID CONDITION HAPPEN? * The root cause hasn't been identified yet, but similar leakages have been observed due to wear and tear and/or corrosion. * * CONSEQUENCES: * Possible reduction in operations efficiency and water wastage. Untreated, could increase maintenance costs. * * REQUIREMENTS IMPACTED: * Environment compliance due to water wastage. * * ADVERSE PHYSICAL CONDITIONS: * Water leakage from 18A Cooling Tower * * WHO WAS NOTIFIED: * Operations Supervisor, Maintenance Team * * KNOWLEDGEABLE INDIVIDUALS: * Supervisor, Maintenance Team, Gilmore, Reyes, Cooper * * REPEAT OR SIMILAR CONDITION: * Yes, several instances were recorded in the past. * * IMMEDIATE ACTIONS AND RECOMMENDED ACTIONS: * The maintenance team to conduct immediate inspection and repair. Water usage should be monitored closely. * 04/12/2019 15:37:42 EMILY BARNES (INCIDENT) * Maintenance team inspected the unit and identified a fractured joint as the cause of the leakage. The joint is being replaced and routine inspection intervals are recommended for review in order to prevent recurrence. | What was the immediate action recommended following the discovery of water leakage from the 18A Cooling Tower? | The maintenance team to conduct immediate inspection and repair. Water usage should be monitored closely.
140 | 2018-03-24 | 30765493 | 80234561 | Unscheduled motor shut down on 18A pump | S4CW -4CWE4 | * **************Incident Description************** * Notification 000030765493 Details * *********************************************************** * 03/24/2018 08:30:12 INCIDENT REPORT (INCIDENT REPORT) * Report submitted by: Mark Lawson ENTITY\INCIDENT: * * CONDITION DESCRIPTION/LOCATION (THE INAPPROPRIATE ACTION AND ITS NEGATIVE EFFECT/INCLUDE A DETAILED LOCATION DESCRIPTION): * The 18A pump motor unexpectedly shut down at 0800, although no alarms had tripped. The motor was recently returned from maintenance under work order 80191324. The current and temperature readings were normal prior to the event, but shortly after the incident, the temperature began to rise. The maintenance team was immediately notified. * * ACTIVITIES, PROCESSES, PROCEDURES INVOLVED: * Regular operations and monitoring in coordination with S3.OP-SO.CW-0002. * * WHY DID CONDITION HAPPEN? * At present, the cause is unknown and under investigation. Electrical failure is being considered as a main possibility. * * CONSEQUENCES: * Potential disruption in cooling water supply, potential damage to the motor. * * REQUIREMENTS IMPACTED: * Continuous operation of 18A Pump. * * ADVERSE PHYSICAL CONDITIONS: * Overheating of 18A pump motor. * * WHO WAS NOTIFIED: * Maintenance Supervisor, Operations Manager. * * KNOWLEDGEABLE INDIVIDUALS: * Mark Lawson, Dave Wilson, Jenny Thompson. * * REPEAT OR SIMILAR CONDITION: * No * * IMMEDIATE ACTIONS AND RECOMMENDED ACTIONS: * Temporarily switch to backup pump, and inspect the 18A motor to identify and rectify the issue. Continue to monitor temperature and current readings. * 03/25/2018 12:20:45 JANE DOE (INCIDENT) * The inspection revealed that the motor shut down due to a faulty connection. The connection has been fixed and after running a few tests, the pump is now back in operation. All parameters are normal. | What was the initial reaction after the unexpected shutdown of the 18A pump motor? | The maintenance team was immediately notified.
141 | 2018-02-05 | 30830670 | 80250032 | 40A Motor High temperature | S5CE -5CWE9 | * *************Incident Description************** * Notification 000030830670 Details * *********************************************************** * 02/05/2018 11:51:45 OPERATIONAL REPORT (OPERATIONAL INFO) * Report submitted by: David Winter 321-987-6543 * INCIDENT\OPERATIONAL: * * 1) CONDITION DESCRIPTION/LOCATION (The inappropriate action and its negative effect/Include a detailed location description): * Upon routine inspection at 1100 on 05/02/2018, the operator noticed high temperature in the 40A Motor. The unit was immediately shut down for safety evaluation. The temperature was higher than normal operating parameters and it posed potential risk of breakdown. No external signs of damage were observed. * * 2) ACTIVITIES, PROCESSES, PROCEDURES INVOLVED: * Routine inspection, Initial evaluation: S5.OP-AB.CE-0001, S5.OP-AE.CE-0001 targeting equipment shutdown and cooling procedures. * * 3) WHY DID CONDITION HAPPEN: * Unknown at this moment, but previous incidents with similar conditions indicated possibility of coolant failure or debris blockage. * * 4) CONSEQUENCES: * Risk of efficiency loss or severe damage if motor continued to operate under high temperature. * * 5) REQUIREMENTS IMPACTED: * Regular operational schedule, potential system downtime. * * 6) ADVERSE PHYSICAL CONDITION: * High temperature in 40A Motor, potential motor internals damage. * * 7) WHO WAS NOTIFIED: * Control Room, Safety Officer, Maintenance Team. * * 8) KNOWLEDGEABLE INDIVIDUALS: * Thomas Jackson, Robert Lee, Emily White. * * 9) REPEAT OR SIMILAR CONDITION: * No, first time recorded. * * 10) IMMEDIATE AND RECOMMENDED ACTIONS: * Immediate shutdown of 40A Motor, followed by detailed investigation. Suggesting standard maintenance check focusing on coolant system and thermal insulation. * * Updated: David Winter 02.05.2018 12:25:19 * ------------------------------------------------------------ * | What actions were taken when high temperature was detected in the 40A Motor? | The unit was immediately shut down for safety evaluation.
142 | 2018-10-03 | 30897651 | 80298456 | 31B turbine unusual vibration | S4CW -4CWE5 | * **************Incident Description************** * Notification 000030897651 Details * *********************************************************** * 10/03/2018 14:52:24 INCIDENT REPORT (INCIDENT REPORT) * Report submitted by: Morgan Brown 136-467-8980 ENTITY\INCIDENT: * CONDITION DESCRIPTION/LOCATION (THE INAPPROPRIATE ACTION AND ITS NEGATIVE EFFECT/INCLUDE A DETAILED LOCATION DESCRIPTION): * During the routine inspection of Unit 4 turbines, abnormal vibrations were detected on the 31B turbine. Inspection with a stethoscope revealed a sound consistent with potential bearing wear or internal damage. The 31B turbine speed and temperature were within normal parameters. * * ACTIVITIES, PROCESSES, PROCEDURES INVOLVED: * Routine inspection, operation of 31B turbine * WHY DID CONDITION HAPPEN? * Unknown, potentially due to bearing wear, misalignment, or other internal damage. * * CONSEQUENCES: * Potential turbine failure, decreased efficiency, safety hazard * * REQUIREMENTS IMPACTED: * Turbine operation, operational safety * * ADVERSE PHYSICAL CONDITIONS: * Abnormal vibration and noise at 31B turbine * * WHO WAS NOTIFIED: * Supervisor, Maintenance Team, Safety Officer * * KNOWLEDGEABLE INDIVIDUALS: * Maintenance Team, Safety Officer * * REPEAT OR SIMILAR CONDITION: * No, this is the first incident of its kind * * IMMEDIATE ACTIONS AND RECOMMENDED ACTIONS: * Shutdown of 31B turbine for further inspection and possible repair or maintenance action. * 10/04/2018 09:59:32 MORGAN BROWN (INCIDENT) * Inspection of the 31B turbine has been initiated. Further recommendations and actions will be determined based on findings of the inspection. | What immediate action was recommended after the abnormal vibrations were detected on the 31B turbine? | Shutdown of 31B turbine for further inspection and possible repair or maintenance action.
143 | 2017-09-15 | 30817234 | 80236905 | Noise from 7C Water pump 7XK3 | S1DE -1PET4 | * **************Incident Description************** * Notification 000030817234 Details * *********************************************************** * 09/15/2017 16:14:00 INCIDENT REPORT (INCIDENT REPORT) * Report submitted by: Robert Smith ENTITY\INCIDENT: * * CONDITION DESCRIPTION/LOCATION (THE INAPPROPRIATE ACTION AND ITS NEGATIVE EFFECT/INCLUDE A DETAILED LOCATION DESCRIPTION): * During a standard checks, it was ascertained that the 7C water pump was making an unusual noise. This pump is generally quiet. The inlet pressure was seen at 9 psig, with current at 220. The temperature around the pump was within the normal range but the noise persisted. * * ACTIVITIES, PROCESSES, PROCEDURES INVOLVED: * Current Check, Standard Monitoring * * WHY DID CONDITION HAPPEN? * At this stage, the underlying reason for the issue cannot be confirmed. Possible reasons could be rubble in the pump or damage to the pump itself. * * CONSEQUENCES: * Probable reduced efficiency, potential failure of the pump * * REQUIREMENTS IMPACTED: * Normal operation, Service reliability * * ADVERSE PHYSICAL CONDITIONS: * Excessive noise levels emanating from the pump without any distinct reason * * WHO WAS NOTIFIED: * Area Supervisor/ INCIDENT TEAM * * KNOWLEDGEABLE INDIVIDUALS: * Maintenance Team * * REPEAT OR SIMILAR CONDITION: * Yes, multiple instances * * IMMEDIATE ACTIONS AND RECOMMENDED ACTIONS: * Pump intake requires cleaning; monitoring should be rigorous. If noise persists, an in-depth inspection may be essential. * 09/15/2017 18:55:23 ROBERT SMITH (INCIDENT) * Recommending a comprehensive inspection to identify the cause behind the noise. | What immediate and recommended actions were taken in response to the unusual noise from the 7C water pump? | Pump intake requires cleaning; monitoring should be rigorous. If noise persists, an in-depth inspection may be essential. Recommending a comprehensive inspection to identify the cause behind the noise.
144 | 2020-11-29 | 30975328 | 90325471 | Anomalous vibration in 9C Heat Exchanger Pump | S5HE -5HEE9-PUMP | * **************Incident Description************** * Notification 000030975328 Details * *********************************************************** * 11/29/2020 18:20:35 INCIDENT REPORT (INCIDENT REPORT) * Report submitted by: Lisa King 123-789-4560 ENTITY\INCIDENT: * CONDITION DESCRIPTION/LOCATION (THE INAPPROPRIATE ACTION AND ITS NEGATIVE EFFECT/INCLUDE A DETAILED LOCATION DESCRIPTION): * During evening rounds, 9C Heat Exchanger Pump was identified to be vibrating excessively. Inspection found no external or obvious sources for the vibration. Associated instrumentation in S5.OP-AB.HE-0009 indicated normal performance parameters. * * ACTIVITIES, PROCESSES, PROCEDURES INVOLVED: * Routine Round * WHY DID CONDITION HAPPEN? * Unknown. The cause and source of the vibration remain undetermined. * * CONSEQUENCES: * If not resolved, vibration may cause mechanical failure or damage to the heat exchanger pump. * * REQUIREMENTS IMPACTED: * Normal operation and potential heat exchange efficiency. * * ADVERSE PHYSICAL CONDITIONS: * Abnormal vibration in heat exchanger pump with no identifiable cause * * WHO WAS NOTIFIED: * Supervisor/ Incident Team * * KNOWLEDGEABLE INDIVIDUALS: * Incident Team, Maintenance Team * * REPEAT OR SIMILAR CONDITION: * No similar incidences reported. * * IMMEDIATE ACTIONS AND RECOMMENDED ACTIONS: * Initiation of S5.OP-AB.HE-0009. Contact Maintenance for immediate problem assessment and potential repair. * 11/30/2020 07:35:15 LISA KING (INCIDENT) * Maintenance report shows the vibration was due to a misaligned coupling. The coupling was realigned, and the pump is back to normal operation. Condition resolved. No further action required. | What was the immediate action recommended after the excessive vibration was identified in the 9C Heat Exchanger Pump? | Initiation of S5.OP-AB.HE-0009. Contact Maintenance for immediate problem assessment and potential repair.
145 | 2019-03-25 | 30768295 | 90248576 | Leakage at Valve V7 pump | S4CW -4CWE7 | * **************Incident Description************** * Notification 000030768295 Details * *********************************************************** * 03/25/2019 15:17:00 INCIDENT REPORT (INCIDENT REPORT) * Report submitted by: David Thomas ENTITY\INCIDENT: * * CONDITION DESCRIPTION/LOCATION (THE INAPPROPRIATE ACTION AND ITS NEGATIVE EFFECT/INCLUDE A DETAILED LOCATION DESCRIPTION): * On 03/25/19, routine inspection disclosed a minor leak at V7 pump. The immediate response was to tighten the valve which resulted in interruption of leak for a brief period, but leakage resumed thereafter. Inspection revealed worn out valve gaskets, which might be the cause for the leak. * * ACTIVITIES, PROCESSES, PROCEDURES INVOLVED: * S4.OP.AB-CW-0009, S4.OP-SO.CW-0003 * * WHY DID CONDITION HAPPEN? * Possible wear and tear of valve gaskets, requiring replacement. * * CONSEQUENCES: * Prolonged leakage could lead to reduction in pump pressure, affecting overall system efficiency. * * REQUIREMENTS IMPACTED: * Valve maintenance * * ADVERSE PHYSICAL CONDITIONS: * Leak from V7 Pump Valve * * WHO WAS NOTIFIED: * Maintenance Crew, Supervisor * * KNOWLEDGEABLE INDIVIDUALS: * Supervisor, Maintenance Crew, White, Green * * REPEAT OR SIMILAR CONDITION: * No * * IMMEDIATE ACTIONS AND RECOMMENDED ACTIONS: * Replacement of valve gaskets. If necessary valve V7 may have to be completely replaced. * 03/28/2019 10:09:11 DAVID THOMAS (INCIDENT) * Valve gasket was replaced and no further leakage observed since then. Monitoring continuously to ensure no further leakage. | What was the immediate response following the detection of a leak in the V7 pump? | The immediate response was to tighten the valve which resulted in interruption of leak for a brief period, but leakage resumed thereafter.
146 | 2022-01-30 | 31044715 | 80285432 | 18B Pump motor failure post overhaul | S4CW -4CWE7 | * **************Incident Description************** * Notification 000031044715 Details * *********************************************************** * 01/30/2022 10:32:05 INCIDENT REPORT (INCIDENT REPORT) * Report submitted by: Jennifer Taylor ENTITY\INCIDENT: * * CONDITION DESCRIPTION/LOCATION (THE INAPPROPRIATE ACTION AND ITS NEGATIVE EFFECT/INCLUDE A DETAILED LOCATION DESCRIPTION): * In 04/2021, notification 31003942 identified that 17B Pump returned from maintenance with an unexpected motor failure. The issue was resolved under the work order 80268901 and procedure changes were made in June 2021 for S4.OP-SO.CW-0002 to provide guidance for inspecting motor conditions. Following the changes, 18B pump was serviced in November 2021 under work order 80286913 and faced a similar motor failure incident. This suggests that the revised procedure may not be adequately addressing all potential issues. The nature of failures and changes made need to be reassessed for a better response. * ACTIVITIES, PROCESSES, PROCEDURES INVOLVED: * Routine maintenance, Hit-and-miss motor failures despite procedural updates illustrated in S4.OP-SO.CW-0002. * * WHY DID CONDITION HAPPEN? * The causes for repeated failure incidents, despite procedural changes, remain unclear. * * CONSEQUENCES: * Potential to undermine the reliability of the equipment and inflating maintenance costs. * * REQUIREMENTS IMPACTED: * Equipment availability and functionality. * * ADVERSE PHYSICAL CONDITIONS: * Failed motor after regular maintenance * * WHO WAS NOTIFIED: * Maintenance Supervisor, Technical Team * * KNOWLEDGEABLE INDIVIDUALS: * Maintenance Supervisor, Technical Team, Lead Engineer * * REPEAT OR SIMILAR CONDITION: * Yes, similar incidents reported under notification 31003942 were resolved but have reoccurred. * * IMMEDIATE ACTIONS AND RECOMMENDED ACTIONS: * Need for a more in-depth diagnostic assessment and a reevaluation of the procedural updates, especially for S4.OP-SO.CW-0002 * 02/02/2022 | What actions were recommended after the repeated pump motor failures? | Need for a more in-depth diagnostic assessment and a reevaluation of the procedural updates, especially for S4.OP-SO.CW-0002.
147 | 2017-09-13 | 30788904 | 80236411 | Noisy operations 3A COP | S4SW -4SWE5-DIST | * **************Incident Description************** * Notification 000030788904 Details * *********************************************************** * 09/13/2017 08:30:23 INCIDENT REPORT (INCIDENT REPORT) * Report submitted by: Lucy Gomez ENTITY\INCIDENT: * CONDITION DESCRIPTION/LOCATION (THE INAPPROPRIATE ACTION AND ITS NEGATIVE EFFECT/INCLUDE A DETAILED LOCATION DESCRIPTION): * On 09/13/17, during the routine operational tracking, an excessive noise level was reported from the 3A COP. The pump was manually shut down from Unit 4 Switch room. No signs of immediate damage were observed externally, however, nonuniform operation is suspected. Investigative actions were initiated pursuant to S3.OP-AB.CW-0002 Abnormal Noise Protocol. * * ACTIVITIES, PROCESSES, PROCEDURES INVOLVED: * Routine operation, Abnormal Noise Protocol under S3.OP-AB.CW-0002 * * WHY DID CONDITION HAPPEN: * Unknown at the moment. Excessive wear of the pump components or blockage due to debris could be the causes. * * CONSEQUENCES: * Noise indicates irregular functioning which could enhance the risk of mechanical failure. Effectiveness and reliable functionality of the unit might be compromised. * * REQUIREMENTS IMPACTED: * Operational efficiency, equipment health. * * ADVERSE PHYSICAL CONDITIONS: * Excessive noise levels from 3A COP, potential internal irregularities. * * WHO WAS NOTIFIED: * Switch Room Operators, Maintenance Department * * KNOWLEDGEABLE INDIVIDUALS: * Arnold, Lewis, Madison * * REPEAT OR SIMILAR CONDITION: * No direct repeat, but similar issues have been reported on other units * * IMMEDIATE ACTIONS AND RECOMMENDED ACTIONS: * Initiation of a detailed investigation of 3A COP * 09/15/2017 15:25:34 LUCY GOMEZ (INCIDENT) * The investigation revealed the noise was due to a build-up of debris and minor blockage. The pump was dismantled, cleaned, and reassembled. The pump is now | What was the cause of the excessive noise from the 3A COP? | The investigation revealed the noise was due to a build-up of debris and minor blockage.
148 | 2017-10-30 | 30921344 | 90138562 | Odd vibrations from 30A Pump | S5CW -2CWE7-MTRD | * ****************Incident Description***************** * Notification 000030921344 Details * ************************************************************** * SUMMARY: PRIMARY CHECKS MADE IN ACCORDANCE WITH * ***S5.OP-SO.CW-0002 "PUMP OPERATIONAL ASSESSMENT STANDARDS"**** * * 1) Condition Description/Location (The inappropriate action and its negative effect/Include a detailed location description): * At 1653 on 10/30/17, the maintenance crew reported unusual vibrations from the 30A Pump. An immediate shut down was initiated from the Control Room to prevent further complications. Technical inspection did not reveal any obvious external damage but recorded unusual vibration levels. Pump vibrations were atypical compared to other similar pumps currently in operation. This event triggered the rollout of S5.OP-AB.CW-0003, Pump Abnormality Standards due to the unexpected shutdown of 30A Pump. * 2) ACTIVITIES, PROCESSES, PROCEDURES INVOLVED: * S5.OP.AB-CW-0003, S5.OP-SO.CW-0002 * 3) WHY DID CONDITION HAPPEN: * Unclear, although similar pump vibrations have been observed in the past * 4) CONSEQUENCES: * Immediate consequences include reduced efficiency, potential internal pump damage * 5) REQUIREMENTS IMPACTED: * Out of service Pump * 6) ADVERSE PHYSICAL CONDITION: * Unusual vibrations from 30A Pump motor, possible internal damage * 7) WHO WAS NOTIFIED: * Control Room, Maintenance Team * 8) KNOWLEDGEABLE INDIVIDUALS: * Raymond, Phillips, Carter * 9) REPEAT OR SIMILAR CONDITION: * Yes, similar instances have occurred * 10) IMMEDIATE AND RECOMMENDED ACTIONS: * Technical team to investigate the 30A Pump Motor * * Updated: JOHN SMITH, 10.30.2017 20:30:21 * ------------------------------------------------------------ * 11/02/2017 09:30:45 SUSAN JO | What were the immediate actions taken when the unusual vibrations were reported from the 30A Pump? | An immediate shut down was initiated from the Control Room to prevent further complications.
149 | 2019-12-11 | 30824579 | 80199834 | Pump 5B unusual vibration | S5CW -5CWE2 | * **************Incident Description************** * Notification 000030824579 Details * *********************************************************** * 12/11/2019 19:15:24 INCIDENT REPORT (INCIDENT REPORT) * Report submitted by: Olivia Green ENTITY\INCIDENT: * * CONDITION DESCRIPTION/LOCATION (THE INAPPROPRIATE ACTION AND ITS NEGATIVE EFFECT/INCLUDE A DETAILED LOCATION DESCRIPTION): * On 12/11/2019, during routine maintenance, it was noticed that Pump 5B began to vibrate unusually. The initial check did not reveal any visible cause. The pump was isolated and taken offline to avoid further risk. * * ACTIVITIES, PROCESSES, PROCEDURES INVOLVED: * Routine maintenance, S5.OP-SO.CW-0002, S5.OP-AB.CW-0008 * * WHY DID CONDITION HAPPEN? * The cause is unknown at the moment. The pump did not show any signs of unusual behavior before today. * * CONSEQUENCES: * Continuous operation in this condition could lead to pump damage or breakdown. * * REQUIREMENTS IMPACTED: * Reduced pumping efficiency, potential delay in routine operation. * * ADVERSE PHYSICAL CONDITIONS: * High vibration level on pump 5B. * * WHO WAS NOTIFIED: * Supervisor, Maintenance Team * * KNOWLEDGEABLE INDIVIDUALS: * Maintenance Team, Supervisor, Technical Lead * * REPEAT OR SIMILAR CONDITION: * No, this is the first incident of unusual vibration on pump 5B. * * IMMEDIATE ACTIONS AND RECOMMENDED ACTIONS: * The pump was taken off-line immediately. A detailed inspection is recommended to identify the cause of the vibration. * 12/12/2019 09:28:50 OLIVIA GREEN (INCIDENT) * Maintenance team will initiate inspection to trace the root cause of the vibration. All findings will be documented and necessary repairs, if any, will be carried out as soon as possible. | What immediate action was taken upon discovering the unusual vibrations in pump 5B? | The pump was taken off-line immediately.
150 | 2018-12-01 | 30851277 | 80234598 | Vibration detected on Static Transfer Switch | S1SW -1BWR3-ELED | * **************Incident Description************** * Notification 000030851277 Details * *********************************************************** * 12/01/2018 06:15:00 INCIDENT REPORT (INCIDENT REPORT) * Report submitted by: George Lopez ENTITY\INCIDENT: * * 1) CONDITION DESCRIPTION/LOCATION (THE INAPPROPRIATE ACTION AND ITS NEGATIVE EFFECT/INCLUDE A DETAILED LOCATION DESCRIPTION): * At approximately 05:50 on 12/01/18, an anomaly was observed with the Static Transfer Switch. The switch initiated an unexpected transfer to the alternate power source. It was also observed that the unit appeared to be vibrating. * * 2) ACTIVITIES, PROCESSES, PROCEDURES INVOLVED: * S1.OP.EL.SW-0002, S1.OP.EL.BW-0003 * * 3) WHY DID CONDITION HAPPEN: * At this time the cause of the issue is unknown but switches have shown similar disturbances in the past * * 4) CONSEQUENCES: * Unintended power transfers could lead to downtime if the alternate power source is unavailable. * * 5) REQUIREMENTS IMPACTED: * Uninterrupted power transfer * * 6) ADVERSE PHYSICAL CONDITION: * Unusual vibration of the Static Transfer Switch and unintended power transfer * * 7) WHO WAS NOTIFIED: * Supervisor, Electrical Department * * 8) KNOWLEDGEABLE INDIVIDUALS: * Jackson, Cook, Williams * * 9) REPEAT OR SIMILAR CONDITION: * Yes, similar incidents have occurred sporadically * * 10) IMMEDIATE AND RECOMMENDED ACTIONS: * Electrical Department to conduct a thorough investigation of the issue and recommend a course of action * * Updated: GEORGE LOPEZ 12.01.2018 08:00:19 * ------------------------------------------------------------ * 12/10/2018 13:31:48 JOHN DOE, P.E. (INCIDENT) * The investigation has been carried out and it was determined that the issue was due to a loose connection causing unsteady | What was the identified cause of the Static Transfer Switch issue? | The issue was due to a loose connection causing unsteady.
151 | 2018-02-15 | 30760177 | 80020212 | 16B pump abnormal vibration | S4TW -4TWE5 | * **************Incident Description************** * Notification 000030760177 Details * *********************************************************** * 0215/15/2018 10:45:28 INCIDENT REPORT (INCIDENT REPORT) * Report submitted by: David Williams ENTITY\INCIDENT: * * CONDITION DESCRIPTION/LOCATION (THE INAPPROPRIATE ACTION AND ITS NEGATIVE EFFECT/INCLUDE A DETAILED LOCATION DESCRIPTION): * Operator noted abnormal vibration from the 16B Pump during the routine rounds. Vibration levels were high, but the pump performance was within acceptable limits. The location was near the Unit 4 cooling tower, specifically on 16B pump. * * ACTIVITIES, PROCESSES, PROCEDURES INVOLVED: * S4.OP.AB-TW-0001: Routine checks and monitoring * * WHY DID CONDITION HAPPEN? * Unknown, could be caused by misalignment, bearing issues or other internal defects. * * CONSEQUENCES: * Potential mechanical damage and unplanned pump outage. * * REQUIREMENTS IMPACTED: * Potential upset in cooling tower operation. * * ADVERSE PHYSICAL CONDITIONS: * High vibration on 16B Pump * * WHO WAS NOTIFIED: * Supervisor, Maintenance team, Control Room. * * KNOWLEDGEABLE INDIVIDUALS: * Dylan Chase, Maria Collins. * * REPEAT OR SIMILAR CONDITION: * Yes, similar issues reported in the past. * * IMMEDIATE ACTIONS AND RECOMMENDED ACTIONS: * Maintenance team was alerted to investigate the cause of vibration, if vibration worsens then shut the pump immediately and check for internal damages. * 02/17/2018 11:56:47 JANE DOE (INCIDENT) * After inspection, it was found that the misalignment in the pump caused the high vibration. The pump was realigned, after which the vibrations reduced to normal level. The system is back online and functioning within normal parameters. Further monitor for any abnormality. | What immediate action was taken upon observing the abnormal vibration on the 16B pump? | Maintenance team was alerted to investigate the cause of vibration, if vibration worsens then shut the pump immediately and check for internal damages.
152 | 2022-01-11 | 30915470 | 80253640 | Overheating of 05B compressor unit | S4CW -4CWE9 | * **************Incident Description************** * Notification 000030915470 Details * *********************************************************** * 01/11/2022 15:05:00 INCIDENT REPORT (INCIDENT REPORT) * Report submitted by: David Foster ENTITY\INCIDENT: * * CONDITION DESCRIPTION/LOCATION (THE INAPPROPRIATE ACTION AND ITS NEGATIVE EFFECT/INCLUDE A DETAILED LOCATION DESCRIPTION): * At 1420hrs on 11/1/22, the 05B compressor unit showed signs of overheating. Cooling operations were initiated and the unit was brought offline to prevent further damage. The condition was noted during routine health monitoring of the unit. * * ACTIVITIES, PROCESSES, PROCEDURES INVOLVED: * S4.OP.AB-CW-0003, Routine Unit Monitoring * * WHY DID CONDITION HAPPEN? * Possible failure of the cooling system, investigation is ongoing. * * CONSEQUENCES: * Potential damage to compressor unit, reduced compressor availability. * * REQUIREMENTS IMPACTED: * Normal operations of the compressor. * * ADVERSE PHYSICAL CONDITIONS: * Overheating Compressor Unit * * WHO WAS NOTIFIED: * Supervisor, Operations Team, Maintenance Team * * KNOWLEDGEABLE INDIVIDUALS: * Ops Lead, Maintenance Lead, Engineers * * REPEAT OR SIMILAR CONDITION: * No, first-time occurrence * * IMMEDIATE ACTIONS AND RECOMMENDED ACTIONS: * Initiate investigation of cooling failure, maintenance check of other compressor units. * * 01/13/2022 09:10:15 DAVID FOSTER (INCIDENT) * The overheating was determined to be the result of a blockage in the coolant lines of the compressor unit. The unit has been repaired and is now operational after the lines have been cleaned. Maintenance has been advised to include this in their periodic checks. | What was the identified cause of the overheating of the 05B compressor unit? | The overheating was determined to be the result of a blockage in the coolant lines of the compressor unit.
153 | 2020-02-15 | 30765489 | 90248736 | Moisture detected in Pump 18C motor | S4CW -4CWE7 | * **************Incident Description************** * Notification 000030765489 Details * *********************************************************** * 02/15/2020 06:48:59 INCIDENT REPORT (INCIDENT REPORT) * Report submitted by: Emily Jones 555-666-7777 ENTITY\INCIDENT: * CONDITION DESCRIPTION/LOCATION (THE INAPPROPRIATE ACTION AND ITS NEGATIVE EFFECT/INCLUDE A DETAILED LOCATION DESCRIPTION): * During insulation resistance test, moisture was detected within the insulation of the Pump 18C motor. The moisture could cause shorting and pose a risk of equipment damage and potential safety hazards. * * ACTIVITIES, PROCESSES, PROCEDURES INVOLVED: * Routine maintenance check and insulation resistance testing * * WHY DID CONDITION HAPPEN? * Possible insulation failure due to aging or exposure to environmental conditions. * * CONSEQUENCES: * Potential for equipment failure and safety risks * * REQUIREMENTS IMPACTED: * Equipment safety and reliability * * ADVERSE PHYSICAL CONDITIONS: * Presence of moisture within pump motor insulation * * WHO WAS NOTIFIED: * Maintenance Team, Supervisor * * KNOWLEDGEABLE INDIVIDUALS: * Emily Jones, Maintenance Team, Supervisor * * REPEAT OR SIMILAR CONDITION: * No previous incidents of this nature * * IMMEDIATE ACTIONS AND RECOMMENDED ACTIONS: * Immediate drying of the motor's insulation and further inspection to determine the extent of the moisture intrusion to prevent future incidents. * 02/15/2020 09:12:20 EMILY JONES (INCIDENT) * Pump motor has been dried and retested. No further traces of moisture detected. Recommend routine inspections for moisture intrusion as standard part of maintenance procedure. | What were the immediate actions taken after the detection of moisture in the pump motor's insulation? | Immediate drying of the motor's insulation and further inspection to determine the extent of the moisture intrusion to prevent future incidents.
154 | 2021-06-18 | 31557293 | 90234567 | Unusual vibration on generator 10C | S5GN -5GWE10 | * **************Incident Description************** * Notification 000031557293 Details * *********************************************************** * 06/18/2021 15:15:33 INCIDENT REPORT (INCIDENT REPORT) * Report submitted by: Emily Walker * * CONDITION DESCRIPTION/LOCATION (THE INAPPROPRIATE ACTION AND ITS NEGATIVE EFFECT/INCLUDE A DETAILED LOCATION DESCRIPTION): * At 1530 hours on 6/18/21, maintenance reported unusual vibration on generator 10C. The anomaly was identified during a routine condition monitoring inspection. The machine was promptly idled to prevent potential damage. * * ACTIVITIES, PROCESSES, PROCEDURES INVOLVED: * Routine Condition Monitoring * * WHY DID CONDITION HAPPEN? * Not immediately known; it could possibly be alignment issues or loose components. Earlier instances indicated bearing issues. * * CONSEQUENCES: * Continual operation in this state can cause severe damage to the generator and disrupt power supply. * * REQUIREMENTS IMPACTED: * Unavailable generator could potentially affect power supply, possibly leading to loss of electricity for dependent equipment or sections. * * ADVERSE PHYSICAL CONDITIONS: * Unusual vibration noted on Generator 10C. * * WHO WAS NOTIFIED: * Maintenance Supervisor, Incident Team * * KNOWLEDGEABLE INDIVIDUALS: * William Mathews - Head of Maintenance, Incident team * * REPEAT OR SIMILAR CONDITION: * Yes, but not often on this generator * * IMMEDIATE ACTIONS AND RECOMMENDED ACTIONS: * The generator is currently idled for maintenance technicians to investigate. If similar bearing issues are noted, necessary replacements should be initiated quickly to restore machine to operational status. Rigorous monitoring should follow post-maintenance to assure correct operation. * 06/21/2021 11:03:47 EMILY WALKER (Incident Response Coordinator) * Maintenance report indicates an imbalance issue due to looseness in the rotor. The fancy shaft has been realigned and the generator is now back in duty after a successful run trial. Regular monitoring is advised for the next couple of days. | What was the identified issue with generator 10C and how was it addressed? | Maintenance report indicates an imbalance issue due to looseness in the rotor. The fancy shaft has been realigned and the generator is now back in duty after a successful run trial. Regular monitoring is advised for the next couple of days.
155 | 2017-12-12 | 30778091 | 80223491 | 14B Cooling Pump abnormal vibration | S4CW -4CWE7 | * **************Incident Description************** * Notification 000030778091 Details * *********************************************************** * 12/12/2017 13:40:47 INCIDENT REPORT (INCIDENT REPORT) * Report submitted by: William Foster ENTITY\INCIDENT: * * CONDITION DESCRIPTION/LOCATION (THE INAPPROPRIATE ACTION AND ITS NEGATIVE EFFECT/INCLUDE A DETAILED LOCATION DESCRIPTION): * Today at 0910, during a routine inspection, abnormal vibration was observed in the 14B Cooling Pump. The pump was immediately shut down to prevent any potential damage. There was no sign of overheating or leakage, but the vibration was definitely higher than the standard baseline. * * ACTIVITIES, PROCESSES, PROCEDURES INVOLVED: * Inspection of pump, immediate shutdown. * * WHY DID CONDITION HAPPEN? * Exact reason is unknown. It is suspected that either there is an imbalance due to debris or a mechanical failure inside the pump. * * CONSEQUENCES: * If not addressed, the abnormal vibration could lead to mechanical failure causing loss of pump function and possible damage to surrounding equipment. * * REQUIREMENTS IMPACTED: * Operational efficiency and safety are at risk * * ADVERSE PHYSICAL CONDITIONS: * Excessive vibration in 14B Cooling Pump. * * WHO WAS NOTIFIED: * Maintenance Supervisor, Operations Control, and Engineer on duty. * * KNOWLEDGEABLE INDIVIDUALS: * McCraw, Rodriguez, Haynes. * * REPEAT OR SIMILAR CONDITION: * No * * IMMEDIATE ACTIONS AND RECOMMENDED ACTIONS: * Maintenance team to conduct thorough inspection and carry out necessary repairs or part replacements. Investigation required to find the root source of the vibration. * 12/13/2017 16:23:17 WILLIAM FOSTER (INCIDENT) * Initial inspection shows signs of possible impeller imbalance. Dismantling and detailed inspection planned. More updates to follow. | What immediate action was taken when abnormal vibration was detected in the cooling pump? | The pump was immediately shut down to prevent any potential damage.
156 | 2020-12-04 | 30900132 | 80222030 | Fluctuations in 18A coolant pump output | S1CW -1CWE5 | * **************Incident Description************** * Notification 000030900132 Details * *********************************************************** * 12/04/2020 10:23:48 INCIDENT REPORT (INCIDENT REPORT) * Report submitted by: Howard Baker ENTITY\INCIDENT: * * CONDITION DESCRIPTION/LOCATION (THE INAPPROPRIATE ACTION AND ITS NEGATIVE EFFECT/INCLUDE A DETAILED LOCATION DESCRIPTION): * While performing system monitoring duties, fluctuations were observed in the output of the 18A coolant pump system. These deviations from the standard output could potentially affect the effectiveness of the coolant system, risking overheating and performance issues. * * ACTIVITIES, PROCESSES, PROCEDURES INVOLVED: * Regular system monitoring and performance checks * * WHY DID CONDITION HAPPEN? * The cause of the fluctuation is unknown at this time. However, possibilities include issues with the power supply, worn out components, or a buildup of debris in the system. * * CONSEQUENCES: * In the event of further degradation, the pump output could fall below necessary levels, potentially causing overheating and a cascade of related issues. * * REQUIREMENTS IMPACTED: * Routine pump operation and system cooling * * ADVERSE PHYSICAL CONDITIONS: * Fluctuations in pump output could potentially lead to overheating, leading to potential serious damage. * * WHO WAS NOTIFIED: * Maintenance Team, Incident Reporting Team * * KNOWLEDGEABLE INDIVIDUALS: * Maintenance Team, System Engineers * * REPEAT OR SIMILAR CONDITION: * No * * IMMEDIATE ACTIONS AND RECOMMENDED ACTIONS: * Maintenance Team to investigate the source of the fluctuations and fix if needed. This could involve cleaning or replacing the pump, or troubleshooting the power supply. * 12/07/2020 09:45:00 JOHN DOE (INCIDENT) * After inspection, no significant material buildup was found. Fluctuations have subsided after a system reset, but are being closely monitored for further anomalies. Guidance has been updated in the system monitoring procedures to check for such output fluctuations. | What actions were taken following the identification of the incident? | Maintenance Team to investigate the source of the fluctuations and fix if needed. This could involve cleaning or replacing the pump, or troubleshooting the power supply. After inspection, no significant material buildup was found. Fluctuations have subsided after a system reset, but are being closely monitored for further anomalies. Guidance has been updated in the system monitoring procedures to check for such output fluctuations.
157 | 2018-04-16 | 30890732 | 80228501 | Abnormal Vibration in 7B Pump | S3CW -3CWE8 | * **************Incident Description************** * Notification 000030890732 Details * *********************************************************** * 04/16/2018 15:47:23 INCIDENT REPORT (INCIDENT REPORT) * Report submitted by: David Wills ENTITY\INCIDENT : * * CONDITION DESCRIPTION/LOCATION (THE INAPPROPRIATE ACTION AND ITS NEGATIVE EFFECT/INCLUDE A DETAILED LOCATION DESCRIPTION): * During the 6-hourly condition monitoring round, abnormal vibration from the 7B Pump was reported. No other unusual metrics were noted. Immediate shut down was carried out from the main control room and the vibration subsided. Further examination will be required to determine the reason for this condition. * * ACTIVITIES, PROCESSES, PROCEDURES INVOLVED: * S3.OP.EX.CW-0003, S2.OP-AB.CW-0005 were followed for the shut down. * * WHY DID CONDITION HAPPEN? * Unknown, could be due to misalignment or a mechanical issue. * * CONSEQUENCES: * Severe damage to pump if it continued to operate under such conditions. * * REQUIREMENTS IMPACTED: * Disruption of regular operation due to shut down. * * ADVERSE PHYSICAL CONDITIONS: * Rise in vibration levels in 7B pump. * * WHO WAS NOTIFIED: * Control Room was notified immediately. Maintenance Department was informed for further inspection. * * KNOWLEDGEABLE INDIVIDUALS: * Cooper, Johnson, Black. * * REPEAT OR SIMILAR CONDITION: * No such incidents with the 7B pump reported earlier. * * IMMEDIATE ACTIONS AND RECOMMENDED ACTIONS: * Arrangement for maintenance inspection and necessary repairs. * 04/17/2018 08:15:44 JASON BLACK (INCIDENT) * After inspection, it was observed that the bearing was worn out causing the abnormal vibration. The bearing was replaced and the pump was re-started. The vibration levels have returned to the norms. | What was the cause of the abnormal vibration in the 7B Pump? | After inspection, it was observed that the bearing was worn out causing the abnormal vibration. The bearing was replaced and the pump was re-started. The vibration levels have returned to the norms.
158 | 2019-11-23 | 30856241 | 90134675 | Abnormal vibration at 18B Pump Post-Repair | S4CW -4CWE4 | * **************Incident Description************** * Notification 000030856241 Details * *********************************************************** * 11/23/2019 15:30:21 INCIDENT REPORT (INCIDENT REPORT) * Report submitted by: Kelly Thompson ENTITY\INCIDENT: * * CONDITION DESCRIPTION/LOCATION (THE INAPPROPRIATE ACTION AND ITS NEGATIVE EFFECT/INCLUDE A DETAILED LOCATION DESCRIPTION): * Following scheduled maintenance, 18B Pump exhibited distinct vibration. The pump had been serviced under work order 90127930 to replace the driveshaft. Now that it is re-installed and in operation, abnormal vibration is observed. Based on pump history, such behavior is not expected post-maintenance. * * ACTIVITIES, PROCESSES, PROCEDURES INVOLVED: * Post-Maintenance Operation of 18B Pump * * WHY DID CONDITION HAPPEN? * The root cause is not immediately clear, it might be related to driveshaft installation. * * CONSEQUENCES: * Left unchecked, abnormal vibration could lead to premature mechanical failure and unplanned downtime. * * REQUIREMENTS IMPACTED: * Usual pump operation and maintenance schedules. * * ADVERSE PHYSICAL CONDITIONS: * Prolonged exposure to unexpected vibration levels could lead to mechanical malfunction. * * WHO WAS NOTIFIED: * Maintenance Supervisor, Operations Manager * * KNOWLEDGEABLE INDIVIDUALS: * Motor Engineers * * REPEAT OR SIMILAR CONDITION: * No, this is a new condition post-maintenance. * * IMMEDIATE ACTIONS AND RECOMMENDED ACTIONS: * Immediate shutdown and inspection of the pump. Mechanical engineers should evaluate the driveshaft installation and vibration source. * 11/24/2019 11:32:12 KELLY THOMPSON (INCIDENT) * Pump maintenance team dispatched, 18B Pump is currently under inspection. Further updates to be provided upon assessment completion. The team will focus on the driveshaft as initial point of suspicion. | What immediate actions were recommended after the distinct vibration was observed in the 18B Pump? | Immediate shutdown and inspection of the pump. Mechanical engineers should evaluate the driveshaft installation and vibration source.
159 | 2020-12-05 | 30875942 | 80267912 | Incidence of high vibration in 3A pump | S4CW -4CWE8 | * **************Incident Description************** * Notification 000030875942 Details * *********************************************************** * 12/05/2020 08:29:46 INCIDENT REPORT (INCIDENT REPORT) * Report submitted by: Robert Johnson ENTITY\INCIDENT: * CONDITION DESCRIPTION/LOCATION (THE INAPPROPRIATE ACTION AND ITS NEGATIVE EFFECT/INCLUDE A DETAILED LOCATION DESCRIPTION): * During the operation shift, a high vibration incidence in 3A pump was observed. The vibration monitor recorded readings showing a significant increase over the norm for this equipment. * * ACTIVITIES, PROCESSES, PROCEDURES INVOLVED: * S4.OP-SO.CW-0005, S4.OP-SO.CW0004 * * WHY DID CONDITION HAPPEN? * Not immediately clear. Cause could be mechanical damage, alignment issue, or less likely, a process disturbance. * * CONSEQUENCES: * Prolonged operation under these conditions could lead to severe damage to the pump and affect the unit's availability. * * REQUIREMENTS IMPACTED: * Reliability of the 3A Pump system. * * ADVERSE PHYSICAL CONDITIONS: * High vibrational levels on the 3A Pump. * * WHO WAS NOTIFIED: * Maintenance Superintendent, Operations Manager * * KNOWLEDGEABLE INDIVIDUALS: * Harry Wilson, Operations Technician; Jenna Simmons, Vibration Analyst * * REPEAT OR SIMILAR CONDITION: * No, this is the first time such an issue has been raised regarding this equipment. * * IMMEDIATE ACTIONS AND RECOMMENDED ACTIONS: * Immediate shutdown of the pump and conduct a detailed vibration analysis to determine the root cause. * Update: ROBERT JOHNSON 12.05.2020 16:24:12 ------------------------------------------------------------ * 12/12/2020 14:45:01 JOHN SMITH (Maintenance Technician) * The pump was shut down and a detailed investigation was carried out. It was found that misalignment was the cause of the high vibrations. After realignment and balancing of the pump, it was put back into service. | What was the immediate action taken after observing the high vibration incidence in the pump? | Immediate shutdown of the pump and conduct a detailed vibration analysis to determine the root cause.
160 | 2021-05-12 | 30922345 | 80232815 | 33B pump unusual vibration | S4CW -4CWE8 | * **************Incident Description************** * Notification 000030922345 Details * *********************************************************** * 05/12/2021 14:16:56 INCIDENT REPORT (INCIDENT REPORT) * Report submitted by: Olivia Smith ENTITY\INCIDENT: * * CONDITION DESCRIPTION/LOCATION (THE INAPPROPRIATE ACTION AND ITS NEGATIVE EFFECT/INCLUDE A DETAILED LOCATION DESCRIPTION): * During maintenance check run, a strong unusual vibration was noticed in the 33B Pump. This was not normal. It was isolated immediately, and an emergency inspection was initiated. * * ACTIVITIES, PROCESSES, PROCEDURES INVOLVED: * Maintenance check run, immediate isolation and emergency inspection * * WHY DID CONDITION HAPPEN? * Cause undetermined. Possible alignment issues or damage to internal components. * * CONSEQUENCES: * Potential failure of the 33B pump, causing interruption to normal operation. * * REQUIREMENTS IMPACTED: * Maintenance procedure and pump operation * * ADVERSE PHYSICAL CONDITIONS: * Unusual high vibration on 33B pump * * WHO WAS NOTIFIED: * Control Room, Supervisor, Maintenance Team * * KNOWLEDGEABLE INDIVIDUALS: * Olivia Smith, Maintenance Team * * REPEAT OR SIMILAR CONDITION: * No * * IMMEDIATE ACTIONS AND RECOMMENDED ACTIONS: * An inspection of internal components and alignment to be carried out. Detailed analysis of vibration data is needed. * * 05/12/2021 18:06:22 OLIVIA SMITH (INCIDENT) * A first inspection revealed no obvious mechanical failure. Vibration levels have reduced after initial observation but remain higher than normal. Machine alignment to be checked next, and a vibration analysis specialist has been contacted for a detailed assessment. | What immediate actions were taken following the detection of unusual high vibration in the 33B pump? | Immediate actions were "Maintenance check run, immediate isolation and emergency inspection." Additionally, "An inspection of internal components and alignment to be carried out. Detailed analysis of vibration data is needed."
161 | 2019-04-03 | 31012476 | 90247890 | Clogged filter in Pump 18B | S4CL -4CLF3-MTR9 | * **************Incident Description************** * Notification 000031012476 Details * *********************************************************** * 04/03/2019 15:33:42 INCIDENT REPORT (INCIDENT REPORT) * Report submitted by: Emily Johnson ENTITY\INCIDENT: * * CONDITION DESCRIPTION/LOCATION (THE INAPPROPRIATE ACTION AND ITS NEGATIVE EFFECT/INCLUDE A DETAILED LOCATION DESCRIPTION): * On April 3rd at 1500 hours, Pump 18B was found to be operating at diminished efficiency by Control Room Operator Smith. It was discovered during a routine integrity check that the filter of pump 18B is clogged. The pump was taken offline immediately and an emergency work order was issued. * * ACTIVITIES, PROCESSES, PROCEDURES INVOLVED: * S4.OP.AB-CF-0003, S4.OP-SO.CF-0001 * * WHY DID CONDITION HAPPEN? * The exact cause is unclear at this stage, though it is suspected that build-up of normal system debris could be the culprit. * * CONSEQUENCES: * Diminished efficiency, potential of damage to pump internals due to restricted flow. * * REQUIREMENTS IMPACTED: * Normal pump operation. * * ADVERSE PHYSICAL CONDITIONS: * Restriction in flow through Pump 18B, increased vibration. * * WHO WAS NOTIFIED: * Control Room, Maintenance Team * * KNOWLEDGEABLE INDIVIDUALS: * Smith, Williams, Taylor * * REPEAT OR SIMILAR CONDITION: * No * * IMMEDIATE ACTIONS AND RECOMMENDED ACTIONS: * Initiation of emergency maintenance to clear filter and restore function. * 04/04/2019 09:12:22 EMILY JOHNSON (INCIDENT) * Maintenance successfully cleared the filter. Upon completion of work, the pump was restored back to its normal operational state. Further investigations are ongoing to prevent similar incidents. | What immediate actions were taken after the detection of the issue with Pump 18B? | Initiation of emergency maintenance to clear filter and restore function.
162 | 2022-03-10 | 30958330 | 80510020 | Failure of 17B coolant pump | S4CW -4CWE6 | * **************Incident Description************** * Notification 000030958330 Details * *********************************************************** * 03/10/2022 08:47:38 INCIDENT REPORT (INCIDENT REPORT) * Report submitted by: Jack Robinson ENTITY\INCIDENT: * * CONDITION DESCRIPTION/LOCATION (THE INAPPROPRIATE ACTION AND ITS NEGATIVE EFFECT/INCLUDE A DETAILED LOCATION DESCRIPTION): * On 3/10/22 at 0830, a complete failure was experienced with the 17B coolant pump. The pump stopped working abruptly, and there was a sudden decrease in the coolant flow rate. The cooling system dipped below the Safe Operating Limit (SOL). Efforts to restart the pump were not successful. The operational disruption led to quick activation of the standby pump. * * ACTIVITIES, PROCESSES, PROCEDURES INVOLVED: * Emergency pump activation - S4.OP.AB-CW-0002 * * WHY DID CONDITION HAPPEN? * Preliminary investigation suggests a potential mechanical failure, but a detailed inspection is warranted. * * CONSEQUENCES: * Interruption to normal operation, potential heat damage to equipment. * * REQUIREMENTS IMPACTED: * System redundancy and equipment integrity. * * ADVERSE PHYSICAL CONDITIONS: * Complete pump failure, potential heat buildup. * * WHO WAS NOTIFIED: * Site Maintenance Manager, Incident Team. * * KNOWLEDGEABLE INDIVIDUALS: * Jack Robinson, Sarah Mitchell * * REPEAT OR SIMILAR CONDITION: * No * * IMMEDIATE ACTIONS AND RECOMMENDED ACTIONS: * Detailed inspection of the failed pump, check system for potential heat damage, review of emergency pump operations. * 03/10/2022 12:30:43 JOHN CARTER (INCIDENT) * Inspection has begun, findings will be updated and necessary recommendations will be made promptly. | What immediate actions were recommended following the incident with the 17B coolant pump? | Detailed inspection of the failed pump, check system for potential heat damage, review of emergency pump operations.
163 | 2018-12-12 | 35064820 | 80235072 | Unexpected vibration in pump 17B | S4CW -4CWE5 | * **************Incident Description************** * Notification 000035064820 Details * *********************************************************** * 12/12/2018 14:35:00 INCIDENT REPORT (INCIDENT REPORT) * Report submitted by: RICHARD HARRISON ENTITY\INCIDENT: * * CONDITION DESCRIPTION/LOCATION (THE INAPPROPRIATE ACTION AND ITS NEGATIVE EFFECT/INCLUDE A DETAILED LOCATION DESCRIPTION): * During operating rounds, the operator reported unusual vibrations on 17B Pump motor. The pump was taken out of service from Unit 4 and was barred over. No obvious damage was visible when the motor was inspected visually after shutdown. The vibrations reportedly stopped after shutdown. * * ACTIVITIES, PROCESSES, PROCEDURES INVOLVED: * Surveillance rounds, S4.OP-SO.CW-0004 * * WHY DID CONDITION HAPPEN: * Unknown, it may be due to bearing wear or internal mechanical issues. * * CONSEQUENCES: * If not investigated and resolved, it could potentially lead to mechanical breakdown of the pump * * REQUIREMENTS IMPACTED: * Pump 17B taken out of service * * ADVERSE PHYSICAL CONDITIONS: * Unusual vibrations from 17B pump * * WHO WAS NOTIFIED: * Maintenance Team, Control Room Supervisor * * KNOWLEDGEABLE INDIVIDUALS: * WILSON, KATIE, PETER * * REPEAT OR SIMILAR CONDITION: * No, this is the first observation of this condition on 17B Pump. * * IMMEDIATE ACTIONS AND RECOMMENDED ACTIONS: * Maintenance team to conduct thorough investigation of 17B pump prior to placing it back in service. Cause of the vibrations needs to be identified and rectified before the pump is restarted. * 12/14/2018 10:30:45 RICHARD HARRISON (INCIDENT) * Pump 17B has been investigated, it was found that a bearing was loose and that had caused the vibrations. The bearing was replaced and the pump was tested successfully with no unusual vibrations noted. | What was the immediate action taken when unusual vibrations were reported on 17B pump motor? | The pump was taken out of service from Unit 4 and was barred over. Maintenance team to conduct thorough investigation of 17B pump prior to placing it back in service. Cause of the vibrations needs to be identified and rectified before the pump is restarted.
164 | 2018-12-14 | 30914231 | 85034789 | Unusual Oil Leak in 32D Motor | S4MC -4MCE7 | * **************Incident Description************** * Notification 000030914231 Details * *********************************************************** * 12/14/2018 17:33:00 INCIDENT REPORT (INCIDENT REPORT) * Report submitted by: Samantha Green ENTITY\INCIDENT: * * CONDITION DESCRIPTION/LOCATION (THE INAPPROPRIATE ACTION AND ITS NEGATIVE EFFECT/INCLUDE A DETAILED LOCATION DESCRIPTION): * On 12/14/18, a control room operator noticed an unexpected oil leak from 32D Motor during the routine check. Oil spill observed on floor. Immediate shut down was initiated according to Procedure S4.OP-AB.MC-0035. The source of leak was found to be from a broken seal on the oil pump. * * ACTIVITIES, PROCESSES, PROCEDURES INVOLVED: * S4.OP.AB-MC-0035, S4.OP.SO.MC-0007 * * WHY DID CONDITION HAPPEN? * The exact reason for the broken seal is not clear yet. Though seal wear-and-tear is expected with operating time, such a failure is unusual. * * CONSEQUENCES: * Potential damage to the motor due to lack of lubrication, possible environmental impact due to oil spill * * REQUIREMENTS IMPACTED: * 32D unit operation, environmental compliance * * ADVERSE PHYSICAL CONDITIONS: * Oil leak from 32D Motor, possible motor damage * * WHO WAS NOTIFIED: * Control room, Maintenance Supervisor, and Environmental department * * KNOWLEDGEABLE INDIVIDUALS: * Davis, Robinson, Bailey * * REPEAT OR SIMILAR CONDITION: * No * * IMMEDIATE ACTIONS AND RECOMMENDED ACTIONS: * Replacement of the broken seal and thorough inspection of the unit for any similar issue. Investigation into the cause of seal failure. * * Updated: SAMANTHA GREEN 12.14.2018 18:30:22 * ------------------------------------------------------------ * 12/18/2018 08:25:51 JASON BAKER (MAIN) * Upon inspection, seal failure due to an unexpected fluctuation in | What immediate action was taken when the oil leak from the 32D Motor was discovered? | Immediate shut down was initiated according to Procedure S4.OP-AB.MC-0035.
165 | 2019-01-17 | 30986837 | 80231589 | Overheating in 11A Motor Post Maintenance | S4TF -4TFE6-RITL | * **************Incident Description************** * Notification 000030986837 Details * *********************************************************** * 01/17/2019 14:32:12 INCIDENT REPORT (INCIDENT REPORT) * Report submitted by: Emily Green ENTITY\INCIDENT: * * CONDITION DESCRIPTION/LOCATION (THE INAPPROPRIATE ACTION AND ITS NEGATIVE EFFECT/INCLUDE A DETAILED LOCATION DESCRIPTION): * After the procedure under work order 80231589, overheating was noticed in the 11A motor of unit 4. The temperature margin differed significantly compared to other units. Overheating was not present prior to maintenance. * * ACTIVITIES, PROCEDURES, PROCESSES INVOLVED: * S4.OP.AB-TF-0001, S4.OP-SO.TF-0002 * * WHY DID CONDITION HAPPEN? * Uncertain, potentially due to enhancements in the motor components or assembly process during maintenance. * * CONSEQUENCES: * Possibility of motor failure and reduction in machine effectiveness * * REQUIREMENTS IMPACTED: * Normal functioning of unit * * ADVERSE PHYSICAL CONDITIONS: * Overheating of 11A motor, potential internal wear or damage * * WHO WAS NOTIFIED: * Supervisor, Maintenance department, and engineering unit * * KNOWLEDGEABLE INDIVIDUALS: * Thompson, Evelyn, Brown * * REPEAT OR SIMILAR CONDITION: * No, this is a unique issue. * * IMMEDIATE ACTIONS AND RECOMMENDED ACTIONS: * Persistent monitoring of motor temperature, Engineers to explore adjustments in the component designs and update process guidance. * 01/18/2019 11:08:43 EMILY GREEN (INCIDENT) * After closer inspection, no internal damage was found. However, modifications in the motor components seem to be affecting normal temperature levels. An update in procedure guidelines is strongly recommended for similar future enhancements. | What immediate and recommended actions were proposed following the overheating of the 11A motor in unit 4? | Persistent monitoring of motor temperature, Engineers to explore adjustments in the component designs and update process guidance.
166 | 2017-09-30 | 30759140 | 80245566 | Interruption with 30C Pump System | S1CW -1CWE1-CMTR | * **************Incident Description************** * Notification 000030759140 Details * *********************************************************** * REPORT DATE: 09/30/2017 14:12:00 * Report submitted by supervisor Sam Walton. * ENTITY\INCIDENT: * * 1) CONDITION DESCRIPTION/LOCATION (THE INAPPROPRIATE ACTION AND ITS NEGATIVE EFFECT/INCLUDE A DETAILED LOCATION DESCRIPTION): * At 1420 on the 30/09/2017, Operator Johnson reported an issue with the 30C Pump system. The system detection screen reported a pressure drop alongside a drop in fluid flow. The 30C Pump was manually shut down from Main Control Room, and an auxiliary pump was engaged. Initial investigation did not reveal any leaks but there was a significant drop in fluid temperatures. S1.OP-AB.CW-0002 Procedure Interruption was initiated due to the stop-prescribed operation of 30C Pump. * * 2) ACTIVITIES, PROCESSES, PROCEDURES INVOLVED: * S1.OP.AB-CW-0002, S1.OP-SO.CW-0002 * * 3) WHY DID CONDITION HAPPEN: * Unknown at present, although similar scenarios reported previously were due to valve failures. * * 4) CONSEQUENCES: * Potential immediate loss of efficiency, possible pump wear or damage over time if the issue isn’t addressed. * * 5) REQUIREMENTS IMPACTED: * Continuous operation * * 6) ADVERSE PHYSICAL CONDITION: * Pressure drop and unexpected halt of 30C pump operation, possible internal damage * * 7) WHO WAS NOTIFIED: * Control Room, Maintenance Team * * 8) KNOWLEDGEABLE INDIVIDUALS: * Davis, Lee, Smith * * 9) REPEAT OR SIMILAR CONDITION: * No * * 10) IMMEDIATE AND RECOMMENDED ACTIONS: * Initiate a detailed inspection of 30C Pump and system. * * Updated: SAM WALTON 09.30.2017 | What was the immediate action recommended after the incident involving 30C Pump system? | Initiate a detailed inspection of 30C Pump and system.
167 | 2020-11-11 | 30953236 | 80262059 | OVERHEATING OF 17B GENERATOR | S1GE -1GET1 | * **************Incident Description************** * Notification 000030953236 Details * *********************************************************** * 11/11/2020 16:32:24 INCIDENT REPORT (INCIDENT REPORT) * Report submitted by: Jennifer Thompson ENTITY\INCIDENT: * * CONDITION DESCRIPTION/LOCATION (THE INAPPROPRIATE ACTION AND ITS NEGATIVE EFFECT/INCLUDE A DETAILED LOCATION DESCRIPTION): * Presents the scenario whereby the 17B Generator was found to be overheating during the standard operational check. The unit was shut down immediately to prevent further damage. It was noted that the cooling system was functioning below optimal condition which could have triggered the generator's overheat protective system. * * ACTIVITIES, PROCESSES, PROCEDURES INVOLVED: * Unit operational check and emergency shutdown * * WHY DID CONDITION HAPPEN? * Likely due to the under-performance of the cooling system * * CONSEQUENCES: * Generator shutdown disrupts the continuity of service. * If overheating persists, heavy damage could occur leading to replacement. * * REQUIREMENTS IMPACTED: * Failure to meet power supply demands. * * ADVERSE PHYSICAL CONDITIONS: * Overheating of 17B generator. * * WHO WAS NOTIFIED: * Supervisor, Operations team * * KNOWLEDGEABLE INDIVIDUALS: * James Bradford, Systems Manager; Ali Mohammed, Lead Engineer. * * REPEAT OR SIMILAR CONDITION: * No * * IMMEDIATE ACTIONS AND RECOMMENDED ACTIONS: * A comprehensive check of the cooling system confirmed the malfunction. It was subsequently repaired with the generator restored to operation. Consideration to replace the cooling unit if the problem recurs. * * 11/12/2020 15:26:43 JAMES BRADFORD (INCIDENT) * Maintenance has reviewed the cooling system extensively. No further issues were found. System is now fully operational. Detailed logging of system performance for future reference is recommended, especially temperature readings during peaks hours of operation. | What were the consequences of the 17B Generator overheating? | Generator shutdown disrupts the continuity of service. If overheating persists, heavy damage could occur leading to replacement.
168 | 2017-04-22 | 30768549 | 80284537 | 7B Pump vibration issue post service | S4CW -4CWE8 | * **************Incident Description************** * Notification 000030768549 Details * *********************************************************** * 04/22/2017 15:37:00 INCIDENT REPORT (INCIDENT REPORT) * Report submitted by: Richard Carter ENTITY\INCIDENT: * * CONDITION DESCRIPTION/LOCATION (THE INAPPROPRIATE ACTION AND ITS NEGATIVE EFFECT/INCLUDE A DETAILED LOCATION DESCRIPTION): * In the recent 7B Pump service under work order 80248157, the pump has returned to operation with a concerning degree of vibration. The vibration was initially noticed in the routine inspection following completion of the service. The issue could suggest a potential pump alignment problem or a mechanical defect. * * ACTIVITIES, PROCESSES, PROCEDURES INVOLVED: * S4.OP.AB-CW-0004, Inspection following routine service * * WHY DID CONDITION HAPPEN? * Unknown, potential poor alignment or mechanical defect post service. * * CONSEQUENCES: * Extended use with this condition may result in premature failure of the pump. * * REQUIREMENTS IMPACTED: * Pump reliability, expected vibration levels * * ADVERSE PHYSICAL CONDITIONS: * Unusual vibration in 7B pump post service. * * WHO WAS NOTIFIED: * Maintenance Supervisor, Control Room * * KNOWLEDGEABLE INDIVIDUALS: * Carter, Green, Evans * * REPEAT OR SIMILAR CONDITION: * No, this is the first time for this situation. * * IMMEDIATE ACTIONS AND RECOMMENDED ACTIONS: * Schedule urgent attention for checking the alignment and general health check of the 7B Pump. If necessary, involve engineering. * 04/25/2017 17:02:34 RICHARD CARTER (INCIDENT) * The preliminary inspection shows a minor misallignment problem in the motor and pump shaft 7B. The motor and pump shall be re-aligned under supervision and the situation will be closely monitored. | What was the identified issue with the 7B pump after its recent service? | The pump has returned to operation with a concerning degree of vibration. The issue could suggest a potential pump alignment problem or a mechanical defect.
169 | 2021-04-12 | 30870125 | 80231960 | 16B Pump high vibration post-overhaul | S4CW -4CWE2 | * **************Incident Description************** * Notification 000030870125 Details * *********************************************************** * 04/12/2021 14:24:47 INCIDENT REPORT (INCIDENT REPORT) * Report submitted by: Grace Edwards ENTITY\INCIDENT: * * CONDITION DESCRIPTION/LOCATION (THE INAPPROPRIATE ACTION AND ITS NEGATIVE EFFECT/INCLUDE A DETAILED LOCATION DESCRIPTION): * 16B Pump, after undergoing a complete overhaul as per work order 80231960, was showing higher vibration levels than usual. This is not in alignment with historical data, as the pump, typically, post-maintenance should operate smoothly. * * ACTIVITIES, PROCESSES, PROCEDURES INVOLVED: * Maintenance Procedure S4.OP-SO.CW-0002 was followed during the overhaul * * WHY DID CONDITION HAPPEN? * The precise cause is unknown, but mechanical imbalance or poor assembly could be potential factors. * * CONSEQUENCES: * Could lead to premature wear of components, potential pump damage and operational inefficiency. * * REQUIREMENTS IMPACTED: * Usual operational status, as the equipment needs to be further analysed and rectified. * * ADVERSE PHYSICAL CONDITIONS: * High vibration levels in 16B pump post-maintenance * * WHO WAS NOTIFIED: * Maintenance Supervisor, Safety Team * * KNOWLEDGEABLE INDIVIDUALS: * Maintenance Supervisor, Safety Team, Technical Specialist * * REPEAT OR SIMILAR CONDITION: * No, this is an isolated incident. * * IMMEDIATE ACTIONS AND RECOMMENDED ACTIONS: * Thorough analysis of the assembly process, and potential re-balancing or re-assembly of the pump components. * 04/15/2021 09:24:47 GRACE EDWARDS (INCIDENT) * On thorough investigation, it was discovered that the rotor alignment was faulty. The pump was reassembled, balanced, and is now operating within normal vibration limits. | What corrective actions were taken after the improper maintenance incident involving the 16B Pump? | On thorough investigation, it was discovered that the rotor alignment was faulty. The pump was reassembled, balanced, and is now operating within normal vibration limits.
170 | 2013-04-18 | 30705603 | 80210207 | Unexpected vibration in 8B Pump Motor | S4CW -4CWE8 | * **************Incident Description************** * Notification 000030705603 Details * *********************************************************** * 04/18/2013 21:30:06 INCIDENT REPORT (INCIDENT REPORT) * Report submitted by: Max Short ENTITY\INCIDENT: * * CONDITION DESCRIPTION/LOCATION (THE INAPPROPRIATE ACTION AND ITS NEGATIVE EFFECT/INCLUDE A DETAILED LOCATION DESCRIPTION): * At 2110 on 04/18/13 during a regular inspection, a high level of vibration was observed on the 8B pump motor, beyond its normal operation parameters. The Pump was immediately stopped, resulting in no observable damage to the unit. No external signs of distress were noted, however the cause for vibration remains unknown. Immediate shut down procedure S4.OP-AB.CW-0006 criticality level 2 was initiated. * * ACTIVITIES, PROCESSES, PROCEDURES INVOLVED: * S4.OP.AB-CW-0006, S4.OP-SO.CW-0015 * * WHY DID CONDITION HAPPEN? * The root cause of this excessive vibration is yet to be determined. However, similar issues in other pump motors have been observed during times of high demand. * * CONSEQUENCES: * Immediate consequences include potential motor damage. If unchecked, possibility of mechanical failure when motor is back in service. * * REQUIREMENTS IMPACTED: * Regular pump operation * * ADVERSE PHYSICAL CONDITIONS: * High level of vibrations from 8B pump motor, potential internal damage. * * WHO WAS NOTIFIED: * Supervisor, Maintenance Team * * KNOWLEDGEABLE INDIVIDUALS: * Williams, Johnson, Thompson * * REPEAT OR SIMILAR CONDITION: * No. This is the first time 8B pump motor has shown such an abnormality. * * IMMEDIATE ACTIONS AND RECOMMENDED ACTIONS: * Conduct a thorough inspection and detailed study of 8B Pump Motor. Consult with engineering if necessary. * * Updated: MAX SHORT 04.18.2013 22:20:19 * ------------------------------------------------------------ * 04/ | What immediate actions were recommended after the excessive vibration was observed in the 8B pump motor? | Conduct a thorough inspection and detailed study of 8B Pump Motor. Consult with engineering if necessary.
171 | 2022-02-15 | 30829843 | 90204872 | Overheating of Pump 9C | S4CW -4CWE8 | * **************Incident Description************** * Notification 000030829843 Details * *********************************************************** * 02/15/2022 07:47:17 INCIDENT REPORT (INCIDENT REPORT) * Report submitted by: Patricia Watson 098-765-4321 * ENTITY\INCIDENT: * CONDITION DESCRIPTION/LOCATION (THE INAPPROPRIATE ACTION AND ITS NEGATIVE EFFECT/INCLUDE A DETAILED LOCATION DESCRIPTION): * During a routine round, the operator noticed Pump 9C was running hot. Based on the temperature reading of the pump, which was beyond the permissible limit, an immediate shutdown was initiated from Unit 4 Control Room. No traces of fire or smoke were reported; however, there was a distinct smell of burning insulation. The Pump, despite exhibiting higher temperature readings, showed no visible signs of external damage. * * ACTIVITIES, PROCESSES, PROCEDURES INVOLVED: * S4.OP-AB.CW-0002, S4.OP-SO.CW-0002 * * WHY DID CONDITION HAPPEN? * Unclear, although there have been past reports of pump overheating incidents. * * CONSEQUENCES: * Potential for equipment damage, leading to loss of efficiency or possible shutdown. * * REQUIREMENTS IMPACTED: * Regular pump operation, potential interruption of service * * ADVERSE PHYSICAL CONDITIONS: * Overheating of Pump 9C, possibly resulting in internal damage. * * WHO WAS NOTIFIED: * Supervisor, Engineering Team * * KNOWLEDGEABLE INDIVIDUALS: * Richards, Simpson, Cooper * * REPEAT OR SIMILAR CONDITION: * Yes, incidents of pump overheating have been reported in the past * * IMMEDIATE ACTIONS AND RECOMMENDED ACTIONS: * Maintenance to inspect Pump 9C and address potential issues. * 02/15/2022 13:32:50 PATRICIA WATSON (INCIDENT) * The subsequent investigation identified no electrical failure. Instead, excess debris had built up causing increased friction and subsequent heat. The debris has been removed, and the pump is now back in operation. Continued monitoring recommended. | What immediate action was taken when Pump 9C was found to be overheating? | An immediate shutdown was initiated from Unit 4 Control Room. No traces of fire or smoke were reported; however, there was a distinct smell of burning insulation. The Pump, despite exhibiting higher temperature readings, showed no visible signs of external damage.
172 | 2017-02-18 | 30947102 | 80284943 | Irregular Vibration from 18A Pump motor | S5CW -2CWE8-MTRF | * **************Incident Description************** * Notification 000030947102 Details * *********************************************************** * SUMMARY: EVALUATE POSSIBILITY IN ACCORDANCE WITH * ****PS-AA-125 "ISSUE IDENTIFICATION AND SCREENING PROCESS"***** * * 1) CONDITION DESCRIPTION/LOCATION (The inappropriate action and its negative effect/Include a detailed location description): * At 1502 on 2/18/17, maintenance staff identified that unusual vibration was coming from the 18A Pump motor. 18A Pump kept operating under constant vigil. Engineers were alerted and they confirmed the unusual vibration but there were no imminent signs of system failure. A strong smell of alloy dust was present. The motor was shut down for a brief span for a quick checkup but the problem continued after restart. S5.OP-AB.CW-0005 Pump Irregularity was initiated. * * 2) ACTIVITIES, PROCESSES, PROCEDURES INVOLVED: * S5.OP.AB-CW-0005, S5.OP-SO.CW-0018 * * 3) WHY DID CONDITION HAPPEN: * Not confirmed. Could be a bearing issue or an internal misalignment. * * 4) CONSEQUENCES: * Failure or reduced efficiency of the pump. May lead to stressed operational parameters. A sudden failure might lead to unscheduled shutdown. * * 5) REQUIREMENTS IMPACTED: * Pump stability and reliability. * * 6) ADVERSE PHYSICAL CONDITION: * Vibrations from 18A Pump motor, potential internal damage * * 7) WHO WAS NOTIFIED: * Site Supervisor, Engineering Department * * 8) KNOWLEDGEABLE INDIVIDUALS: * Carter, Baldwin, Snow * * 9) REPEAT OR SIMILAR CONDITION: * Yes, previous condition identified caused by misalignment * * 10) IMMEDIATE AND RECOMMENDED ACTIONS: * Conduct thorough investigation on 18A Pump Motor and rectify issues ASAP. * * Updated: GEORGE TURNER 02.18.2017 | What immediate and recommended actions were suggested in response to the unusual vibration coming from the 18A Pump motor? | Conduct thorough investigation on 18A Pump Motor and rectify issues ASAP.
173 | 2018-02-09 | 30780258 | 90211217 | Leakage from cooling system 53B | S4CW -4CWE5 | * **************Incident Description************** * Notification 000030780258 Details * *********************************************************** * 02/09/2018 06:25:00 INCIDENT REPORT (INCIDENT REPORT) * Report submitted by: David Martin ENTITY\INCIDENT: * * CONDITION DESCRIPTION/LOCATION (THE INAPPROPRIATE ACTION AND ITS NEGATIVE EFFECT/INCLUDE A DETAILED LOCATION DESCRIPTION): * At 0625 on 2/9/18 during standard morning check, a dripping sound was heard from the engine room. Upon investigation, a slow leakage was identified from the cooling system 53B. The leak detection panel indicated a minor coolant leak. The issue was promptly reported to the control room and the necessary actions were initiated. * * ACTIVITIES, PROCESSES, PROCEDURES INVOLVED: * Normal morning check, Leak detection, S4.OP-AB.CW-0009 - Leak check * * WHY DID CONDITION HAPPEN? * Preliminary investigation suggests that the pump seal may have been damaged or have worn out. * * CONSEQUENCES: * Potential drip could lead to a cooling system failure if not addressed promptly. * * REQUIREMENTS IMPACTED: * Normal operation, Immediate repair required * * ADVERSE PHYSICAL CONDITIONS: * Slow leak from the cooling system 53B, drop in coolant level * * WHO WAS NOTIFIED: * Control Room, Emergency Response Team, Chief Engineer * * KNOWLEDGEABLE INDIVIDUALS: * Johnson, Lee, Martinez * * REPEAT OR SIMILAR CONDITION: * No prior records of leak from cooling system 53B * * IMMEDIATE ACTIONS AND RECOMMENDED ACTIONS: * Isolate the pump and carry out a thorough inspection. Replace the seal if it is found to be defective. * 02/09/2018 14:36:20 DAVID MARTIN (INCIDENT) * The pump has been isolated and is currently awaiting inspection. A deep-dive investigation will be carried out to prevent similar incidents in future. | What immediate actions were recommended after identifying the coolant leak in the cooling system 53B? | Isolate the pump and carry out a thorough inspection. Replace the seal if it is found to be defective.
174 | 2019-05-25 | 30972202 | 90082734 | Overheating in 16B Pump | S4CW -4CWE7 | * **************Incident Description************** * Notification 000030972202 Details * *********************************************************** * 05/25/2019 15:32:00 INCIDENT REPORT (INCIDENT REPORT) * Report submitted by: Robert Williams ENTITY\INCIDENT: * * CONDITION DESCRIPTION/LOCATION (THE INAPPROPRIATE ACTION AND ITS NEGATIVE EFFECT/INCLUDE A DETAILED LOCATION DESCRIPTION): * At 1512 on 5/25/19, Pump 16B was found to be running hot during routine monitoring. The temperature increase was identified through temperature sensors installed on the pump. Fire Department and Operations inspection confirmed no fire, but a burnt smell suggested possible internal damage. The pump was immediately shut down to prevent further damage. There were no external signs of damage. * * ACTIVITIES, PROCESSES, PROCEDURES INVOLVED: * S4.OP-AB.PP-0007, Routine monitoring and pump running process * * WHY DID CONDITION HAPPEN: * The cause is yet unknown. Previous instances with similar pumps suggest possible obstruction within the pump. * * CONSEQUENCES: * Potential risk of motor breakdown and subsequent decrease in unit efficiency * * REQUIREMENTS IMPACTED: * Pump operations * * ADVERSE PHYSICAL CONDITIONS: * Overheating in 16B Pump, risk of internal damage * * WHO WAS NOTIFIED: * Control Room, Maintenance team, Fire Department * * KNOWLEDGEABLE INDIVIDUALS: * Roberts, Anderson, Clark * * REPEAT OR SIMILAR CONDITION: * Yes. This is a recurring issue with similar pumps. * * IMMEDIATE ACTIONS AND RECOMMENDED ACTIONS: * Operations and maintenance teams to investigate 16B Pump. * Engineering to review issues related to similar reports and recommend appropriate actions. * Updated: ROBERT WILLIAMS 25.05.2019 17:20:00 * 29/05/2019 15:22:52 LISA PERRY (MAINTENANCE) * The maintenance team inspected the pump and found a buildup of sediment causing the obstruction and subsequent overheating. The pump has been | What was the cause of the overheating in pump 16B and how was it identified? | The maintenance team inspected the pump and found a buildup of sediment causing the obstruction and subsequent overheating.
175 | 2021-10-22 | 31044072 | 90234597 | Oil leakage from pump P-13A | S4OL -4OLE1 | * **************Incident Description************** * Notification 000031044072 Details * *********************************************************** * 10/22/2021 07:29:50 INCIDENT REPORT (INCIDENT REPORT) * Report submitted by: Emma King ENTITY\INCIDENT: * * CONDITION DESCRIPTION/LOCATION (THE INAPPROPRIATE ACTION AND ITS NEGATIVE EFFECT/INCLUDE A DETAILED LOCATION DESCRIPTION): * During a routine inspection, oil leakage was observed from pump P-13A. The oil pressure was recorded at 10 psi, which is noticeably lower than other pumps in the same service. A puddle of oil has formed under the pump assembly. Because of the visible oil leakage and lower pressure, the Equipment Integrity Team was instantly alerted. * * ACTIVITIES, PROCESSES, PROCEDURES INVOLVED: * Routine equipment inspection. * * WHY DID CONDITION HAPPEN? * Preliminary investigations suggest possible failure of pump seal. However, the accurate cause has yet to be identified. * * CONSEQUENCES: * Oil leaks may lead to equipment failure, environmental and fire safety hazards. * * REQUIREMENTS IMPACTED: * Pump operation and maintenance, environmental obligations. * * ADVERSE PHYSICAL CONDITIONS: * Oil leakage from Pump P-13A. * * WHO WAS NOTIFIED: * Equipment Integrity Team, Safety Team * * KNOWLEDGEABLE INDIVIDUALS: * Equipment Integrity Team, Operations Lead. * * REPEAT OR SIMILAR CONDITION: * Not known at this stage. * * IMMEDIATE ACTIONS AND RECOMMENDED ACTIONS: * Stop the pump, clean the oil spill, and mobilize the Pump Maintenance Team for immediate pump seal replacement and inspection. * 10/24/2021 14:12:48 EMMA KING (INCIDENT) * Pump P-13A has been taken offline for seal replacement, following the successful deployment of alternative pumping arrangements to maintain operation continuity. | What immediate actions were recommended after the oil leakage was discovered? | Stop the pump, clean the oil spill, and mobilize the Pump Maintenance Team for immediate pump seal replacement and inspection.
176 | 2017-01-22 | 40830721 | 90126975 | 13B Motor experienced vibration Post Servicing | S4CW -3CWE4 | * **************Incident Description************** * Notification 000040830721 Details * *********************************************************** * 01/22/2017 16:50:47 INCIDENT REPORT (INCIDENT REPORT) * Report submitted by: Sarah Williams ENTITY\INCIDENT: * * CONDITION DESCRIPTION/LOCATION (THE INAPPROPRIATE ACTION AND ITS NEGATIVE EFFECT/INCLUDE A DETAILED LOCATION DESCRIPTION): * After servicing, the 13B motor was noticed to have abnormal vibration during operation. This incident was reported at 1640 hours from Control Room 3. Initial inspection did not reveal any external mechanical damage. Further testing showed that the motor vibrations were higher than other similar units. Procedure S4.OP-SO.CW-0002 was initiated to investigate the abnormality. * * ACTIVITIES, PROCESSES, PROCEDURES INVOLVED: * Vibration Testing, S4.OP-SO.CW-0002 * * WHY DID CONDITION HAPPEN? * Potential incorrect re-installation or inherent defect, requires further investigation. * * CONSEQUENCES: * Increased wear and tear, potential motor damage if untreated, can affect the operation efficiency. * * REQUIREMENTS IMPACTED: * Normal operation of the 13B pump motor. * * ADVERSE PHYSICAL CONDITIONS: * High vibration levels at the pump motor. * * WHO WAS NOTIFIED: * Operations Supervisor, Maintenance Team * * KNOWLEDGEABLE INDIVIDUALS: * Sarah Williams, Operational Team, Maintenance Team. * * REPEAT OR SIMILAR CONDITION: * No, this is the first occurrence. * * IMMEDIATE ACTIONS AND RECOMMENDED ACTIONS: * Isolation and deeper investigation of the motor is recommended. The operational parameters need to be verified and adjustments should be made to correct the vibration issue. * 01/23/2017 11:05:24 NEIL ADAMS (MAINTENANCE TEAM) * We checked the installation and found that there was misalignment in the drive chain during the servicing. After realignment and testing, the vibration returned to normal parameters. Further monitoring is recommended to ensure stable operation. | What was discovered during the investigation of the abnormal vibration in the 13B motor after servicing? | We checked the installation and found that there was misalignment in the drive chain during the servicing. After realignment and testing, the vibration returned to normal parameters. Further monitoring is recommended to ensure stable operation.
177 | 2017-05-31 | 30786532 | 80642108 | 34B pump having low pressure issues | S4CW -4CWE8 | * **************Incident Description************** * Notification 000030786532 Details * *********************************************************** * 05/31/2017 14:15:48 INCIDENT REPORT (INCIDENT REPORT) * Report submitted by: Bob Taylor ENTITY\INCIDENT: * * CONDITION DESCRIPTION/LOCATION (THE INAPPROPRIATE ACTION AND ITS NEGATIVE EFFECT/INCLUDE A DETAILED LOCATION DESCRIPTION): * During a regular operation, an issue was discovered with the 34B pump exhibiting lower than normal pressure. Normal operation requires pressure at 15 psig and the current measurement was 9 psig. The pump wasn't making any unusual noise or responding to manual pressure adjustment. * * ACTIVITIES, PROCESSES, PROCEDURES INVOLVED: * S4.OP-IP.CW-0004, S4.OP-AB.CW-0031 * * WHY DID CONDITION HAPPEN? * At first glace, the condition seems inexplicable. A leak test will be required to ascertain the root cause. * * CONSEQUENCES: * Impending loss of pump function, decreased system efficiency. * * REQUIREMENTS IMPACTED: * Normal operating conditions. Potential disruption of service. * * ADVERSE PHYSICAL CONDITIONS: * Low pressure at 34B pump with no evident cause. * * WHO WAS NOTIFIED: * Supervisor, Engineering Team * * KNOWLEDGEABLE INDIVIDUALS: * Engineering Team, Bob Taylor * * REPEAT OR SIMILAR CONDITION: * No known repeat or similar condition. * * IMMEDIATE ACTIONS AND RECOMMENDED ACTIONS: * Perform leak test, investigate further if necessary. If the issue persists, pump replacement may be considered. * 05/31/2017 16:27:24 BOB TAYLOR (INCIDENT) * Leak test performed, results indicate minor internal leak. Shall schedule further investigation and possible repair. | What was the identified issue with the 34B pump during the regular operation? | During a regular operation, an issue was discovered with the 34B pump exhibiting lower than normal pressure. Normal operation requires pressure at 15 psig and the current measurement was 9 psig. The pump wasn't making any unusual noise or responding to manual pressure adjustment.
178 | 2018-02-11 | 30935614 | 80241532 | Intermittent failure of 14B Pump | S3CW -3CWE5 | * **************Incident Description************** * Notification 000030935614 Details * *********************************************************** * 02/11/2018 10:21:00 INCIDENT REPORT (INCIDENT REPORT) * Report submitted by: David Hilson ENTITY\INCIDENT: * * CONDITION DESCRIPTION/LOCATION (THE INAPPROPRIATE ACTION AND ITS NEGATIVE EFFECT/INCLUDE A DETAILED LOCATION DESCRIPTION): * The operator reported that 14B Pump has been experiencing intermittent failures during its operation. This is not a normal characteristic of 14B Pump. Further inspection revealed that the pump is operating outside of its design parameters. The potential cause of the intermittent failure could be clogged filters or worn out components. * * ACTIVITIES, PROCESSES, PROCEDURES INVOLVED: * Routine operation checks, S3.OP-AB.CW-0002, S3.OP-SO.CW-0002 * * WHY DID CONDITION HAPPEN? * Unclear at this point, possibly due to clogged filters or aging components. * * CONSEQUENCES: * Potential for complete pump failure. Also, abnormal operating parameters may impact efficiency or cause additional wear. * * REQUIREMENTS IMPACTED: * Normal operation, maintenance schedules * * ADVERSE PHYSICAL CONDITIONS: * Intermittent Pump Failure * * WHO WAS NOTIFIED: * Supervisor, Maintenance, Operations * * KNOWLEDGEABLE INDIVIDUALS: * Operations Team, Maintenance, David Hilson * * REPEAT OR SIMILAR CONDITION: * No, this is the first occurrence of such incident. * * IMMEDIATE ACTIONS AND RECOMMENDED ACTIONS: * Need an Inspection of the pump including filters, seals, and bearings. Maintenance to address the identified issues and operational parameter deviations. * * 02/15/2018 14:58:34 DAVID HILSON (INCIDENT) * Maintenance has been completed. The issue was related to worn out components. All the worn out components are now replaced and 14B pump is operating within normal parameters. Further checks to be conducted to ensure the issue does not recur. | What immediate actions were recommended to address the intermittent failure of the 14B Pump? | Need an Inspection of the pump including filters, seals, and bearings. Maintenance to address the identified issues and operational parameter deviations.
179 | 2019-06-07 | 40930455 | 90130255 | Abnormal vibration from Condenser 2X | S4CW -4CWE10 | * **************Incident Description************** * Notification 000040930455 Details * *********************************************************** * 06/07/2019 16:02:00 INCIDENT REPORT (INCIDENT REPORT) * Report submitted by: Robert Green ENTITY\INCIDENT: * * CONDITION DESCRIPTION/LOCATION (THE INAPPROPRIATE ACTION AND ITS NEGATIVE EFFECT/INCLUDE A DETAILED LOCATION DESCRIPTION): * During routine inspection, abnormal vibration was noted from Condenser 2X. The imbalance was noticeable, and a comparison with records showed a significant departure from the unit's normal operation parameters. The condenser was not showing any visible signs of damage but the vibration was higher than the normal levels. * * ACTIVITIES, PROCESSES, PROCEDURES INVOLVED: * Regular inspection and review of visual and auditory abnormality of Condenser 2X. * * WHY DID CONDITION HAPPEN? * At this stage, the cause of the vibrations is unknown. Potential causes could be loss of balance in the condenser motor or possible internal damage. * * CONSEQUENCES: * Prolonged operation in this condition could lead to severe damage to the unit, leading to a failure which could impact overall system performance. * * REQUIREMENTS IMPACTED: * Operational stability and efficiency of the condenser unit. * * ADVERSE PHYSICAL CONDITION: * Excessive vibration in the Condenser 2X, potential of internal damage * * WHO WAS NOTIFIED: * Maintenance Team, Supervisor * * KNOWLEDGEABLE INDIVIDUALS: * Robert Green, Jason Taylor, Sarah Miller * * REPEAT OR SIMILAR CONDITION: * This is the first noted occurrence of such a condition. * * IMMEDIATE ACTIONS AND RECOMMENDED ACTIONS: * The Condenser 2X should be shut down for an immediate inspection to determine the cause of the vibrations and address them appropriately. * 06/08/2019 11:01:16 ROBERT GREEN (INCIDENT) * Fear of internal damage necessitated an inspection. The imbalance was caused due to a misalignment in the motor shaft. Realignment was carried out, vibration | What immediate action was recommended to address the abnormal vibrations in the condenser unit? | The Condenser 2X should be shut down for an immediate inspection to determine the cause of the vibrations and address them appropriately.
180 | 2018-10-30 | 30762409 | 80246310 | Strange Vibration from 19F Compressor | S4CW -4CWE2 | * **************Incident Description************** * Notification 000030762409 Details * *********************************************************** * 10/30/2018 16:12:00 INCIDENT REPORT (INCIDENT REPORT) * Report submitted by: Laura White ENTITY\INCIDENT: * * CONDITION DESCRIPTION/LOCATION (THE INAPPROPRIATE ACTION AND ITS NEGATIVE EFFECT/INCLUDE A DETAILED LOCATION DESCRIPTION): * During regular monitoring, unexpected vibrations were detected on the 19F compressor. Initial diagnostics indicated a potentially misaligned rotor, which could potentially lead to premature failure and unit downtime. Immediate action was taken to shut down unit pending further investigation. * * ACTIVITIES, PROCESSES, PROCEDURES INVOLVED: * Regular monitoring, vibration analysis, compressor shutdown * * WHY DID CONDITION HAPPEN? * Potential misalignment during previous maintenance activity. * * CONSEQUENCES: * Premature failure and unit shutdown if not addressed promptly. * * REQUIREMENTS IMPACTED: * Plant availability and reliability * * ADVERSE PHYSICAL CONDITIONS: * Unexpected vibration from the 19F Compressor * * WHO WAS NOTIFIED: * Plant Supervisor, Maintenance Team * * KNOWLEDGEABLE INDIVIDUALS: * Laura White, Plant Supervisor, Maintenance Team * * REPEAT OR SIMILAR CONDITION: * No, this is the first occurrence on this unit. * * IMMEDIATE ACTIONS AND RECOMMENDED ACTIONS: * Immediate shutdown of 19F Compressor for further diagnostic and potential corrective maintenance. If misalignment is confirmed, review and revise maintenance procedures to prevent recurrence. * 10/31/2018 13:09:00 LAURA WHITE (INCIDENT) * Malfunction was confirmed to be a misalignment during routine maintenance. The unit was re-aligned, tested and returned to service. Revised maintenance procedures to include additional checks for alignment. | What immediate actions were taken following the detection of unexpected vibrations from the 19F Compressor? | Immediate shutdown of 19F Compressor for further diagnostic and potential corrective maintenance. If misalignment is confirmed, review and revise maintenance procedures to prevent recurrence.
181 | 2018-02-15 | 30835420 | 80265937 | Cooling fan malfunction at station 6 | S6VQ -6VQB2-FLR6 | * **************Incident Description************** * Notification 000030835420 Details * *********************************************************** * 02/15/2018 14:14:28 INCIDENT REPORT (INCIDENT REPORT) * Report submitted by: David Thompson ENTITY\INCIDENT: * * CONDITION DESCRIPTION/LOCATION (THE INAPPROPRIATE ACTION AND ITS NEGATIVE EFFECT/INCLUDE A DETAILED LOCATION DESCRIPTION): * During a scheduled station visit, a loud whirring noise was heard from the cooling fan at station 6. Upon inspection, it was discovered that the fan was running at a speed higher than normal, posing a risk of overheating or causing potential mechanical damage to the fan. * * ACTIVITIES, PROCESSES, PROCEDURES INVOLVED: * Scheduled station visit, regular preventive maintenance * * WHY DID CONDITION HAPPEN? * Probably due to a fault in the fan speed control system. Previous incidents in other stations hint at this problem. * * CONSEQUENCES: * Potential damage to the cooling fan, leading to overheating of station equipment, reduction in efficiency and increase in maintenance costs. * * REQUIREMENTS IMPACTED: * Maintaining proper station temperature. * * ADVERSE PHYSICAL CONDITIONS: * Greater noise level from the cooling fan, risk of the fan overheating. * * WHO WAS NOTIFIED: * Maintenance Supervisor, Station Manager. * * KNOWLEDGEABLE INDIVIDUALS: * Maintenance Team * * REPEAT OR SIMILAR CONDITION: * Yes, similar incidents have occurred in different stations. * * IMMEDIATE ACTIONS AND RECOMMENDED ACTIONS: * The faulty cooling fan needs to be examined immediately and repaired or replaced if necessary. The fan speed control system must also be checked to prevent similar incidents in the future. * 02/15/2018 16:49:45 DAVID THOMPSON (INCIDENT) * The cooling fan at station 6 has been examined. The fan speed has been adjusted back to normal. A fault was detected in the speed control system and has been rectified. Monitoring will continue to ensure the problem does not recur. | What immediate actions were taken after the cooling fan incident was discovered at station 6? | The cooling fan at station 6 has been examined. The fan speed has been adjusted back to normal. A fault was detected in the speed control system and has been rectified. Monitoring will continue to ensure the problem does not recur.
182 | 2019-12-12 | 30991345 | 90876234 | OVERHEATING OF CONDENSER PUMP 23B | S4CW -4CWE4 | * **************Incident Description************** * Notification 000030991345 Details * *********************************************************** * 12/12/2019 14:04:02 INCIDENT REPORT (INCIDENT REPORT) * Report submitted by: Thomas Clark ENTITY\INCIDENT: * * CONDITION DESCRIPTION/LOCATION (THE INAPPROPRIATE ACTION AND ITS NEGATIVE EFFECT/INCLUDE A DETAILED LOCATION DESCRIPTION): * At 1432 on 12/12/19, the technician reported an unusual level of heat from the condenser pump 23B. The pump was immediately shut down from Unit 4 Control Room and the heat subsided. Safety Department and Operations inspection did not reveal any fire, however, an odor of overheated components was noticeable. Pump operating temperatures appeared similar to others in operation, however, a faint hissing sound was noted. S4.OP-SO.TE-0009 Pump Abnormality had been initiated due to emergency shut down of 23B Pump. * * ACTIVITIES, PROCESSES, PROCEDURES INVOLVED: * S4.OP-SO.TE-0009, S4.OP-AB.TE-0001 * * WHY DID CONDITION HAPPEN: * Unsure at the moment, although similar overheating issues have been reported previously. * * CONSEQUENCES: * Immediate effect negated by pump shut down, but potential internal damage could result in decreased efficiency when the unit is revived. * * REQUIREMENTS IMPACTED: * Offline pump, possibly impaired operation * * ADVERSE PHYSICAL CONDITION: * Overheating of 23B Pump motor, suspected internal damage. * * WHO WAS NOTIFIED: * Control Room, Safety Department * * KNOWLEDGEABLE INDIVIDUALS: * Richardson, Grey, Adams * * REPEAT OR SIMILAR CONDITION: * Yes, similar conditions have occurred. * * IMMEDIATE AND RECOMMENDED ACTIONS: * Maintenance team to diagnose 23B Pump Motor * * Updated: THOMAS CLARK 12.12.2019 17:53:21 * ------------------------------------------------------------ * 12/19/ | What was the immediate action taken when the unusual heat level was reported from the condenser pump 23B? | The pump was immediately shut down from Unit 4 Control Room and the heat subsided.
183 | 2018-09-05 | 30789045 | 90123456 | Abnormal temperature at 17B Pump | S3CW -3CWE7 | * **************Incident Description************** * Notification 000030789045 Details * *********************************************************** * 09/05/2018 08:30:20 INCIDENT REPORT (INCIDENT REPORT) * Report submitted by: David White ENTITY\INCIDENT: * * CONDITION DESCRIPTION/LOCATION (THE INAPPROPRIATE ACTION AND ITS NEGATIVE EFFECT/INCLUDE A DETAILED LOCATION DESCRIPTION): * At routine check, it was noted that the 17B Pump was showing higher than normal operating temperature. The indication occurred in Unit 3 Control Room. Immediate shut down of the 17B pump and cooling procedure was carried out accordingly. Upon inspection by maintenance team, no external damage was observed. * * ACTIVITIES, PROCESSES, PROCEDURES INVOLVED: * Regular monitoring, S3.OP-AB.CW-0005, and S3.OP-SO.CW-0005 * * WHY DID CONDITION HAPPEN? * The exact cause is yet to be determined. Previous incidents of temperature increase have been linked to internal wear or blockage in the cooling channels. * * CONSEQUENCES: * Potential decrease in pump efficiency and risk of major failure if not addressed promptly. * * REQUIREMENTS IMPACTED: * Scheduled operation of the 17B pump * * ADVERSE PHYSICAL CONDITIONS: * High operational temperature of 17B pump * * WHO WAS NOTIFIED: * Control Room, Maintenance team * * KNOWLEDGEABLE INDIVIDUALS: * Clark, Benson, Green * * REPEAT OR SIMILAR CONDITION: * No previous incidents recorded for the 17B pump, but similar issues have occurred with other pumps. * * IMMEDIATE ACTIONS AND RECOMMENDED ACTIONS: * Conduct system check and maintenance scheduled for overhaul and inspection. * 09/05/2018 12:53:57 DAVID WHITE (INCIDENT) * The maintenance team has assessed the pump and is taking the necessary actions. After the maintenance is completed, the pump will be closely monitored for any further temperature variations. | What were the immediate actions taken following the high temperature incident with the 17B pump? | Immediate shut down of the 17B pump and cooling procedure was carried out accordingly. Upon inspection by maintenance team, no external damage was observed.
184 | 2022-06-11 | 309830418 | 80456732 | Unusual vibration from 25C CW Pump | S5CW -5CWE2 | * **************Incident Description**************** * Notification 0000309830418 Details * ************************************************************ * 06/11/2022 14:26:03 INCIDENT REPORT (INCIDENT REPORT) * Report submitted by: Max Richards 555-321-0987 ENTITY\INCIDENT: * * CONDITION DESCRIPTION/LOCATION (THE INAPPROPRIATE ACTION AND ITS NEGATIVE EFFECT/INCLUDE A DETAILED DESCRIPTION LOCATION): * While doing a routine check, operator detected unusual vibrations from the 25C Pump. Accelerometers confirmed the anomaly. All other parameters including temperature, pressure and flow were normal. Previous records do not show any such vibration from this pump. * * ACTIVITIES, PROCESSES, PROCEDURES INVOLVED: * Routine check and vibration monitoring, S5.OP-SO.CW-0003 * * WHY DID CONDITION HAPPEN? * Unknown, possible bearing failure or imbalance. * * CONSEQUENCES: * Potential failure of pump, disrupted operation. * * REQUIREMENTS IMPACTED: * Normal operation, vibration limits * * ADVERSE PHYSICAL CONDITIONS: * Elevated vibration detected at 25C Pump * * WHO WAS NOTIFIED: * Supervisor/ INCIDENT TEAM * * KNOWLEDGEABLE INDIVIDUALS: * Incident Team, Supervisors, Maintenance Department * * REPEAT OR SIMILAR CONDITION: * No, first occurrence * * IMMEDIATE ACTIONS AND RECOMMENDED ACTIONS: * Reduce pump operation to minimum safe level, notify maintenance for detailed inspection and necessary action. * 06/11/2022 18:07:10 MAX RICHARDS (INCIDENT) * The maintenance team has been alerted and they are planning an inspection in the next maintenance window. Considering the emergency, sooner action may be required. | What was the anomaly detected in the routine check of the 25C Pump? | Operator detected unusual vibrations from the 25C Pump.
185 | 2018-09-29 | 30943560 | 80234507 | 30B Pump Motor Vibration | S4CW -4CWE4 | * **************Incident Description************** * Notification 000030943560 Details * *********************************************************** * 09/29/2018 14:35:12 INCIDENT REPORT (INCIDENT REPORT) * Report submitted by: Emma Johnson ENTITY\INCIDENT: * * CONDITION DESCRIPTION/LOCATION (THE INAPPROPRIATE ACTION AND ITS NEGATIVE EFFECT/INCLUDE A DETAILED LOCATION DESCRIPTION): * While performing routine inspections, abnormal vibration was detected in the 30B Pump Motor. The pump was running at an output pressure of 45 PSI with an input current of 400A. The ambient temperature was about 35°C. The vibration was also confirmed by visual observation and the corresponding sound. The lack of any recent maintenance record suggests a possible mechanical issue. * * ACTIVITIES, PROCESSES, PROCEDURES INVOLVED: * Routine inspection and measurements, * S4.OP-AB.CW-0002 Pump Vibration Detection and Management * * WHY DID CONDITION HAPPEN? * It's unclear at this time. Potential reasons could be misalignment, bearing defects, or mechanical looseness. The pump’s maintenance history does not suggest any similar past occurrences. * * CONSEQUENCES: * On-going operation with excessive vibration can lead to catastrophic failures and necessary pump replacement. An unexpected pump failure could lead to system inefficiencies and safety issues. * * REQUIREMENTS IMPACTED: * Continuous operation. * * ADVERSE PHYSICAL CONDITIONS: * Excessive vibration and noise at the 30B pump. * * WHO WAS NOTIFIED: * Control Room, Maintenance Team * * KNOWLEDGEABLE INDIVIDUALS: * Wilson, Thomas, Olivia * * REPEAT OR SIMILAR CONDITION: * No previous condition reported * * IMMEDIATE ACTIONS AND RECOMMENDED ACTIONS: * Recommend immediate shut down of 30B pump and scheduling thorough diagnostics and maintenance. * 09/29/2018 17:10:28 EMMA JOHNSON (INCIDENT) * The maintenance team is allocated to investigate and the pump is now out of service till further actions are taken. | What immediate actions were recommended following the detection of abnormal vibration in the 30B Pump Motor? | Recommend immediate shut down of 30B pump and scheduling thorough diagnostics and maintenance.
186 | 2020-03-10 | 30962842 | 80527860 | Unexpected vibration from 5B Pump | S4CW -4CWE2 | * **************Incident Description************** * Notification 000030962842 Details * *********************************************************** * 03/10/2020 13:51:37 INCIDENT REPORT (INCIDENT REPORT) * Report submitted by: Emily Green 975-842-1011 ENTITY\INCIDENT: * CONDITION DESCRIPTION/LOCATION (THE INAPPROPRIATE ACTION AND ITS NEGATIVE EFFECT/INCLUDE A DETAILED LOCATION DESCRIPTION): * Noticed unexpected vibration from the 5B pump during routine check. The severity of the vibration decreased when the speed was reduced. No noise or temperature increase was observed. All other parameters such as caviation, impeller clearance seemed normal, suggesting this could be a sign of possible impending failures of the motor or the pump. * * ACTIVITIES, PROCESSES, PROCEDURES INVOLVED: * Regular Monitoring, SOP-S4.CW-0001 * WHY DID CONDITION HAPPEN? * Uncertain, possibly wear and tear or imbalance in the rotor. * * CONSEQUENCES: * It may cause equipment failure or reduced efficiency. * * REQUIREMENTS IMPACTED: * Regular operation, potential pump shutdown. * * ADVERSE PHYSICAL CONDITION: * Significant vibration observed in 5B pump * * WHO WAS NOTIFIED: * Maintenance team/ Supervisor * * KNOWLEDGEABLE INDIVIDUALS: * Henry, Johnson, Daniel * * REPEAT OR SIMILAR CONDITION: * No * * IMMEDIATE ACTIONS AND RECOMMENDED ACTIONS: * Perform detailed inspection to identify the root cause of the vibration, possibly perform vibration analysis and balance the rotors if needed. If the issue persists, replace the pump before it leads to more severe problems. * 03/12/2020 10:29:47 EMILY GREEN (INCIDENT) * Vibration analysis is ongoing. Soon we will be able to identify the cause of increased vibration. | What immediate action was recommended upon noticing the unexpected vibration in the 5B pump? | Perform detailed inspection to identify the root cause of the vibration, possibly perform vibration analysis and balance the rotors if needed. If the issue persists, replace the pump before it leads to more severe problems.
187 | 2019-12-10 | 40105097 | 90518912 | Unexpected coolant leaks in B4 Pump | S5RF -5RFE2-LKD | * **************Incident Description************** * Notification 000040105097 Details * *********************************************************** * 12/10/2019 08:18:37 INCIDENT REPORT (INCIDENT REPORT) * Report submitted by: Daniel Ford ENTITY\INCIDENT: * * CONDITION DESCRIPTION/LOCATION (THE INAPPROPRIATE ACTION AND ITS NEGATIVE EFFECT/INCLUDE A DETAILED LOCATION DESCRIPTION): * At 0800 on 12/10/19, during the routine inspection, the B4 pump expressed unexpected coolant leakage. The leakage was significant, causing the pump function to slow down. Immediate shut down was executed from the Main Control Room to avoid any further spillage. Emergency assistance was called in. Initial Check revealed no external damage. * * ACTIVITIES, PROCESSES, PROCEDURES INVOLVED: * Routine inspection and emergency shutdown protocol S5.OP-AB.RF-0005, S5.OP-SO.RF-0004 * * WHY DID CONDITION HAPPEN? * Initial hypothesis suggests the gasket failure, but the exact cause is currently unknown. There were instances of similar events in the past. * * CONSEQUENCES: * A potential risk of pump damage, loss of coolant could lead to overheating. * * REQUIREMENTS IMPACTED: * Pump operation was momentarily halted affecting the regular schedule. * * ADVERSE PHYSICAL CONDITIONS: * Coolant leaks from B4 pump, possible internal damage due to gasket failure. * * WHO WAS NOTIFIED: * Control Room, Immediate Response Team * * KNOWLEDGEABLE INDIVIDUALS: * Graham, Martinez, Peterson * * REPEAT OR SIMILAR CONDITION: * Yes, there were few events with different pumps in the past. * * IMMEDIATE ACTIONS AND RECOMMENDED ACTIONS: * Immediate replacement of gasket and inspection of B4 Pump is in process. * * Updated: DANIEL FORD 12.10.2019 12:30:21 * ----------------------------------------------------------- * 12/20/2019 09:37:11 STEVE SMITH (ENGINEER) * Issue originated from failure of gasket. The | What immediate actions were taken following the coolant leakage from the B4 pump? | Immediate replacement of gasket and inspection of B4 Pump is in process.
188 | 2018-10-07 | 30987654 | 80541239 | 34B Pump abrupt vibration | S4CW -4CWE7 | * **************Incident Description************** * Notification 000030987654 Details * *********************************************************** * 10/07/2018 11:11:00 INCIDENT REPORT (INCIDENT REPORT) * Report submitted by: Jack Martin ENTITY\INCIDENT: * * CONDITION DESCRIPTION/LOCATION (THE INAPPROPRIATE ACTION AND ITS NEGATIVE EFFECT/INCLUDE A DETAILED LOCATION DESCRIPTION): * While conducting the standard inspection, the operator experienced sudden high vibration in the 34B Pump Unit 4. The pump was shut down immediately, to avoid damage. There are no previous records of similar vibration issues in this unit. The cause is undetermined at this time, but initial checks suggest a mechanical issue. * * ACTIVITIES, PROCESSES, PROCEDURES INVOLVED: * Regular inspection protocol - Routine Check * * WHY DID CONDITION HAPPEN? * Uncertain at this point. A mechanical malfunction is suspected. * * CONSEQUENCES: * Potential severe damage to the pump if ignored, affecting the efficiency and operation. * * REQUIREMENTS IMPACTED: * Availability of 34B pump until resolved. * * ADVERSE PHYSICAL CONDITIONS: * High pump vibration * * WHO WAS NOTIFIED: * Maintenance Department, Operations Supervisor * * KNOWLEDGEABLE INDIVIDUALS: * Maintenance Department, Operations Manager, Expert operators * * REPEAT OR SIMILAR CONDITION: * No * * IMMEDIATE ACTIONS AND RECOMMENDED ACTIONS: * Initiate detailed analysis & investigation of 34B Pump Unit 4. Check for both mechanical and electrical aspects of the system. * 10/08/2018 16:52:12 JACK MARTIN (INCIDENT) * The inspection identified a misalignment issue caused by recent maintenance. Alignments have been re-adjusted and the vibration issue is resolved. The system is back online. | What was the immediate action taken in response to the high vibration in the 34B Pump Unit 4? | The pump was shut down immediately, to avoid damage.
189 | 2019-01-10 | 30755123 | 80455540 | 30B Pump Leakage | S3CW -3CVE7-PMPD | * **************Incident Description************** * Notification 000030755123 Details * *********************************************************** * 01/10/2019 11:15:26 INCIDENT REPORT (INCIDENT REPORT) * Report submitted by: Emily Black 999-888-7777 ENTITY\INCIDENT: * CONDITION DESCRIPTION/LOCATION (THE INAPPROPRIATE ACTION AND ITS NEGATIVE EFFECT/INCLUDE A DETAILED LOCATION DESCRIPTION): * After annual maintenance, the 30B Pump had visible leakage. The leakage was small but consistent, indicating a potential issue with the seals or pressure relief valve. * * ACTIVITIES, PROCESSES, PROCEDURES INVOLVED: * Post-maintenance start-up checks * * WHY DID CONDITION HAPPEN? * Unknown, the seals were replaced during maintenance. Possible cause could be improper installation or faulty new parts. * * CONSEQUENCES: * Possible increased wear on the pump, potential for larger leak leading to operational disruptions. * * REQUIREMENTS IMPACTED: * Possible disruptions to normal operations * * ADVERSE PHYSICAL CONDITIONS: * Ongoing leakage from 30B pump * * WHO WAS NOTIFIED: * Supervisor, Maintenance Team * * KNOWLEDGEABLE INDIVIDUALS: * Emily Black, Supervisor, Maintenance Team * * REPEAT OR SIMILAR CONDITION: * No * * IMMEDIATE ACTIONS AND RECOMMENDED ACTIONS: * Revisit maintenance done on 30B pump, particularly focusing on the seals and pressure relief valve. Monitor the pump closely for any changes. * 01/10/2019 13:47:12 EMILY BLACK (INCIDENT) * The maintenance team was called back to check the pump. They are investigating the seals and pressure relief valve as potential sources of the leak. | What immediate actions were recommended after the incident involving the 30B pump leakage? | Revisit maintenance done on 30B pump, particularly focusing on the seals and pressure relief valve. Monitor the pump closely for any changes.
190 | 2020-10-12 | 40975310 | 90120977 | 9C Pump Failure | S6TR -6TRE2 | * **************Incident Description************** * Notification 000040975310 Details * *********************************************************** * 10/12/2020 15:33:40 INCIDENT REPORT (INCIDENT REPORT) * Report submitted by: Amelia Watson * ENTITY\INCIDENT: * * CONDITION DESCRIPTION/LOCATION (THE INAPPROPRIATE ACTION AND ITS NEGATIVE EFFECT/INCLUDE A DETAILED LOCATION DESCRIPTION): * On 10/12/20, during a routine operation, the 9C pump unexpectedly failed. There were no immediate signs of external damage, but the pump was not responsive and had to be isolated from the system. The potential cause and effects are still under investigation. * * ACTIVITIES, PROCESSES, PROCEDURES INVOLVED: * S6.OP-TR-0003, S6.OP-PF.TR-0005 * * WHY DID CONDITION HAPPEN: * Unknown at this time. Further investigation is needed to identify the root cause. * * CONSEQUENCES: * Potential disruption in operations, possible maintenance cost, and loss of efficiency if the pump sustained internal damage. * * REQUIREMENTS IMPACTED: * Regular system operation, pump availability * * ADVERSE PHYSICAL CONDITION: * Nonresponsive pump with no visible external damage. * * WHO WAS NOTIFIED: * Control Room, Maintenance Team * * KNOWLEDGEABLE INDIVIDUALS: * Thomson, Garrett, Peterson * * REPEAT OR SIMILAR CONDITION: * No, this is the first time for this incident. * * IMMEDIATE AND RECOMMENDED ACTIONS: * The failed pump will be inspected and tested by the maintenance team. Operations should be ready to shift the workload to auxiliary pumps if necessary. * Updated: Amelia Watson 10.12.2020 18:52:07 * ------------------------------------------------------------ * 10/17/2020 14:37:29 EVELYN SMITH (NUSER) * The cause of the pump failure was due to an internal mechanical malfunction. All defected parts were replaced, and the pump has been successfully tested and re-entered back into service. | What immediate and recommended actions were taken following the pump failure incident? | The failed pump will be inspected and tested by the maintenance team. Operations should be ready to shift the workload to auxiliary pumps if necessary.
191 | 2017-09-15 | 30987652 | 80245603 | 5B Pump abnormal vibration | S4CW -4CWE1 | * **************Incident Description************** * Notification 000030987652 Details * ************************************************************ * 09/15/2017 08:32:14 INCIDENT REPORT (INCIDENT REPORT) * Report submitted by: Laura Thompson 987-654-3210 ENTITY\INCIDENT: * CONDITION DESCRIPTION/LOCATION (THE INAPPROPRIATE ACTION AND ITS NEGATIVE EFFECT/INCLUDE A DETAILED LOCATION DESCRIPTION): * During a scheduled test, 5B Pump showed signs of abnormal vibration. The vibration data indicated an increase of 10% compared to previous tests. The Lab test result doesn’t show any irregularity in coolant level. The vibration could be due to a potential bearing problem. * * ACTIVITIES, PROCESSES, PROCEDURES INVOLVED: * Scheduled Test. * * WHY DID CONDITION HAPPEN? * Unclear, possibly related to a potential bearing problem. * * CONSEQUENCES: * Potential decreased performance, pump failure leading to system downtime. * * REQUIREMENTS IMPACTED: * Scheduled Tests which could lead to delay in system operations. * * ADVERSE PHYSICAL CONDITIONS: * High vibration levels on the pump without a clear cause. * * WHO WAS NOTIFIED: * Supervisor and the Maintenance team. * * KNOWLEDGEABLE INDIVIDUALS: * Maintenance Team. * * REPEAT OR SIMILAR CONDITION: * No, this is the first reported case of such kind. * * IMMEDIATE ACTIONS AND RECOMMENDED ACTIONS: * Inspection of Bearings & other mechanical parts. If vibration continues, the pump may need to be replaced. * 09/16/2017 14:14:09 LAURA THOMPSON (INCIDENT) * The inspection has been carried out. Bearings showing signs of wear. Recommending parts replacement to prevent failure. | What immediate action was recommended due to the abnormal vibration of the pump? | Inspection of Bearings & other mechanical parts. If vibration continues, the pump may need to be replaced.
192 | 2017-10-29 | 30735262 | 80256974 | Leakage observed in valve 16B | S3CW -3CWE7 | * **************Incident Description************** * Notification 000030735262 Details * *********************************************************** * 10/29/2017 08:35:14 INCIDENT REPORT (INCIDENT REPORT) * Report submitted by: William Anderson ENTITY\INCIDENT: * * CONDITION DESCRIPTION/LOCATION (THE INAPPROPRIATE ACTION AND ITS NEGATIVE EFFECT/INCLUDE A DETAILED LOCATION DESCRIPTION): * During a walk-down, Engr. William Anderson observed water leakage in valve 16B. The leakage appeared to be a result of a faulty gasket in the valve assembly. Immediate shut down of valve assembly was done from Unit 3 Control Room. * * ACTIVITIES, PROCESSES, PROCEDURES INVOLVED: * Normal Walkdown * * WHY DID CONDITION HAPPEN? * Presumably due to gasket wear and tear or improper assembly. * * CONSEQUENCES: * Even though the valve was immediately shut down, continuous leakage could lead to wastage of water, and prolonged leakage may cause damage to the associated equipment and may negatively impact the plant performance. * * REQUIREMENTS IMPACTED: * Normal operation * * ADVERSE PHYSICAL CONDITIONS: * Water leakage from Valve 16B * * WHO WAS NOTIFIED: * Control Room, Maintenance Team * * KNOWLEDGEABLE INDIVIDUALS: * William Anderson, Shift Supervisor, Plant Engineer * * REPEAT OR SIMILAR CONDITION: * No * * IMMEDIATE ACTIONS AND RECOMMENDED ACTIONS: * Replacement of the faulty gasket and thorough inspection of the valve assembly to prevent recurrence. Assembly to be inspected properly at the time of commissioning after replacement. * 10/29/2017 10:51:54 WILLIAM ANDERSON (INCIDENT) * The maintenance team initiated S3.OP.AB.VL-0001 to change the valve's gasket. The valve has been placed back into service and is under observation. | What was the immediate action taken after discovering the water leakage in valve 16B? | Immediate shut down of valve assembly was done from Unit 3 Control Room.
193 | 2020-07-12 | 30971045 | 80252915 | Unexpected fluctuation in 9B Pump | S4CW -4CWE2 | * **************Incident Description************** * Notification 000030971045 Details * *********************************************************** * 07/12/2020 19:00:12 INCIDENT REPORT (INCIDENT REPORT) * Report submitted by: Dave Crisp ENTITY\INCIDENT: * * CONDITION DESCRIPTION/LOCATION (THE INAPPROPRIATE ACTION AND ITS NEGATIVE EFFECT/INCLUDE A DETAILED LOCATION DESCRIPTION): * The Operator found sudden fluctuation in the 9B Pump during a regular update check. Immediate system shutdown was initiated to avoid any further complications. An inspection revealed no exterior signs of damage, but fleeting pressure changes were noted. * * ACTIVITIES, PROCESSES, PROCEDURES INVOLVED: * Routine system check and emergency shutdown procedure S4.OP.AB-PUMP-003 * * WHY DID CONDITION HAPPEN? * The exact cause of this issue could not be determined at this point. It could potentially be due to a fault in the system controller. * * CONSEQUENCES: * Potential system failure in case of unchecked fluctuation, leading to significant operational downtime. * * REQUIREMENTS IMPACTED: * Regular operation of the 9B Pump. * * ADVERSE PHYSICAL CONDITIONS: * Transient pressure variations in the 9B Pump. * * WHO WAS NOTIFIED: * Supervisor, Engineering Team * * KNOWLEDGEABLE INDIVIDUALS: * Supervisor, Mr. Watson, Pump specialists - Stefen and Kacie * * REPEAT OR SIMILAR CONDITION: * No, this is the first instance with the 9B Pump. * * IMMEDIATE ACTIONS AND RECOMMENDED ACTIONS: * Technical team to conduct an in-depth analysis of the system to identify the underlying issue. The control software may also need an update. * * 07/15/2020 08:30:06 DAVE CRISP (INCIDENT) * The primary analysis suggested possible faults in the system control panel. A complete system check is required before re-operation. No traces of mechanical issues were found in the pump. | What immediate actions were recommended after the 9B Pump incident? | Technical team to conduct an in-depth analysis of the system to identify the underlying issue. The control software may also need an update.
194 | 2020-01-10 | 40100256 | 90112253 | Excessive vibration from 27B pump motor | S4OW -4OWE3 | * **************Incident Description************** * Notification 000040100256 Details * *********************************************************** * 01/10/2020 07:30:36 INCIDENT REPORT (INCIDENT REPORT) * Report submitted by: Daniel Williams ENTITY\INCIDENT: * * CONDITION DESCRIPTION/LOCATION (THE INAPPROPRIATE ACTION AND ITS NEGATIVE EFFECT/INCLUDE A DETAILED LOCATION DESCRIPTION): * During initial operation for the morning shift, operator observed excessive vibration from the 27B pump. The operation of the pump was immediately halted and an inspection was carried out. Vibrations were associated with a substantial increase in power consumption. The area around the motor cooled and there was no noticeable odor or physical damage. Immediate actions were taken to shift power to alternate pump. * * ACTIVITIES, PROCESSES, PROCEDURES INVOLVED: * Regular startup of 27B pump * WHY DID CONDITION HAPPEN? * Still under investigation. Motor misalignment or worn out parts may be possible causes. * * CONSEQUENCES: * Potential reduction in operational efficiency and possible irreversible damage to pump. * * REQUIREMENTS IMPACTED: * Operational scheduling * * ADVERSE PHYSICAL CONDITIONS: * Increased vibration leading to high energy consumption * * WHO WAS NOTIFIED: * Maintenance Team, Shift Supervisor * * KNOWLEDGEABLE INDIVIDUALS: * Daniel Williams, Maintenance Team * * REPEAT OR SIMILAR CONDITION: * No previous instances * * IMMEDIATE ACTIONS AND RECOMMENDED ACTIONS: * Maintenance team engaged to carry out a thorough motor pump inspection. If vibration persists, consideration for pump replacement should be made; * * 01/11/2020 07:46:21 DANIEL WILLIAMS (INCIDENT) * The issue has been resolved. The cause of the vibration was due to a misalignment of the motor. The motor was realigned and is now functioning normally. | What was the immediate action taken after the excessive vibration from the 27B pump was observed? | The operation of the pump was immediately halted and an inspection was carried out. Immediate actions were taken to shift power to alternate pump.
195 | 2018-12-16 | 30985419 | 90252947 | 33B Pump vibration issues | S4CW -4CWE5 | * **************Incident Description************** * Notification 000030985419 Details * *********************************************************** * 12/16/2018 10:35:26 INCIDENT REPORT (INCIDENT REPORT) * Report submitted by: Thomas Wilson ENTITY\INCIDENT: * * CONDITION DESCRIPTION/LOCATION (THE INAPPROPRIATE ACTION AND ITS NEGATIVE EFFECT/INCLUDE A DETAILED LOCATION DESCRIPTION): * During a scheduled maintenance shutdown, the 33B Pump was found to have high vibrations. The vibrations were noted following the overhaul of the pump carried out under work order 90236245. There are concerns that the pump might have been improperly assembled or a component is defective. The pump operation has been halted temporarily to avoid any potential damage. * * ACTIVITIES, PROCESSES, PROCEDURES INVOLVED: * S4.OP-AB.CW-0005, S4.OP-SO.CW-0003 * * WHY DID CONDITION HAPPEN? * Unclear at this moment, potential improper assembly or defective component could be the reason. * * CONSEQUENCES: * If not addressed promptly, could result in pump failure or reduction in overall system efficiency. * * REQUIREMENTS IMPACTED: * Temporary shutdown of 33B pump operation. * * ADVERSE PHYSICAL CONDITIONS: * High vibration level in the 33B Pump post maintenance. * * WHO WAS NOTIFIED: * Maintenance Supervisor, Engineering Team * * KNOWLEDGEABLE INDIVIDUALS: * Williams, Anderson, Garcia * * REPEAT OR SIMILAR CONDITION: * No * * IMMEDIATE ACTIONS AND RECOMMENDED ACTIONS: * Engineering to inspect the 33B Pump and determine the root cause of vibrations, necessary repairs or replacements to be carried out based on findings. * * Updated: THOMAS WILSON 12.16.2018 14:15:23 * ------------------------------------------------------------ * 12/29/2018 09:03:34 OLIVIA GREEN (MAINTENANCE) * Post inspection, it was identified that misalignment of the pump components was causing the vibrations. The 33 | What was identified as the cause for the high vibrations in the 33B Pump post maintenance? | Post inspection, it was identified that misalignment of the pump components was causing the vibrations.
196 | 2020-11-15 | 30742568 | 80259873 | Unusual vibration in Pump 10D | S4CW -4CWE1 | * **************Incident Description************** * Notification 000030742568 Details * *********************************************************** * 11/15/2020 17:42:22 INCIDENT REPORT (INCIDENT REPORT) * Report submitted by: Emily Carter 123-789-4560 * ENTITY\INCIDENT: * CONDITION DESCRIPTION/LOCATION (THE INAPPROPRIATE ACTION AND ITS NEGATIVE EFFECT/INCLUDE A DETAILED LOCATION DESCRIPTION): * During evening rounds, operator noticed an unsual vibration in Pump 10D. It was operating at typical pressure but showed vibration levels higher than normal operation standards. All other pumps were running under standard conditions. Pump 10D emergency shut down initiated from Unit 4 Control Room and the vibration stopped. The station inspection team did not identify any apparent damage or leaks. The pump will remain offline until further investigation and assessment can be performed. S4.OP-AB.CW-0010 Pump Operation Abnormality was initiated due to the emergency shutdown of 10D Pump. * * ACTIVITIES, PROCESSES, PROCEDURES INVOLVED: * S4.OP.AB-CW-0010, S4.OP-SO.CW-0010 * * WHY DID CONDITION HAPPEN? * Unclear at this moment, although similar anomalies have been reported on different units before. * * CONSEQUENCES: * No immediate consequences, but potential pump damage which could generate efficiency problems once the unit comes back online. * * REQUIREMENTS IMPACTED: * Offline pump operation * * ADVERSE PHYSICAL CONDITIONS: * Unusual vibration from Pump 10D, internal damage potential * * WHO WAS NOTIFIED: * Control Room, Maintenance Team * * KNOWLEDGEABLE INDIVIDUALS: * Cooper, Taylor, Davis * * REPEAT OR SIMILAR CONDITION: * Yes, but not frequent * * IMMEDIATE AND RECOMMENDED ACTIONS: * Conduct a thorough inspection of the Pump 10D * * Updated: EMILY CARTER 11.15.2020 22:00:45 * ------------------------------------------------------------ * 11/18/202 | What was the unusual condition noticed in Pump 10D? | During evening rounds, operator noticed an unsual vibration in Pump 10D. It was operating at typical pressure but showed vibration levels higher than normal operation standards.
197 | 2018-10-10 | 30760005 | 80491207 | Undue noise from 9B pump motor | S3CW -3CWE7-MTRD | * **************Incident Description************** * Notification 000030760005 Details * *********************************************************** * SUMMARY: ENSURE SYNC WITH * ****PS-BB-133 "ISSUE DETECTION AND RESOLUTION PROCESS"***** * * 1) Condition Description/Location (The inappropriate action and its negative effect/Include a detailed location description): * At 1340 on 10/10/18 it was reported by the operator that an unusual noise was coming from the 9B Pump motor. The motor was immediately put off from Unit 3 Control Room. Operation inspection revealed no leaks but an abnormal sound could be sensed. Pump motor temperatures were higher compared to others currently in operation. No external damage signs were manifest. S3.OP-AB.CW-0003 Pump Irregularity was triggered due to the unexpected shutdown of 9B Pump. * * 2) ACTIVITIES, PROCESSES, PROCEDURES INVOLVED: * S3.OP.AB-CW-0002, S3.OP-SO.CW-0002 * * 3) WHY DID CONDITION HAPPEN: * Unclear, though motors have produced abnormal noise in the past * * 4) CONSEQUENCES: * No immediate consequences, but a potential damage could cause inefficient performance when the unit is reactivated. * * 5) REQUIREMENTS IMPACTED: * Out-of-service pump * * 6) ADVERSE PHYSICAL CONDITION: * Noise from 9B Pump motor, potential internal damage * * 7) WHO WAS NOTIFIED: * Control Room, Maintenance Department * * 8) KNOWLEDGEABLE INDIVIDUALS: * Thompson, Green, Rose * * 9) REPEAT OR SIMILAR CONDITION: * Could not confirm * * 10) IMMEDIATE AND RECOMMENDED ACTIONS: * Maintenance to check 9B Pump Motor * * Updated: JASON TAYLOR 10.10.2018 15:56:37 * ------------------------------------------------------------ * 11/01/2018 12:45 | What were the immediate actions taken after the unusual noise was detected in the 9B Pump motor? | The motor was immediately put off from Unit 3 Control Room.
198 | 2018-05-15 | 30841678 | 90284531 | SF6 leak at Busbar Cubicle B | S4SW -4SWE12 | * **************Incident Description************** * Notification 000030841678 Details * *********************************************************** * 05/15/2018 13:42:00 INCIDENT REPORT (INCIDENT REPORT) * Report submitted by: Daniel Ross ENTITY\INCIDENT: * * CONDITION DESCRIPTION/LOCATION (THE INAPPROPRIATE ACTION AND ITS NEGATIVE EFFECT/INCLUDE A DETAILED LOCATION DESCRIPTION): * During the routine inspection at 13:42 on 15/05/2018, Daniel Ross reported SF6 gas leak from Busbar Cubicle B. The leak was isolated and SF6 gas was vented to atmosphere. Engineers and Operations teams were notified and they promptly attended to the issue. Plant safety team was called to assess potential hazards and environmental impact. Immediate checks were done and no high-risk concern was identified. * * ACTIVITIES, PROCESSES, PROCEDURES INVOLVED: * S4.SP.AB-SW-0001, S4.SP-SO.SW-0001 * * WHY DID CONDITION HAPPEN: * Unknown, seals on the cubicle could have deteriorated over time leading to the SF6 leak. * * CONSEQUENCES: * Potential area of risk for staff, potential environmental impact, and interruption in normal operation. * * REQUIREMENTS IMPACTED: * Equipment operation due to SF6 leak. * * ADVERSE PHYSICAL CONDITION: * SF6 gas leak from Busbar Cubicle B * * WHO WAS NOTIFIED: * Control Room, Safety Team * * KNOWLEDGEABLE INDIVIDUALS: * Watts, Johnson, Kim * * 7) REPEAT OR SIMILAR CONDITION: * Yes, previous SF6 leaks were reported on other cubicles * * 8) IMMEDIATE AND RECOMMENDED ACTIONS: * Isolate and rectify the SF6 leak, assess for any damage to the cubicle, conduct a seal check on all other cubicles as a precaution. * Updated: DANIEL ROSS 05.15.2018 15:33:10 * ------------------------------------------------------------ * 05/17/2018 | What immediate and recommended actions were taken after the SF6 gas leak from Busbar Cubicle B? | Isolate and rectify the SF6 leak, assess for any damage to the cubicle, conduct a seal check on all other cubicles as a precaution.
199 | 2020-01-15 | 40081920 | 90172639 | Loud noise from 17B Generator | S4GE -4GE5 | * **************Incident Description************** * Notification 000040081920 Details * *********************************************************** * 07/15/2020 14:30:28 INCIDENT REPORT (INCIDENT REPORT) * Report submitted by: Benny White, 987-654-3210 * ENTITY\INCIDENT: * CONDITION DESCRIPTION/LOCATION (THE INAPPROPRIATE ACTION AND ITS NEGATIVE EFFECT/INCLUDE A DETAILED LOCATION DESCRIPTION): * During regular inspection at 1415, the operator reported loud noise coming from 17B Generator. Generator was immediately shut down in adherence to S4.OP-AB.GE-0007 Generator Emergency Procedure and the noise ceased. No visible damage was observable on the generator. However, the frequency monitor showed slight fluctuation prior to the shutdown. No previous incidents of such noise and frequency behavior were reported for this unit. * * ACTIVITIES, PROCESSES, PROCEDURES INVOLVED: * S4.OP.AB-GE-0007, S4.OP-SO.GE-0003 * * WHY DID CONDITION HAPPEN: * Unknown cause for the noise and frequency fluctuation. * * CONSEQUENCES: * Potential internal mechanical or electrical damage, leading to efficiency loss or unforeseen shut down. * * REQUIREMENTS IMPACTED: * Normal operation of the 17B generator. * * ADVERSE PHYSICAL CONDITIONS: * Loud noise and frequency fluctuation from 17B Generator. * * WHO WAS NOTIFIED: * Supervisor, Maintenance Team * * KNOWLEDGEABLE INDIVIDUALS: * Adams, Johnson, Baker * * REPEAT OR SIMILAR CONDITION: * No * * IMMEDIATE AND RECOMMENDED ACTIONS: * Perform detailed inspection and run diagnostic tests on 17B Generator. * * Updated: BENNY WHITE 07.15.2020 15:00:15 * ------------------------------------------------------------ * 07/20/2020 13:30:07 LISA GREEN (NUSER) * The inspection showed that there was an alignment issue with the internal components of the generator. The generator was adjusted, realigned, and the frequency | What was the observed issue with the 17B generator and what actions were recommended? | During regular inspection at 1415, the operator reported loud noise coming from 17B Generator. Generator was immediately shut down in adherence to S4.OP-AB.GE-0007 Generator Emergency Procedure and the noise ceased. No visible damage was observable on the generator. However, the frequency monitor showed slight fluctuation prior to the shutdown. No previous incidents of such noise and frequency behavior were reported for this unit. Perform detailed inspection and run diagnostic tests on 17B Generator.
200 | 2018-04-17 | 30852054 | 80231569 | OVERHEATING IN 45B MOTOR | S4CW -4CWE7 | * **************Incident Description************** * Notification 000030852054 Details * *********************************************************** * 04/17/2018 08:28:25 INCIDENT REPORT (INCIDENT REPORT) * Report submitted by: John Walters 987-654-3210 ENTITY\INCIDENT: * CONDITION DESCRIPTION/LOCATION (THE INAPPROPRIATE ACTION AND ITS NEGATIVE EFFECT/INCLUDE A DETAILED LOCATION DESCRIPTION): * While conducting a routine check at 07:45 on 04/17/18, heat was noticed coming from the 45B Motor. Motor showed no signs of physical damage. Temperature was much higher than similar motors in operation. An emergency shutdown was initiated from Unit 4 Control Room and the heat has since dissipated. No fire was detected but there was a lingering smell of burnt insulation. * * ACTIVITIES, PROCESSES, PROCEDURES INVOLVED: * S1.OP.AB-CW-0005, S1.OP-SO.CW-0018 * * WHY DID CONDITION HAPPEN: * Uncertain at present, possibly due to an internal component issue. This issue has been observed with other motors in the past. * * CONSEQUENCES: * Possibility of reduced motor efficiency and perhaps a longer-term motor damage, depending on the overheating cause. * * REQUIREMENTS IMPACTED: * Motor availability for normal operations. * * ADVERSE PHYSICAL CONDITION: * Overheating in 45B Motor, potential internal component damage. * * WHO WAS NOTIFIED: * Control Room, Maintenance Department * * KNOWLEDGEABLE INDIVIDUALS: * Walters, Thompson, Adams * * REPEAT OR SIMILAR CONDITION: * Yes, past incidents with other motors. * * IMMEDIATE AND RECOMMENDED ACTIONS: * An inspection of the 45B Motor is urgently required for a detailed understanding of the underlying issue. * * Updated: JOHN WALTERS 04.17.2018 09:32:45 * ------------------------------------------------------------ * 04/19/2018 14:12:32 JAMES DOE (NUSER) * | What was the immediate action taken after overheating was identified in Motor 45B? | An emergency shutdown was initiated from Unit 4 Control Room and the heat has since dissipated.
201 | 2020-05-07 | 40892615 | 90215678 | Untypical voltage spike at Generator 3A | S5EL -5ELE7 | * **************Incident Description************** * Notification 000040892615 Details * *********************************************************** * 05/07/2020 16:28:24 INCIDENT REPORT (INCIDENT REPORT) * Report submitted by: Tara Reed 345-678-9012 ENTITY\INCIDENT: * CONDITION DESCRIPTION/LOCATION (THE INAPPROPRIATE ACTION AND ITS NEGATIVE EFFECT/INCLUDE A DETAILED LOCATION DESCRIPTION): * During normal operation, the auxiliary control room noted an unexpected voltage spike on Generator 3A. Quick checks did not reveal any significant load change nor equipment failure. Voltage returned to stable operating range within 2 minutes. * * ACTIVITIES, PROCESSES, PROCEDURES INVOLVED: * S5.OP-AP.EG-0007 and S5.OP-AP.EG-0021 * * WHY DID CONDITION HAPPEN? * Unknown as of now, however, load changes in grid or internal component degradation might be responsible. * * CONSEQUENCES: * Continued voltage spikes might lead to adverse effects on generator or connected equipment, which can disrupt normal operation. * * REQUIREMENTS IMPACTED: * Consistent voltage supply * * ADVERSE PHYSICAL CONDITIONS: * Unstable voltage output * * WHO WAS NOTIFIED: * Supervisor, Electrical Maintenance Team * * KNOWLEDGEABLE INDIVIDUALS: * Supervisor, Electrical Maintenance Team, Grid Operators * * REPEAT OR SIMILAR CONDITION: * No, this is the first recorded incident of this type. * * IMMEDIATE ACTIONS AND RECOMMENDED ACTIONS: * Initiate in depth diagnostic under work order to investigate potential causes for voltage spike. * 05/10/2020 16:19:05 MICHAEL JOHNSON (INCIDENT) * Inspection found a failed component within the governor control system. Repairs happened immediately, tested, and the generator was returned to its normal operation. | What immediate actions were recommended after the incident of voltage spike on Generator 3A? | Initiate in depth diagnostic under work order to investigate potential causes for voltage spike.
202 | 2020-12-31 | 31012020 | 80236541 | Over temperature in Fan Motor 23C | S4FN -4FNE3 | * **************Incident Description************** * Notification 000031012020 Details * *********************************************************** * 12/31/2020 16:30:00 INCIDENT REPORT (INCIDENT REPORT) * Report submitted by: David Barnes ENTITY\INCIDENT: * * CONDITION DESCRIPTION/LOCATION (THE INAPPROPRIATE ACTION AND ITS NEGATIVE EFFECT/INCLUDE A DETAILED LOCATION DESCRIPTION): * At 1630 on 12/31, the operator reported Fan Motor 23C was over-temp. The equipment was shut down immediately due to the inbuilt emergency shutdown system. No visible smoke or fire damage noticed but there was a noticeable odor of burnt wires. Further inspection by the maintenance team suggested possible fault in the motor insulation. The maintenance shutdown plan S4.OP-AB.FAN-0001 was initiated based on incident. * * ACTIVITIES, PROCESSES, PROCEDURES INVOLVED: * S4.OP.AB-FAN-0001, S4.OP-SO.FAN-0001 * * WHY DID CONDITION HAPPEN: * Unknown, frequently rotating devices like fan motors may fail due to various reasons * * CONSEQUENCES: * Fan Motor is offline. If left unaddressed, could lead to overheating and potential equipment inefficiency. * * REQUIREMENTS IMPACTED: * Fan Motor not available * * ADVERSE PHYSICAL CONDITION: * Over-temp of Fan Motor 23C, could have potential internal damage * * WHO WAS NOTIFIED: * Control Room, Maintenance Team * * KNOWLEDGEABLE INDIVIDUALS: * Barnes, David; Dunn, Peter * * REPEAT OR SIMILAR CONDITION: * No Repeat incident. First Notice. * * IMMEDIATE AND RECOMMENDED ACTIONS: * Maintenance needs to investigate Fan Motor 23C. Replace or repair motor as necessary. * * Updated: DAVID BARNES 12.31.2020 18:30:00 * ------------------------------------------------------------ * 01/02/2021 10:30:12 PETER DUNN (NUSER) * The investigation resulted in identification of internal winding failure. | What action was taken when the over-temp of Fan Motor 23C was reported? | The equipment was shut down immediately due to the inbuilt emergency shutdown system.
203 | 2017-05-13 | 30815843 | 80311545 | 16B Pump slow rate flow | S4CW -4CWE5 | * **************Incident Description************** * Notification 000030815843 Details * *********************************************************** * 05/13/2017 10:01:03 INCIDENT REPORT (INCIDENT REPORT) * Report submitted by: David White ENTITY\INCIDENT: * * CONDITION DESCRIPTION/LOCATION (THE INAPPROPRIATE ACTION AND ITS NEGATIVE EFFECT/INCLUDE A DETAILED LOCATION DESCRIPTION): * During regular operations, it was noted that 16B Pump was running at a lower flow rate than usual.The operator identified the slower flow during a routine flow check of 16B pump at 0930. Immediate inspection did not reveal any obvious physical damage or blockage. * * ACTIVITIES, PROCESSES, PROCEDURES INVOLVED: * Regular operations check. * * WHY DID CONDITION HAPPEN? * The reason behind the slow flow is unknown at this moment. Potential issues could be internal blockage or pump malfunction. * * CONSEQUENCES: * Potentially diminished efficiency and increased wear and tear on the pump. * Risk of system failure if the pump fails entirely. * * REQUIREMENTS IMPACTED: * Normal pump operations * * ADVERSE PHYSICAL CONDITIONS: * Lower flow rate from 16B Pump. * * WHO WAS NOTIFIED: * Operations Supervisor, Maintenance Department * * KNOWLEDGEABLE INDIVIDUALS: * Operations staff, Maintenance Department * * REPEAT OR SIMILAR CONDITION: * Not reported in recent history. * * IMMEDIATE ACTIONS AND RECOMMENDED ACTIONS: * Carry out a thorough inspection and maintenance check. If issues persist, consider replacement of 16B pump. * * 05/15/2017 14:15:12 JOHN DOE (INCIDENT) * Inspection found no physical blockage. Motor inspection showed some anomalies. Decided to replace the pump motor with a backup unit. Post-replacement, the pump is back to normal operation rates. | What immediate actions were taken following the incident with the 16B Pump's decreased flow rate? | Carry out a thorough inspection and maintenance check. If issues persist, consider replacement of 16B pump. Inspection found no physical blockage. Motor inspection showed some anomalies. Decided to replace the pump motor with a backup unit. Post-replacement, the pump is back to normal operation rates.
204 | 2019-02-23 | 30879532 | 90264097 | 28B Compressor vibration and noise issue | S4CW -4CWE5 | * **************Incident Description************** * Notification 000030879532Details * *********************************************************** * 02/23/2019 08:27:10 INCIDENT REPORT (INCIDENT REPORT) * Report Submitted by: Steve Thompson ENTITY\INCIDENT: * * CONDITION DESCRIPTION/LOCATION (THE INAPPROPRIATE ACTION AND ITS NEGATIVE EFFECT/INCLUDE A DETAILED LOCATION DESCRIPTION): * The 28B Compressor started producing unusual vibration and noise during the morning shift. The vibrations were higher than the standard operating values. A visual check revealed no external damage. The condition forced partial shut down of the compressor. * * ACTIVITIES, PROCESSES, PROCEDURES INVOLVED: * Routine check of compressor, S4.OP.AB-CW-0031, S4.OP-SO.CW-0002 * * WHY DID CONDITION HAPPEN? * Cause unknown, further investigation required. Possible internal component wear or misalignment. * * CONSEQUENCES: * Potential equipment damage, risk of complete shutdown, decreased efficiency. * * REQUIREMENTS IMPACTED: * Full operation of the 28B compressor * * ADVERSE PHYSICAL CONDITIONS: * Excessive noise, increased vibration levels * * WHO WAS NOTIFIED: * Maintenance Supervisor, Operations Team * * KNOWLEDGEABLE INDIVIDUALS: * Thompson, Johnson, Peterson * * REPEAT OR SIMILAR CONDITION: * Yes, recorded on other compressors but not on 28B so far. * * IMMEDIATE ACTIONS AND RECOMMENDED ACTIONS: * Shutdown of the compressor, urgent assessment by the maintenance team, check alignment and internal parts * 02/23/2019 15:42:26 JACK PIERCE (INCIDENT) * Dispatched technical team to inspect 28B Compressor. Initial troubleshooting did not provide a conclusive result. Technical team proceeding with detailed internal inspection. | What were the immediate actions taken following the incident with the 28B Compressor? | Shutdown of the compressor, urgent assessment by the maintenance team, check alignment and internal parts.
205 | 2020-04-22 | 30952961 | 80920917 | Motor 30B Vibrations in 2CWF | S2CW -2CWFE8 | * **************Incident Description************** * Notification 000030952961 Details * *********************************************************** * 04/22/2020 09:13:33 INCIDENT REPORT (INCIDENT REPORT) * Report submitted by: David Johnson 234-567-8910 ENTITY\INCIDENT: * * CONDITION DESCRIPTION/LOCATION (THE INAPPROPRIATE ACTION AND ITS NEGATIVE EFFECT/INCLUDE A DETAILED LOCATION DESCRIPTION): * During the daily inspection, excess vibrations were noticed in the 30B Motor pump during operation. Alarm 2CWF issued at 0845, motor vibration reported at 32Hz, and the temperature remained normal. The shutdown procedure was initiated, and pump inspection performed. * * ACTIVITIES, PROCESSES, PROCEDURES INVOLVED: * Daily inspection and emergency procedures S2.OP-AC.CW-0004 * * WHY DID CONDITION HAPPEN? * Suspected bearing wear or imbalance in the pump rotor. * * CONSEQUENCES: * Further operation could cause permanent damage to the pump/motor assembly and decrease plant efficiency. * * REQUIREMENTS IMPACTED: * Regular pump operation. * * ADVERSE PHYSICAL CONDITIONS: * Excessive vibration from 30B Motor pump * * WHO WAS NOTIFIED: * Control Room, Maintenance Team * * KNOWLEDGEABLE INDIVIDUALS: * Noel Anderson, Peter Holmes, Olivia Reed * * REPEAT OR SIMILAR CONDITION: * No, first report of this issue. * * IMMEDIATE ACTIONS AND RECOMMENDED ACTIONS: * Initiated the shutdown of 30B Motor pump, perform detailed inspection and maintenance as necessary. * 04/22/2020 11:47:18 DAVID JOHNSON (INCIDENT) * Further inspection revealed worn out bearings, replaced bearings on 30B pump, tests performed showing normal operation and vibrations within acceptable limits. The pump reinstated to regular operation. | What immediate actions were taken after noticing the excessive vibrations from the 30B Motor pump? | Initiated the shutdown of 30B Motor pump, perform detailed inspection and maintenance as necessary.
206 | 2018-11-25 | 30755692 | 80255989 | 32B Pump motor vibration | S4CW -4CWE2 | * **************Incident Description************** * Notification 000030755692 Details * *********************************************************** * 11/25/2018 14:35:34 INCIDENT REPORT (INCIDENT REPORT) * Report submitted by: David Simmons ENTITY\INCIDENT: * * CONDITION DESCRIPTION/LOCATION (THE INAPPROPRIATE ACTION AND ITS NEGATIVE EFFECT/INCLUDE A DETAILED LOCATION DESCRIPTION): * During routine walkthrough, plant technician reported unusual vibration from the 32B Pump motor. After cross-checking with the control room, the motor parameters, such as temperature and load, were observed to be within normal range. However, the vibration could potentially indicate a mechanical failure in progress. * * ACTIVITIES, PROCESSES, PROCEDURES INVOLVED: * Regular inspection and motor monitoring. * * WHY DID CONDITION HAPPEN? * Reason unclear at the moment - possible mechanical failure or internal issue with the pump. * * CONSEQUENCES: * Possible deterioration and failure of 32B pump, which could affect plant operations. * * REQUIREMENTS IMPACTED: * Usual procedures and checks. * * ADVERSE PHYSICAL CONDITIONS: * Unusual vibration at 32B pump motor. * * WHO WAS NOTIFIED: * Area Supervisor, Team leader, Mechanics * * KNOWLEDGEABLE INDIVIDUALS: * Mechanics, Technicians * * REPEAT OR SIMILAR CONDITION: * No previous incidents noted. * * IMMEDIATE ACTIONS AND RECOMMENDED ACTIONS: * Initiate evaluation of 32B Pump motor, perform vibration analysis. If required, replace or repair necessary parts. * 11/28/2018 10:16:07 ANDREW SMITH (INCIDENT) * Initial inspection did not reveal internal damage to the pump. Further testing and inspection is scheduled. Vibration finding should be verified and component specific actions recommended. | What immediate and recommended actions were taken following the unusual vibration at the 32B pump motor? | Initiate evaluation of 32B Pump motor, perform vibration analysis. If required, replace or repair necessary parts.
207 | 2018-04-03 | 30871356 | 80612357 | ABNORMAL VIBRATION OBSERVED IN 14B PUMP | S5PM -5PVE4 | * **************Incident Description************** * Notification 000030871356 Details * *********************************************************** * 04/03/2018 14:23:00 INCIDENT REPORT (INCIDENT REPORT) * Report submitted by: Sam Johnson, Maintenance staff, ENTITY\INCIDENT: * * 1) Condition Description/Location (The inappropriate action and its potential consequence/Include a detailed location description): * During the evening shift, unusual vibration was noticed in the 14B Pump. Fellow technicians confirmed this observation. There were no immediate signs of leakage but the vibration was abnormal. 14B Pump was then put on standby as a precautionary measure. The pump was functioning in Basement Station 5 at the time of the incident. * * 2) ACTIVITIES, PROCESSES, PROCEDURES INVOLVED: * Routine maintenance and inspection * * 3) WHY DID CONDITION HAPPEN: * The exact cause is yet to be determined. Worn out bearings could be a potential cause. * * 4) CONSEQUENCES: * If unchecked, this could lead to pump failure and potential downtime. * * 5) REQUIREMENTS IMPACTED: * Routine inspection and possibly future operations. * * 6) ADVERSE PHYSICAL CONDITION: * Abnormal vibrations observed in 14B Pump. * * 7) WHO WAS NOTIFIED: * Facilities Manager, Supervisor and Safety Team * * 8) KNOWLEDGEABLE INDIVIDUALS: * Facilities Manager, Safety Team, and Maintenance Supervisor * * 9) REPEAT OR SIMILAR CONDITION: * No, this is the first incident of this nature with 14B Pump. * * 10) IMMEDIATE AND RECOMMENDED ACTIONS: * Maintenance team to investigate the source of vibration. Possible bearing replacement, if necessary. * * Updated: SAM JOHNSON 04.03.2018 16:31:23 * ------------------------------------------------------------ * 04/04/2018 09:10:33 DAVID BLOOM (ENGINEERING) * Initial investigation revealed worn-out bearings as the source of vibrations. Parts ordered and pending installation. | What immediate actions were recommended after noticing abnormal vibrations in the pump? | Maintenance team to investigate the source of vibration. Possible bearing replacement, if necessary.
208 | 2020-01-25 | 31054286 | 80264373 | 12C Fan belt abnormal vibration | S4FAN -4FW3 | * **************Incident Description************** * Notification 000031054286 Details * *********************************************************** * 01/25/2020 15:42:00 INCIDENT REPORT (INCIDENT REPORT) * Report submitted by: David Harris ENTITY\INCIDENT: * * CONDITION DESCRIPTION/LOCATION (THE INAPPROPRIATE ACTION AND ITS NEGATIVE EFFECT/INCLUDE A DETAILED LOCATION DESCRIPTION): * During a routine shift changeover, the operator observed that Fan Unit 12C was vibrating more than expected. Upon checking, it was noticed that the fan belt was causing the vibration. The unit was immediately switched off and the fan belt was inspected for any visible damage. * * ACTIVITIES, PROCESSES, PROCEDURES INVOLVED: * Routine check and Shift Handover procedures * * WHY DID CONDITION HAPPEN? * Unknown at this time. There was no prior indication of an issue with the fan belt. * * CONSEQUENCES: * Unknown. The possibility of fan-belt breakdown, with potential cascading effects on the fan unit and possibly the cooling system. * * REQUIREMENTS IMPACTED: * Routine operation of Fan Unit 12C * * ADVERSE PHYSICAL CONDITIONS: * Unusual fan belt vibration. * * WHO WAS NOTIFIED: * Maintenance Team, Station Engineer * * KNOWLEDGEABLE INDIVIDUALS: * David Harris, Jane Doe (Maintenance Team), John Smith (Station Engineer) * * REPEAT OR SIMILAR CONDITION: * No. This is the first incident related to abnormal fan-belt vibration. * * IMMEDIATE ACTIONS AND RECOMMENDED ACTIONS: * The fan belt must be thoroughly inspected for signs of malfunction. New guidelines must be followed according to S4.OP-AB.FAN-0004 to examine other fan units for similar issues. A thorough root-cause analysis must be conducted immediately. * 01/30/2020 10:16:26 JOHN DOE (INCIDENT) * The root cause of the abnormal fan belt vibration has been determined to be due to wear and tear. The belt has been replaced under order 80268000 and the fan unit is back in operation. Recommend a program | What was the initial observation that led to the discovery of the problem with Fan Unit 12C? | During a routine shift changeover, the operator observed that Fan Unit 12C was vibrating more than expected. Upon checking, it was noticed that the fan belt was causing the vibration.
209 | 2018-12-30 | 30743854 | 80234522 | Overheating of Pump 18A | S5PL -5PLD2 | * **************Incident Description************** * Notification 000030743854 Details * *********************************************************** * 12/30/2018 14:38:05 INCIDENT REPORT (INCIDENT REPORT) * Report submitted by: Samuel Thompson ENTITY\INCIDENT: * * CONDITION DESCRIPTION/LOCATION (THE INAPPROPRIATE ACTION AND ITS NEGATIVE EFFECT/INCLUDE A DETAILED LOCATION DESCRIPTION): * During the process of routine monitoring, it was identified that Pump 18A was overheating beyond the normal range. The inlet pressure was increased to 15 psig, and the temperature crossed above the normal threshold. No visible external signs of damage were reported, but the increased temperature was abnormal. * * ACTIVITIES, PROCESSES, PROCEDURES INVOLVED: * S5.OP-AB.PL-0002, S5.OP-SO.PL-0001 * * WHY DID CONDITION HAPPEN? * Not entirely sure, possible internal wear or debris could be a factor * * CONSEQUENCES: * Potential premature failure, reduced efficiency and potential safety hazard * * REQUIREMENTS IMPACTED: * Regular operation of 18A Pump * * ADVERSE PHYSICAL CONDITIONS: * Excessive heat from Pump 18A beyond normal operating range * * WHO WAS NOTIFIED: * Supervisor, Maintenance Team * * KNOWLEDGEABLE INDIVIDUALS: * Samuel Thompson, James Peterson, Sara Jackson * * REPEAT OR SIMILAR CONDITION: * No similar incidents have been reported prior to this. * * IMMEDIATE ACTIONS AND RECOMMENDED ACTIONS: * The pump has been isolated for further investigation by the maintenance team. If any debris or damage is identified, corrective measures would be initiated immediately. * 01/02/2019 10:23:16 SAMUEL THOMPSON (INCIDENT) * On further investigation, a wear related issue was identified. The pump has been repaired and restored to operational status. Recommend scheduling more frequent maintenance to prevent similar conditions in the future. | What was the identified cause of the overheating of Pump 18A and what preventive action was recommended? | On further investigation, a wear related issue was identified. The pump has been repaired and restored to operational status. Recommend scheduling more frequent maintenance to prevent similar conditions in the future.
210 | 2021-04-30 | 30978504 | 80523671 | Unexpected vibrations from 18D motor | S4CW -4CWE7 | * **************Incident Description************** * Notification 000030978504 Details * *********************************************************** * 04/30/2021 10:15:00 INCIDENT REPORT (INCIDENT REPORT) * Report submitted by: James Miller ENTITY\INCIDENT * * CONDITION DESCRIPTION/LOCATION (THE INAPPROPRIATE ACTION AND ITS NEGATIVE EFFECT/INCLUDE A DETAILED LOCATION DESCRIPTION): * At 10:00 on 4/30/21, while performing routine checks, it was identified that unusual vibrations were coming from 18D Motor. Immediate emergency shut down was initiated. The vibrations ceased post shutdown. The Maintenance and Operations teams did not detect any visible damage, but an underlying issue might be present. S4.OP-AB.CW-0002 Vibrations Abnormality procedure initiated. * * ACTIVITIES, PROCESSES, PROCEDURES INVOLVED: * S4.OP.AB-CW-0002, S4.OP-SO.CW-0002 * * WHY DID CONDITION HAPPEN: * Unknown, although motor vibrations have been detected before. * * CONSEQUENCES: * Potential internal damage causing loss of efficiency and potentially leading to a complete breakdown of 18D Motor when the unit returns to operation. * * REQUIREMENTS IMPACTED: * Motor availability. * * ADVERSE PHYSICAL CONDITION: * Unusual vibrations from 18D Motor. * * WHO WAS NOTIFIED: * Control Room, Maintenance Department * * KNOWLEDGEABLE INDIVIDUALS: * Thompson, Bennett, Kelly. * * REPEAT OR SIMILAR CONDITION: * Unknown. * * IMMEDIATE AND RECOMMENDED ACTIONS: * Maintenance needs to investigate 18D Motor to address the cause of vibrations. * * Updated: JAMES MILLER 04.30.2021 13:15:17 * ------------------------------------------------------------ * 05/10/2021 15:11:43 LUCIA BLACK (INCIDENT) * Post-examination, it was discovered that the motor's misalignment was causing the vibrations. Realignment corrected the issue, and the motor is now operational without issues. | What was the cause of the unusual vibrations from 18D Motor and how was it corrected? | The motor's misalignment was causing the vibrations. Realignment corrected the issue, and the motor is now operational without issues.
211 | 2018-12-12 | 30910271 | 80251010 | D1 Pump noisy after restart | S4CW -4CWE3 | * **************Incident Description************** * Notification 000030910271 Details * *********************************************************** * 12/12/2018 15:17:47 INCIDENT REPORT (INCIDENT REPORT) * Report submitted by: Sam Adams ENTITY\INCIDENT: * * CONDITION DESCRIPTION/LOCATION (THE INAPPROPRIATE ACTION AND ITS NEGATIVE EFFECT/INCLUDE A DETAILED LOCATION DESCRIPTION): * Post maintenance restart of D1 Pump initiated high noise levels. No apparent signs of external damage or leaks. Pump pressure and temperature readings were within the acceptable range. However, the noise was discordant with the normal operating conditions of D1 Pump. * * ACTIVITIES, PROCESSES, PROCEDURES INVOLVED: * S4.OP-SO.CW-0001, Post maintenance test * * WHY DID CONDITION HAPPEN? * Not apparent, possibly due to internal wear or undiscovered damage during maintenance. * * CONSEQUENCES: * Potential internal damage which could result in inefficiency or pump failure. * * REQUIREMENTS IMPACTED: * Continuous operation, peace of work environment * * ADVERSE PHYSICAL CONDITIONS: * High noise level of D1 Pump * * WHO WAS NOTIFIED: * Supervisor, Maintenance Team, Safety Officer * * KNOWLEDGEABLE INDIVIDUALS: * Harris, Franklin, Samuels * * REPEAT OR SIMILAR CONDITION: * No * * IMMEDIATE ACTIONS AND RECOMMENDED ACTIONS: * Maintenance Team to conduct immediate inspection and noise level analysis on D1 Pump. * 12/14/2018 08:09:35 SAM ADAMS (INCIDENT) * The inspection indicated that the noise was due to improper alignment of the pump post-maintenance. The pump has been properly aligned, tested, and returned to service with normal noise levels. No internal damage was found. S4.OP-SO.CW-0001 has been updated to include pump alignment steps in the procedure. | What was the cause of the high noise levels in the D1 Pump? | The inspection indicated that the noise was due to improper alignment of the pump post-maintenance.
212 | 2018-05-12 | 30815237 | 80347536 | 17A valve seal leak | S4PV -4PVS2 | * **************Incident Description************** * Notification 000030815237 Details * *********************************************************** * 05/12/2018 11:02:26 INCIDENT REPORT (INCIDENT REPORT) * Report submitted by: Emily Parker ENTITY\INCIDENT: * * CONDITION DESCRIPTION/LOCATION (THE INAPPROPRIATE ACTION AND ITS NEGATIVE EFFECT/INCLUDE A DETAILED LOCATION DESCRIPTION): * Notification 30815237 identified that 17A Valve has a seal leak post-maintenance. The valve was serviced under work order 80347536. The leak was identified during routine inspection. There is potential for product loss and reduced system efficiency. Efforts on improving the condition of the valve should be carried out. * * ACTIVITIES, PROCESSES, PROCEDURES INVOLVED: * Routine check, S4.OP-AB.PV-0002 Procedure Guidance. * * WHY DID CONDITION HAPPEN? * Likely due to a seal or gasket failure during maintenance. * * CONSEQUENCES: * Potential for product loss, reduced system efficiency, environmental impact. * * REQUIREMENTS IMPACTED: * Work safety, effective operation of the valve and linked system. * * ADVERSE PHYSICAL CONDITIONS: * Leak from 17A valve seal * * WHO WAS NOTIFIED: * Maintenance supervisor, Environment Officer * * KNOWLEDGEABLE INDIVIDUALS: * Maintenance Team * * REPEAT OR SIMILAR CONDITION: * No * * IMMEDIATE ACTIONS AND RECOMMENDED ACTIONS: * The 17A valve should be isolated to prevent further leakage, and proper maintenance needs to be performed. All seals and gaskets should be inspected for damage. S4.OP-AB.PV-0002 guide to seal replacement needs to be adhered. * 05/15/2018 14:51:45 JOHN PATTERSON (MAINTENANCE SUPERVISOR) * The valve has been isolated and the seal has been replaced. No further leakage is observed. The valve can be returned to operation. No environmental impact occurred due to the incident. | What immediate actions were taken and recommended after the detection of the valve leak? | The 17A valve should be isolated to prevent further leakage, and proper maintenance needs to be performed. All seals and gaskets should be inspected for damage. S4.OP-AB.PV-0002 guide to seal replacement needs to be adhered.
213 | 2020-04-27 | 30890521 | 80255933 | Unusual Vibrations From 30C Pump Motor | S3CW -4CWE2 | * **************Incident Description************** * Notification 000030890521 Details * *********************************************************** * 04/27/2020 15:30:04 INCIDENT REPORT (INCIDENT REPORT) * Report submitted by: Thomas Green 456-789-1230 ENTITY\INCIDENT: * * CONDITION DESCRIPTION/LOCATION (THE INAPPROPRIATE ACTION AND ITS NEGATIVE EFFECT/INCLUDE A DETAILED LOCATION DESCRIPTION): * During the daily routine inspection, unusual vibrations were noted from the 30C Pump Motor. On checking the reading, pressure was at 18 psig while current read 320. The water level in the reservoir was high at 85ft. Similar circumstances have never been observed before at this pressure level. There is a possibility that the bearings within the pump or the motor could be damaged. * * ACTIVITIES, PROCESSES, PROCEDURES INVOLVED: * Daily routine inspection * * WHY DID CONDITION HAPPEN? * The precise cause is unknown, but suspected to be due to a fault in bearings or motor misalignment. * * CONSEQUENCES: * If unattended, it could lead to serious mechanical failure of the pump. * * REQUIREMENTS IMPACTED: * Normal daily operations * * ADVERSE PHYSICAL CONDITIONS: * High vibrational level from 30C Pump Motor * * WHO WAS NOTIFIED: * Supervisors/ INCIDENT TEAM * * KNOWLEDGEABLE INDIVIDUALS: * Incident Team, Smith, Lee, Brown * * REPEAT OR SIMILAR CONDITION: * No, this is the first time such a condition has been noted. * * IMMEDIATE ACTIONS AND RECOMMENDED ACTIONS: * Shutdown and investigate the cause of unusually high vibration, If confirmed, replace bearings or realign motor. * * 04/30/2020 11:12:45 THOMAS GREEN (INCIDENT) * The incident investigation identified a misalignment of the motor with pump. The motor was realigned and the pump is back in operation with normal readings. | What were the immediate and recommended actions after noticing the unusual vibrations from the pump motor? | Shutdown and investigate the cause of unusually high vibration, If confirmed, replace bearings or realign motor.
214 | 2020-04-17 | 50725490 | 90513287 | 5C Pump unexpected stop during normal use | S4CW -4CWE2 | * **************Incident Description************** * Notification 000050725490 Details * *********************************************************** * 04/17/2020 15:11:34 INCIDENT REPORT (INCIDENT REPORT) * Report submitted by: Rob Thomas 234-567-8901 ENTITY\INCIDENT: * CONDITION DESCRIPTION/LOCATION (THE INAPPROPRIATE ACTION AND ITS NEGATIVE EFFECT/INCLUDE A DETAILED LOCATION DESCRIPTION): * During regular use, the 5C Pump came to an unexpected stop. Current leveled at 0A, no change from previous setting. The pump does not respond to manual restart attempts at local or remote locations. * * ACTIVITIES, PROCESSES, PROCEDURES INVOLVED: * Normal pump operation. * WHY DID CONDITION HAPPEN? * Unknown at this time. There were no prior indications of a problem. * * CONSEQUENCES: * Reduced plant efficiency due to unavailable pump. * * REQUIREMENTS IMPACTED: * Normal operation of the pump. * * ADVERSE PHYSICAL CONDITIONS: * Pump Failure, no known cause. * * WHO WAS NOTIFIED: * Supervisor/ OPERATION TEAM * * KNOWLEDGEABLE INDIVIDUALS: * Operation Team, Maintenance Crew * * REPEAT OR SIMILAR CONDITION: * No, this is the first occurrence. * * IMMEDIATE ACTIONS AND RECOMMENDED ACTIONS: * Contact maintenance to inspect and repair if needed. Maybe necessary to replace pump depending on cause of issue. * 04/18/2020 09:15:22 JOHN DOE (MAINTENANCE) * We have inspected the pump and identified a possible electrical issue. A replacement part has been ordered and is expected to arrive within a week. | What were the immediate and recommended actions taken after the pump failure? | Contact maintenance to inspect and repair if needed. Maybe necessary to replace pump depending on cause of issue.
215 | 2018-12-15 | 30978326 | 80456932 | Power loss in 10B Transformer | S2EL -2ELT0 | * **************Incident Description************** * Notification 000030978326 Details * *********************************************************** * 12/15/2018 07:30:00 INCIDENT REPORT (INCIDENT REPORT) * Report submitted by: Sam Anderson ENTITY\INCIDENT: * * CONDITION DESCRIPTION/LOCATION (THE INAPPROPRIATE ACTION AND ITS NEGATIVE EFFECT/INCLUDE A DETAILED LOCATION DESCRIPTION): * During normal operations, the 10B Transformer experienced an unexpected power loss. The transformer was successfully transferred to backup power without affecting operations. However, the cause of the power loss is currently unknown. * * ACTIVITIES, PROCESSES, PROCEDURES INVOLVED: * S2.EO-OP.EL-0002, S2.EO-AB.EL-0002 * * WHY DID CONDITION HAPPEN? * Unknown, initial reports suggest potential component failure or power supply issue. * * CONSEQUENCES: * Unplanned switch to backup power, potential transformer damage or unavailability. * * REQUIREMENTS IMPACTED: * Normal operation * * ADVERSE PHYSICAL CONDITIONS: * Unexpected power loss at the 10B transformer. * * WHO WAS NOTIFIED: * Supervisor/ INCIDENT TEAM * * KNOWLEDGEABLE INDIVIDUALS: * Incident Team * * REPEAT OR SIMILAR CONDITION: * No, this is a unique incident. * * IMMEDIATE ACTIONS AND RECOMMENDED ACTIONS: * Begin investigation into the cause of power loss, conduct necessary repairs, and ensure power supply reliability to the 10B Transformer. * 12/19/2018 10:55:18 SAM ANDERSON (INCIDENT) * The team found a faulty circuit breaker that caused the power loss. The breaker has been replaced and the transformer is now running on main power supply. | What immediate and recommended actions were taken following the unexpected power loss at the 10B Transformer? | Begin investigation into the cause of power loss, conduct necessary repairs, and ensure power supply reliability to the 10B Transformer.
216 | 2019-02-23 | 30772198 | 80236597 | Unusual vibration from 8D Motor | S4CW -4CWE7 | * **************Incident Description************** * Notification 000030772198 Details * *********************************************************** * 02/23/2019 07:59:45 INCIDENT REPORT (INCIDENT) * Report submitted by: Mark Thompson ENTITY\INCIDENT: * * CONDITION DESCRIPTION/LOCATION (THE INAPPROPRIATE ACTION AND ITS NEGATIVE EFFECT/INCLUDE A DETAILED LOCATION DESCRIPTION): * At 0759 hrs on 2/23/19 the operator reported an unusual vibration emanating from the 8D Motor. As per safety procedure, 8D Motor was immediately put out of operation from Control Room. Standard inspection did not reveal any visible damage, but there were signs of worn out parts. The vibration anomaly was reported under the S4.OP-AB.MT-0002 Motor Anomaly response guidelines. * * ACTIVITIES, PROCESSES, PROCEDURES INVOLVED: * S4.OP.AB-MT-0002, S4.OP-SO.MT-0003 * * WHY DID CONDITION HAPPEN? * Initial observations indicate age-related wear and tear. Further inspection required. * * CONSEQUENCES: * Potential mechanical failure and loss of motor function. * * REQUIREMENTS IMPACTED: * Downtime for 8D Motor * * ADVERSE PHYSICAL CONDITION: * Unusual vibration in 8D Motor, potential internal wear out * * WHO WAS NOTIFIED: * Control Room, Maintenance Team * * KNOWLEDGEABLE INDIVIDUALS: * Wilson, Rodriguez, Clark * * REPEAT OR SIMILAR CONDITION: * Yes, similar incidents reported in the past * * IMMEDIATE ACTIONS AND RECOMMENDED ACTIONS: * Maintenance scheduled to thoroughly inspect 8D Motor * * Updated: MARK THOMPSON 02.23.2019 14:12:34 * --------------------------------------------------------------- * 03/04/2019 10:05:48 JANE DOE (NUSER) * Post-inspection, it was found that the vibration was due to worn-out bearings. Replacement parts were obtained and installed. The motor underwent a successful operational test after | What was the cause of the unusual vibration in the 8D Motor? | The vibration was due to worn-out bearings.
217 | 2016-09-29 | 30780025 | 80265119 | Temperature Spike in 18B Pump Motor | S3CW -3CWE5 | * **************Incident Description************** * Notification 000030780025 Details * *********************************************************** * 09/29/2016 10:18:37 INCIDENT REPORT (INCIDENT REPORT) * Report submitted by: James Anderson ENTITY\INCIDENT: * * CONDITION DESCRIPTION/LOCATION (THE INAPPROPRIATE ACTION AND ITS NEGATIVE EFFECT/INCLUDE A DETAILED LOCATION DESCRIPTION): * During the morning safety check, it was observed that 18B Pump Motor exhibited a sudden spike in temperature. The pump was immediately shutdown for safety and inspection. Initial findings indicate no gross anomalies. Need further investigation to identify the underlying cause. * * ACTIVITIES, PROCESSES, PROCEDURES INVOLVED: * Regular safety check, sudden shutdown procedure S3.OP.SD.CW-0001. * * WHY DID CONDITION HAPPEN? * Unknown, pending thorough investigation. * * CONSEQUENCES: * Potential damage to the pump motor if the issue is not resolved promptly. Could impact operational efficiency. * * REQUIREMENTS IMPACTED: * RP.AB.CW-0001, S3.OP.SD.CW-0001 * * ADVERSE PHYSICAL CONDITIONS: * High temperature of 18B Pump Motor * * WHO WAS NOTIFIED: * Maintenance Team, Supervisor * * KNOWLEDGEABLE INDIVIDUALS: * Maintenance Team Lead, Engineers * * REPEAT OR SIMILAR CONDITION: * No previous similar incidents reported with 18B Pump. * * IMMEDIATE ACTIONS AND RECOMMENDED ACTIONS: * Investigate the underlying cause of the temperature spike. Follow necessary maintenance and repair procedures based upon the results of the investigation. * 09/29/2016 12:50:38 JAMES ANDERSON (INCIDENT) * Preliminary Investigation concluded no visible damage in the motor. However, the source of the temperature spike has not been identified. Recommend further tests to diagnose the specific malfunction. | What immediate actions were recommended following the sudden temperature spike in the pump motor? | Investigate the underlying cause of the temperature spike. Follow necessary maintenance and repair procedures based upon the results of the investigation.
218 | 2019-11-11 | 30780979 | 80262409 | 9C Pump exhibiting fluctuating pressure | S4CW -4CWE2 | * **************Incident Description************** * Notification 000030780979 Details * *********************************************************** * 11/11/2019 10:22:52 INCIDENT REPORT (INCIDENT REPORT) * Report submitted by: Hayley Black 123-987-6543 * ENTITY\INCIDENT: * * CONDITION DESCRIPTION/LOCATION (THE INAPPROPRIATE ACTION AND ITS NEGATIVE EFFECT/INCLUDE A DETAILED LOCATION DESCRIPTION): * During my shift, I noticed that the 9C Pump was exhibiting fluctuating pressure. Initial pressure reading was at 18 psig but was recorded at 24 psig an hour later. I then observed it decrease to 16 psig and spike to 26 psig within 30 minutes. Previous records do not indicate such fluctuations for 9C Pump. * * ACTIVITIES, PROCESSES, PROCEDURES INVOLVED: * Routine pump pressure monitoring * * WHY DID CONDITION HAPPEN? * Uncertain, possible causes could be a blockage in pump or pump damage. * * CONSEQUENCES: * Sudden pump failure, unplanned shutdown * * REQUIREMENTS IMPACTED: * Regular pump operation * * ADVERSE PHYSICAL CONDITIONS: * Spike and drop of pressure at pump with no known cause * * WHO WAS NOTIFIED: * Supervisor, INCIDENT TEAM * * KNOWLEDGEABLE INDIVIDUALS: * Incident team, Harper, Lewis * * REPEAT OR SIMILAR CONDITION: * No, this is a unique situation * * IMMEDIATE ACTIONS AND RECOMMENDED ACTIONS: * Engineering to investigate the underlying cause of pressure fluctuations. If persisting, pump to be serviced. * 11/11/2019 13:48:09 HAYLEY BLACK (INCIDENT) * Fluctuations continue. Arranged for pump servicing. | Why did the 9C Pump pressure fluctuation condition happen? | Uncertain, possible causes could be a blockage in pump or pump damage.
219 | 2020-09-13 | 30994203 | 80244208 | Vibration from Turbine 2T | S4TW -4TWE2 | * **************Incident Description************** * Notification 000030994203 Details * *********************************************************** * 09/13/2020 13:30:47 INCIDENT REPORT (INCIDENT REPORT) * Report submitted by: Michael Middas ENTITY\INCIDENT: * * CONDITION DESCRIPTION/LOCATION (THE INAPPROPRIATE ACTION AND ITS NEGATIVE EFFECT/INCLUDE A DETAILED LOCATION DESCRIPTION): * During an equipment browsing round, an excessive vibration was noticed coming off of Turbine 2T. A touch test confirmed unusual vibration. Subsequent investigation noted an oil discharge at the base of the Turbine 2T. The area was cleared and Turbine 2T was safely shut down. * * ACTIVITIES, PROCESSES, PROCEDURES INVOLVED: * S4.OP-AB.TW-0002, S4.OP-SO.TW-0001 * * WHY DID CONDITION HAPPEN? * Unknown, possibly due to bearing failure or imbalanced rotor. * * CONSEQUENCES: * Potential Turbine damage, reduced operational efficiency * * REQUIREMENTS IMPACTED: * Normal operation * * ADVERSE PHYSICAL CONDITIONS: * Excessive vibration and oil spills. * * WHO WAS NOTIFIED: * Control Room, Maintenance Team * * KNOWLEDGEABLE INDIVIDUALS: * Maintenance Team, Turbine Engineers * * REPEAT OR SIMILAR CONDITION: * Yes, notification 30823156 * * IMMEDIATE ACTIONS AND RECOMMENDED ACTIONS: * Turbine was shut down safely. Maintenance team is assigned for inspection and necessary repair. Engineering team needs to investigate and report on the cause of the incident. Re-inspection and compliance certification needed before restarting Turbine 2T. * 09/16/2020 17:36:21 JOHN DOE (INCIDENT) * The inspection revealed the vibration was due to a rotor balancing issue. The turbine is being rebalanced and will be back in operation post balance verification and safety approval. | What was the cause of the excessive vibration incident related to Turbine 2T? | The inspection revealed the vibration was due to a rotor balancing issue.
220 | 2022-05-10 | 30854292 | 81056371 | Incident with Pump D3- Leakage | S4P -4PWE9 | * **************Incident Description************** * Notification 000030854292 Details * *********************************************************** * 05/10/2022 15:30:18 INCIDENT REPORT (INCIDENT REPORT) * Report submitted by: Emily Johnson ENTITY\INCIDENT: * * 1) CONDITION DESCRIPTION/LOCATION (THE INAPPROPRIATE ACTION AND ITS NEGATIVE EFFECT/INCLUDE A DETAILED LOCATION DESCRIPTION): * At 1500 on 5/10/22, the operator detected leakage in the D3 Pump during routine check. The pump was immediately shut down to prevent any potential damage or adverse effects. The leak was substantial, causing a pool of liquid around the unit. * * 2) ACTIVITIES, PROCESSES, PROCEDURES INVOLVED: * S4.OP-AB.P-0001 and S4.OP-SO.P-0001 * * 3) WHY DID CONDITION HAPPEN: * Cause of leakage is still being investigated. Possible reasons could be wear and tear of the pump or possibly a broken seal. * * 4) CONSEQUENCES: * If not addressed in time, the leakage can cause significant damage to the pump as well as posing safety risks. * * 5) REQUIREMENTS IMPACTED: * Pump operation and maintenance requirements. * * 6) ADVERSE PHYSICAL CONDITION: * Leakage around D3 Pump, potential pump damage. * * 7) WHO WAS NOTIFIED: * Operations Supervisor, Maintenance Team, Workshop Manager * * 8) KNOWLEDGEABLE INDIVIDUALS: * Operators on duty, Maintenance Team, Jenkins, Woodward, Schmidt * * 9) REPEAT OR SIMILAR CONDITION: * No, this is the first incident of its kind * * 10) IMMEDIATE AND RECOMMENDED ACTIONS: * Maintenance team to inspect and repair D3 Pump. Suggestions include checking the pump seal and the condition of the pump as a whole. Operations to monitor closely post repair. * * Updated: EMILY JOHNSON 05.10.2022 17:18:59 * ------------------------------------------------------------ * 06/08/ | What immediate actions were recommended following the leakage incident at the D3 Pump? | Maintenance team to inspect and repair D3 Pump. Suggestions include checking the pump seal and the condition of the pump as a whole. Operations to monitor closely post repair.
221 | 2016-09-12 | 30798465 | 80265289 | 30B Pump excessive vibration | S4CW -4CWE5 | * **************Incident Description************** * Notification 000030798465 Details * *********************************************************** * 09/12/2016 15:33:42 INCIDENT REPORT (INCIDENT REPORT) * Report submitted by: Tom Harris ENTITY\INCIDENT: * * CONDITION DESCRIPTION/LOCATION (THE INAPPROPRIATE ACTION AND ITS NEGATIVE EFFECT/INCLUDE A DETAILED LOCATION DESCRIPTION): * On 09/12/16 during routine monitoring, the 30B Pump was found to exhibit excessive vibration. Following the protocol, the pump was shut down immediately from Unit 3 control room. Initial inspection did not reveal any visible external damage. The course of action was to initiate abnormality procedure S4.OP-AB.CW-0003 * * ACTIVITIES, PROCESSES, PROCEDURES INVOLVED: * S4.OP.AB-CW-0003, S4.OP-S4.CW-0002 * * WHY DID CONDITION HAPPEN? * Still under investigation, preliminary inspection points towards worn out bearings * * CONSEQUENCES: * Vibration may cause structural damage to the pump/motor. If not addressed, it may lead to pump failure. * * REQUIREMENTS IMPACTED: * Operational readiness of 30B pump * * ADVERSE PHYSICAL CONDITIONS: * Increased vibration on 30B pump * * WHO WAS NOTIFIED: * Control Room, Maintenance Team * * KNOWLEDGEABLE INDIVIDUALS: * Ahmed, Foster, Hughes * * REPEAT OR SIMILAR CONDITION: * No * * IMMEDIATE ACTIONS AND RECOMMENDED ACTIONS: * Initiate S4.OP-AB.CW-0003, schedule a detailed inspection and maintenance. * 09/13/2016 11:54:28 TOM HARRIS (INCIDENT) * On initial investigation, the bearings appear worn out. The pump has been taken offline for detailed inspection and necessary repair. The existing procedure needs to be updated for scheduling premature maintenance. | What immediate actions were taken following the excessive vibration of the 30B Pump? | Following the protocol, the pump was shut down immediately from Unit 3 control room. The course of action was to initiate abnormality procedure S4.OP-AB.CW-0003.
222 | 2019-12-01 | 30928432 | 80531560 | High vibration on 30B Heat Exchanger | S4CW -4CWE1 | * **************Incident Description************** * Notification 000030928432 Details * *********************************************************** * 12/01/2019 14:23:11 INCIDENT REPORT (INCIDENT REPORT) * Report submitted by: Elizabeth Martin ENTITY\INCIDENT: * * CONDITION DESCRIPTION/LOCATION (THE INAPPROPRIATE ACTION AND ITS NEGATIVE EFFECT/INCLUDE A DETAILED LOCATION DESCRIPTION): * High vibration was detected on the 30B Heat Exchanger during routine checks. The pump was isolated and shut down to prevent further damage. No visible damage was observed but further investigation is needed to determine the cause of vibration. * * ACTIVITIES, PROCESSES, PROCEDURES INVOLVED: * S4.OP.AB-HE-0003, S4.OP-SO.HE-0002 * * WHY DID CONDITION HAPPEN? * Preliminary investigation suggests possible misalignment or pump damage. * * CONSEQUENCES: * If unresolved, continuous high vibration can cause severe damage to the pump resulting in a future outage. * * REQUIREMENTS IMPACTED: * Normal operations * * ADVERSE PHYSICAL CONDITIONS: * High levels of vibration on the pump. * * WHO WAS NOTIFIED: * Operation Supervisor, Maintenance Team * * KNOWLEDGEABLE INDIVIDUALS: * Squad Maintenance Team, Engineers * * REPEAT OR SIMILAR CONDITION: * No, First time incident * * IMMEDIATE ACTIONS AND RECOMMENDED ACTIONS: * 30B Heat Exchanger to be examined for misalignment or other possible causes. Maintenance team to take necessary actions based on findings. * 12/04/2019 07:22:33 ELIZABETH MARTIN (INCIDENT) * Inspection carried out revealed misalignment as the cause of vibration. Realignment performed and pump returned to normal operation. | What was the immediate action taken after the high vibration was detected on the 30B Heat Exchanger? | The pump was isolated and shut down to prevent further damage. No visible damage was observed but further investigation is needed to determine the cause of vibration.
223 | 2016-09-23 | 30741250 | 80217349 | 13B Pump suddenly failed to start | S4RS -4RWE2 | * **************Incident Description************** * Notification 000030741250 Details * *********************************************************** * 09/23/2016 15:16:10 INCIDENT REPORT (INCIDENT REPORT) * Report submitted by: Samuel White ENTITY\INCIDENT: * CONDITION DESCRIPTION/LOCATION (THE INAPPROPRIATE ACTION AND ITS NEGATIVE EFFECT/INCLUDE A DETAILED LOCATION DESCRIPTION): * On 23rd Sep at 1435 hours, an attempt made to start 13B pump failed. The pump failed to start leaving the system with less redundancy. Immediate attempts were made to troubleshoot and rectify the problem but were not successful. Further investigation is needed. * * ACTIVITIES, PROCESSES, PROCEDURES INVOLVED: * S4.OP-AB.RS-0002, S4.OP-SO.RS-0001 * * WHY DID CONDITION HAPPEN? * Unknown, Never occurred previously, the pump had been maintained as per schedule. * * CONSEQUENCES: * Downtime and loss of redundancy * * REQUIREMENTS IMPACTED: * System functionality * * ADVERSE PHYSICAL CONDITIONS: * No, except the pump failed to start. * * WHO WAS NOTIFIED: * Control Room, Maintenance Department * * KNOWLEDGEABLE INDIVIDUALS: * Smith, Evans, Wilson * * REPEAT OR SIMILAR CONDITION: * No * * IMMEDIATE ACTIONS AND RECOMMENDED ACTIONS: * Maintenance department immediately troubleshoot the pump. If that fails, initiate a full investigation into the reason for failure. * 09/24/2016 08:33:29 SAMUEL WHITE (INCIDENT) * Following a thorough investigation, it was found that a faulty starter contactor was to blame. The contactor was replaced and the pump is now running smoothly. Further tests and monitoring are encouraged to make sure the pump maintains proper operation. | What was the identified cause of the pump failure incident? | It was found that a faulty starter contactor was to blame. The contactor was replaced and the pump is now running smoothly.
224 | 2018-05-10 | 30890124 | 80246930 | Leak detected at joint pipe 40B | S1CW -1CWE7 | * **************Incident Description************** * Notification 000030890124 Details * *********************************************************** * 05/10/2018 14:52:00 INCIDENT REPORT (INCIDENT REPORT) * Report submitted by: Emily White ENTITY\INCIDENT: * * CONDITION DESCRIPTION/LOCATION (THE INAPPROPRIATE ACTION AND ITS NEGATIVE EFFECT/INCLUDE A DETAILED LOCATION DESCRIPTION): * During a routine maintenance inspection at 1330 on 5/10/18, a small leak was observed at the 40B joint pipe in Operation Room 3B. The leak was isolated and manually shut down immediately. There was no significant water found but a damp area around the pipe indicated constant leakage. Technical team was organized immediately for detailed assessment. * * ACTIVITIES, PROCESSES, PROCEDURES INVOLVED: * S1.OP.AB-CW-0002, S1.OP-SO.CW-0002 * * WHY DID CONDITION HAPPEN: * Unknown, Luminal corrosion or gasket failure might have caused the leak. * * CONSEQUENCES: * Continuous leak could have led to water damage and potential structural consequences with downtime for repair. * * REQUIREMENTS IMPACTED: * Regular supply from 40B joint pipe * * ADVERSE PHYSICAL CONDITION: * Leakage at 40B pipe joint, pipe may have interior corrosion * * WHO WAS NOTIFIED: * Manager of Operation Room, Technical Team * * KNOWLEDGEABLE INDIVIDUALS: * Stephen, Sarah, Peter * * REPEAT OR SIMILAR CONDITION: * No * * IMMEDIATE ACTIONS AND RECOMMENDED ACTIONS: * The affected area was immediately isolated and a comprehensive investigation initiated. Further assessment is required by technical team for repair. * * 05/10/2018 17:22:00 EMILY WHITE (INCIDENT) * Technical Team carried out the assessment and found a minor defect in the pipe joint causing the leak. Immediate repair was done, and leak was arrested. Further monitoring will be carried on the repaired joint. | What was the immediate action taken upon discovering the leakage at the 40B joint pipe? | The affected area was immediately isolated and a comprehensive investigation initiated. Further assessment is required by technical team for repair.
225 | 2020-05-18 | 30783150 | 90116745 | 34B Blower producing vibrations | S4CW -4CWE9 | * **************Incident Description************** * Notification 000030783150 Details * *********************************************************** * 05/18/2020 14:59:45 INCIDENT REPORT (INCIDENT REPORT) * Report submitted by: Taylor White, TWHT@state.gov, 321-654-9870 ENTITY\INCIDENT: * * CONDITION DESCRIPTION/LOCATION (THE INAPPROPRIATE ACTION AND ITS NEGATIVE EFFECT/INCLUDE A DETAILED LOCATION DESCRIPTION): * During routine maintenance on 5/18/20, the engineer noticed that the 34B Blower was producing abnormal vibrations. The Blower was turned off for safety reasons. Further investigation revealed an unusual wear pattern on turbine blades. Immediate action was required to avoid any damage to the surrounding components. S4.OP-AB.BL-0002 Blower Abnormality was activated due to vibration sensed by 34B Blower. * * ACTIVITIES, PROCESSES, PROCEDURES INVOLVED: * S4.OP.AB-BL-0002, S4.OP-SO.BR-0003 * * WHY DID CONDITION HAPPEN: * Unknown, could be due to manufacturing flaws or installation issues. * * CONSEQUENCES: * Potential failure of blower, damage to surrounding parts, loss of operational capability. * * REQUIREMENTS IMPACTED: * Normal operations with 34B Blower * * ADVERSE PHYSICAL CONDITIONS: * Unusual vibrations from 34B Blower, Wear pattern on blades * * WHO WAS NOTIFIED: * On-site Maintenance Team, Supervisors, Control Room * * KNOWLEDGEABLE INDIVIDUALS: * Taylor White, Chris Hayes, Morgan Gray * * REPEAT OR SIMILAR CONDITION: * No * * IMMEDIATE ACTIONS AND RECOMMENDED ACTIONS: * Maintenance to thoroughly inspect 34B Blower, focus on the wear pattern on blades, compare it against manufacturer’s specifications. If unable to fix, replace immediately. * * Updated: TAYLOR WHITE 05.18.2020 16:42:22 * ------------------------------------------------------------ * 05/19/202 | What immediate actions were recommended following the abnormal vibrations of the 34B Blower? | Maintenance to thoroughly inspect 34B Blower, focus on the wear pattern on blades, compare it against manufacturer’s specifications. If unable to fix, replace immediately.
226 | 2018-10-04 | 30875219 | 80236541 | Unusual Vibration in 18C Pump | S4CW -4CWE5 | * **************Incident Description************** * Notification 000030875219 Details * *********************************************************** * 10/04/2018 07:34:20 INCIDENT REPORT (INCIDENT REPORT) * Report submitted by: Daniel Perez, 567-890-1234 ENTITY\INCIDENT: * CONDITION DESCRIPTION/LOCATION (THE INAPPROPRIATE ACTION AND ITS NEGATIVE EFFECT/INCLUDE A DETAILED LOCATION DESCRIPTION): * During manual inspection of Plant 4, an unusual vibration was noted in the 18C Pump. The vibration level had exceeded safe operating level since its last maintenance on 7/27/18 under work order 80184567. The abnormal vibration could potentially damage the pump or surrounding equipment. * * ACTIVITIES, PROCESSES, PROCEDURES INVOLVED: * Manual inspection, S4.OP-AB.PM-0003 * * WHY DID CONDITION HAPPEN? * The exact cause remains uncertain, it is suspected that there might be a misalignment or imbalance in the pump or a failure in the pump bearing. * * CONSEQUENCES: * Potential breakdown, decreased operating efficiency, and increased maintenance costs * * REQUIREMENTS IMPACTED: * Plant reliability * * ADVERSE PHYSICAL CONDITIONS: * Excessive vibration from 18C Pump. * * WHO WAS NOTIFIED: * Plant Supervisor, Incident Response Team * * KNOWLEDGEABLE INDIVIDUALS: * Incident Response Team, Plant Engineers * * REPEAT OR SIMILAR CONDITION: * Yes, Notification 30719820 * * IMMEDIATE ACTIONS AND RECOMMENDED ACTIONS: * Initiate vibration analysis, investigate for possible misalignment, check bearings, and update S4.OP-AB.PM-0003 with findings. * 10/04/2018 14:20:28 DANIEL PEREZ (INCIDENT) * Based on the initial investigation, it appears that there is a significant misalignment in the pump shaft. Scheduling for appropriate repair work and revision of the procedure to include more frequent alignment checks. | What were the immediate actions recommended following the detection of unusual vibration in the pump? | Initiate vibration analysis, investigate for possible misalignment, check bearings, and update S4.OP-AB.PM-0003 with findings.
227 | 2019-04-11 | 30814502 | 80236795 | Abnormal Vibration at Compressor 17D | S4CP -4CPE1 | * **************Incident Description************** * Notification 000030814502 Details * *********************************************************** * 04/11/2019 10:45:20 INCIDENT REPORT (INCIDENT REPORT) * Report submitted by: Emily Fisher ENTITY\INCIDENT: * * CONDITION DESCRIPTION/LOCATION (THE INAPPROPRIATE ACTION AND ITS NEGATIVE EFFECT/INCLUDE A DETAILED LOCATION DESCRIPTION): * During a routine inspection, compressor 17D was experiencing higher than normal vibrations. Incident location is at production unit 4. Vibration analysis show an increase from 0.2g to 0.4g. * * ACTIVITIES, PROCESSES, PROCEDURES INVOLVED: * S4.OP.AB-CP-0005, S4.OP-SO.CP-0009 * * WHY DID CONDITION HAPPEN? * Wear and tear or possible bearing damage. * * CONSEQUENCES: * Over time, these vibrations may cause damage and breakdown of the Compressor unit. * * REQUIREMENTS IMPACTED: * Regular operation may be hampered. * * ADVERSE PHYSICAL CONDITIONS: * Higher than normal vibration readings in compressor 17D. * * WHO WAS NOTIFIED: * Inspection Team, Management, Maintenance Department * * KNOWLEDGEABLE INDIVIDUALS: * Inspection Team, Senior Technician (Williams), Operation Supervisor (Miller) * * REPEAT OR SIMILAR CONDITION: * No * * IMMEDIATE ACTIONS AND RECOMMENDED ACTIONS: * Plan for a shutdown to investigate the cause of vibration. Recommend complete vibration analysis and check up for bearing and impeller balance. If necessary, replace bearings and realign compressor. * * 04/12/2019 09:24:00 EMILY FISHER (INCIDENT) * A shutdown has been planned for coming weekend. Team is prepared for extensive vibration analysis checks and possible bearing replacements. | What was the notable change observed in compressor 17D during a routine inspection? | During a routine inspection, compressor 17D was experiencing higher than normal vibrations. Vibration analysis show an increase from 0.2g to 0.4g.
228 | 2019-02-12 | 30834213 | 90232413 | Vibration observed in Condenser Pump E4 | S4CW -4CWE5 | * **************Incident Description************** * Notification 000030834213 Details * *********************************************************** * 02/12/2019 15:23:12 INCIDENT REPORT (INCIDENT REPORT) * Report submitted by: Lisa Parker ENTITY\INCIDENT: * * CONDITION DESCRIPTION/LOCATION (THE INAPPROPRIATE ACTION AND ITS NEGATIVE EFFECT/INCLUDE A DETAILED LOCATION DESCRIPTION): * During a regular CW system inspection, a significant level of vibration was observed in the E4 Condenser Pump. The vibration monitor was reading at 60 mm/s, which is higher than normal operational levels. * * ACTIVITIES, PROCESSES, PROCEDURES INVOLVED: * Regular CW system inspection. * * WHY DID CONDITION HAPPEN? * The root cause of the elevated vibration levels is currently not clear. However, such incidents can be a result of operating conditions, or potential mechanical issues like bearing damage or imbalance in the rotating parts. * * CONSEQUENCES: * High pump vibrations can lead to damage and reduced operational efficiency. Early detection helps in avoiding possible breakdowns. * * REQUIREMENTS IMPACTED: * Normal Operation * * ADVERSE PHYSICAL CONDITIONS: * Elevated vibration level from E4 Condenser Pump * * WHO WAS NOTIFIED: * The Maintenance Team, Operations Manager, System Engineer * * KNOWLEDGEABLE INDIVIDUALS: * Lisa Parker, System Engineer, Maintenance Team * * REPEAT OR SIMILAR CONDITION: * No, this is the first incident of noticeable vibration on E4 pump. * * IMMEDIATE ACTIONS AND RECOMMENDED ACTIONS: * The pump was shutdown for immediate inspection and maintenance. If necessary, parts will be replaced or adjustments made to reduce the vibration. * 02/13/2019 09:25:30 LISA PARKER (INCIDENT) * The inspection identified worn out bearings as the cause of the vibration. Bearings have been replaced and pump has been reassembled and put back into operation. The vibration levels are now within acceptable limits. | What immediate actions were taken following the detection of high vibrations in the E4 Condenser Pump? | The pump was shutdown for immediate inspection and maintenance. If necessary, parts will be replaced or adjustments made to reduce the vibration.
229 | 2020-12-05 | 31098250 | 80235076 | 18D Pump Motor Oil Leakage | S4CW -4CWE9 | * **************Incident Description************** * Notification 000031098250 Details * *********************************************************** * 12/05/2020 14:22:17 INCIDENT REPORT (INCIDENT REPORT) * Report submitted by: Darren Philips ENTITY\INCIDENT: * * CONDITION DESCRIPTION/LOCATION (THE INAPPROPRIATE ACTION AND ITS NEGATIVE EFFECT/INCLUDE A DETAILED LOCATION DESCRIPTION): * Routine surveillance identified an unusual oil leakage from 18D Pump motor. The leakage was observed from the motor sealing area. Since the motor was overhauled under work order 80245710 during last month's maintenance, oil leakage appears uncommon and might suggest a potential sealing problem. * * ACTIVITIES, PROCESSES, PROCEDURES INVOLVED: * S4.OP.AB-CW-0009, S4.OP-SO.CW-0005 * * WHY DID CONDITION HAPPEN? * Preliminary findings suggest seal discrepancy although final cause needs technical investigation. * * CONSEQUENCES: * Potential motor failure, increased maintenance cost, equipment unavailability. * * REQUIREMENTS IMPACTED: * Normal operation. * * ADVERSE PHYSICAL CONDITIONS: * Oil leakage from 18D Pump motor, potential sealing damage. * * WHO WAS NOTIFIED: * Control Room, Maintenance Department. * * KNOWLEDGEABLE INDIVIDUALS: * Davis, Philips, Johnson * * REPEAT OR SIMILAR CONDITION: * No * * IMMEDIATE ACTIONS AND RECOMMENDED ACTIONS: * Secure motor and arrange maintenance inspection. Update relevant procedures to predict this problem in future. * * Updated: DARREN PHILIPS 12.05.2020 16:13:36 * ------------------------------------------------------------ * 12/07/2020 10:23:12 JANE DOE (INCIDENT) * Maintenance inspection confirms a problem with the motor's seal. Temporary measures has been put in place to mitigate the leakage. A new seal has been ordered and will be replaced during the next scheduled maintenance cycle. Incident closed. | What was the unusual incident observed in 18D Pump motor? | Routine surveillance identified an unusual oil leakage from 18D Pump motor. The leakage was observed from the motor sealing area.
230 | 2020-07-18 | 30965841 | 80565738 | 28B Pump vibrating post overhaul | S2CW -2CWE2 | * **************Incident Description************** * Notification 000030965841 Details * *********************************************************** * 07/18/2020 14:32:45 INCIDENT REPORT (INCIDENT REPORT) * Report submitted by: Robert Hughes ENTITY\INCIDENT: * * 1) CONDITION DESCRIPTION/LOCATION (THE INAPPROPRIATE ACTION AND ITS NEGATIVE EFFECT/INCLUDE A DETAILED LOCATION DESCRIPTION): * After returning from maintenance, 28B Pump was found vibrating more than usual. The pump was taken for a routine overhaul under work order 80128769. Subsequent inspections have shown increased vibration levels, indicating potential issues within the pump. The pump is located in Station S2CW, model 2CWE2 * * 2) ACTIVITIES, PROCESSES, PROCEDURES INVOLVED: * S2.OP.AB-CW-0002, S2.OP-SO.CW-0003 * * 3) WHY DID CONDITION HAPPEN? * Potential imbalance within the pump mechanism or improper assembly during overhaul. The exact reason is currently unknown. * * 4) CONSEQUENCES: * Increased wear and tear of pump parts due to increased vibration. This could lead to premature pump failure. * * 5) REQUIREMENTS IMPACTED: * Pump efficiency and reliability * * 6) ADVERSE PHYSICAL CONDITIONS: * Unusual vibration within pump machinery * * 7) WHO WAS NOTIFIED: * Control Room Operator, Maintenance Team, Engineering Department * * 8) KNOWLEDGEABLE INDIVIDUALS: * Thomas, Roberts, Lydia * * 9) REPEAT OR SIMILAR CONDITION: * No, this is the first incident of its kind * * 10) IMMEDIATE ACTIONS AND RECOMMENDED ACTIONS: * Detailed inspection of the 28B Pump to identify the cause of increased vibrations. Possibly disassembling and further analysis of the components, especially those replaced during the recent overhaul. * Updated: ROBERT HUGHES 07.18.2020 15:35:22 * ------------------------------------------------------------ * 08/01/2020 10:34:31 | What were the immediate and recommended actions after the increased vibration was detected in the pump? | Detailed inspection of the 28B Pump to identify the cause of increased vibrations. Possibly disassembling and further analysis of the components, especially those replaced during the recent overhaul.
231 | 2018-12-30 | 40982357 | 90273613 | Overheating of Pump 33C | S4CW -4CWE7 | * **************Incident Description************** * Notification 000040982357 Details * *********************************************************** * 12/30/2018 16:27:43 INCIDENT REPORT (INCIDENT REPORT) * Report submitted by: Robert Smith 987-654-3210 ENTITY\INCIDENT: * CONDITION DESCRIPTION/LOCATION (THE INAPPROPRIATE ACTION AND ITS NEGATIVE EFFECT/INCLUDE A DETAILED LOCATION DESCRIPTION): * During a standard inspection, it was observed that pump 33C was overheating. Its temperature reading was significantly higher than its peer pumps. The temperature increase was first noticed at 1427 and by 1520 had climbed dangerously close to the pump’s upper limit. * * ACTIVITIES, PROCESSES, PROCEDURES INVOLVED: * Standard equipment check, S4.OP-AB.CW-0003, S4.OP-SO.CW-0003 * WHY DID CONDITION HAPPEN? * Unclear, requires further investigation. There has been no recent maintenance or disturbance of the pump. * * CONSEQUENCES: * Risk of pump damage or failure, possible interruption to operations. * * REQUIREMENTS IMPACTED: * Flow control, temperature balance * * ADVERSE PHYSICAL CONDITIONS: * Overheating of pump, temperature imbalance * * WHO WAS NOTIFIED: * Supervisor, Maintenance Department * * KNOWLEDGEABLE INDIVIDUALS: * Incident Management Team, Sullivan, Davis, Rodriguez * * REPEAT OR SIMILAR CONDITION: * No * * IMMEDIATE ACTIONS AND RECOMMENDED ACTIONS: * Immediate shutdown and cooling of pump 33C. Request an urgent inspection and maintenance by the technical team. * 12/31/2018 08:11:28 Robert Smith (INCIDENT) * The technical team has cooled down the pump and are performing a thorough inspection to identify the cause of overheating. Updates will be provided as they become available. | What were the immediate actions taken after the incident of pump overheating was discovered? | Immediate shutdown and cooling of pump 33C. Request an urgent inspection and maintenance by the technical team.
232 | 2021-11-15 | 31076549 | 90212356 | Leakage at cooling module M7B | S5CW -5CWE9 | * **************Incident Description************** * Notification 000031076549 Details * *********************************************************** * 11/15/2021 07:57:00 INCIDENT REPORT (INCIDENT REPORT) * Report submitted by: Emma Thompson ENTITY\INCIDENT: * * CONDITION DESCRIPTION/LOCATION (THE INAPPROPRIATE ACTION AND ITS NEGATIVE EFFECT/INCLUDE A DETAILED LOCATION DESCRIPTION): * During the daily systems check, a leakage was noted from Cooling Module M7B. * The leakage rate was about 3 liters per hour. No temperature anomalies noted. * Safety protocols initiated and area has been cordoned off. * * ACTIVITIES, PROCESSES, PROCEDURES INVOLVED: * Daily routine check and safety protocols. * * WHY DID CONDITION HAPPEN? * Cause currently unknown; possible weathering of the module or damage. * * CONSEQUENCES: * Potential module failure, leak could increase causing environmental issues. * * REQUIREMENTS IMPACTED: * Normal operation of the cooling system, environmental safety requirements. * * ADVERSE PHYSICAL CONDITIONS: * Leakage at Cooling Module M7B. * * WHO WAS NOTIFIED: * Supervisor, safety coordinator, environmental officer. * * KNOWLEDGEABLE INDIVIDUALS: * Safety team, plant maintenance team. * * REPEAT OR SIMILAR CONDITION: * No * * IMMEDIATE ACTIONS AND RECOMMENDED ACTIONS: * Maintenance team to inspect leakage, determine cause, and conduct necessary repairs. * Conservation efforts are required until module is restored for safety measures. * 11/15/2021 12:56:11 Emma Thompson (INCIDENT) * An inspection has been scheduled to determine the cause of the leakage and initiate repairs. Meanwhile, all necessary safety measures have been taken and water has been rerouted to maintain normal operation. | What immediate actions were recommended after detecting the leakage at Cooling Module M7B? | Maintenance team to inspect leakage, determine cause, and conduct necessary repairs. Conservation efforts are required until module is restored for safety measures.
233 | 2017-09-16 | 30751230 | 80236905 | Unusual vibration on Pump Motor 33B | S4CW -4CWE2 | * **************Incident Description************** * Notification 000030751230 Details * *********************************************************** * 09/16/2017 10:30:20 INCIDENT REPORT (INCIDENT REPORT) * Report submitted by: Jack Carter ENTITY\INCIDENT: * * CONDITION DESCRIPTION/LOCATION (THE INAPPROPRIATE ACTION AND ITS NEGATIVE EFFECT/INCLUDE A DETAILED LOCATION DESCRIPTION): * At 1020 on 9/16/17 during routine inspection, a noticeable vibration was identified on 33B pump motor. The engine was subsequently shut down to avoid possible internal damage. After cooling, it was inspected for anomalies, but no visible damages nor symptoms were observed. Further checking required to determine the cause. * * ACTIVITIES, PROCESSES, PROCEDURES INVOLVED: * Routine maintenance check S4.OP.AB-CW-0004, S4.OP-SO.CW-0003. * * WHY CONDITION HAPPEN? * Unclear at the moment. This is the first occurrence of this nature. * * CONSEQUENCES: * Possible mechanical damage on the motor leading to efficiency loss. * * REQUIREMENTS IMPACTED: * Unavailability of 33B pump * * ADVERSE PHYSICAL CONDITIONS: * Vibration on 33B Pump motor * * WHO WAS NOTIFIED: * Control Room, Maintenance Team, Engineers * * KNOWLEDGEABLE INDIVIDUALS: * Thompson, Martin, Kelly * * REPEAT OR SIMILAR CONDITION: * This is the first occurrence of this nature. * * IMMEDIATE ACTIONS AND RECOMMENDED ACTIONS: * Investigate the root cause of the vibration, and repair 33B Pump Motor * 09/16/2017 13:15:16 JACK CARTER (INCIDENT) * A team has been assembled for thorough inspection. Reports will be submitted upon identification of the cause. | Who were notified about the incident involving vibration in the 33B pump motor? | Control Room, Maintenance Team, Engineers
234 | 2020-05-11 | 40084309 | 85104920 | Detection of Unit 3 Pump 8A's unusual vibration | S1CW -1CWE5 | * **************Incident Description************** * Notification 000040084309 Details * *********************************************************** * 05/11/2020 14:32:36 INCIDENT REPORT (INCIDENT REPORT) * Report submitted by: William Johnson ENTITY\INCIDENT: * * CONDITION DESCRIPTION/LOCATION (THE INAPPROPRIATE ACTION AND ITS NEGATIVE EFFECT/INCLUDE A DETAILED LOCATION DESCRIPTION): * During the standard monitoring process, an unusual vibration was identified in the 8A pump installed at Unit 3. The On-Site Engineering Team was notified and performed a preliminary inspection of the identified issue. The team noted an excessive vibration and unusual noise from the 8A pump, but pump temperature and current were within normal limits. All details have been documented for further investigation. * * ACTIVITIES, PROCESSES, PROCEDURES INVOLVED: * Standard monitoring process * * WHY DID CONDITION HAPPEN? * The exact cause remains unknown. It could be possible alignment issues or a premature bearing wear. * * CONSEQUENCES: * Excessive wear and tear in pump, potential failure of the pump if not attended to promptly. * * REQUIREMENTS IMPACTED: * Daily functionality and operation of the Unit * * ADVERSE PHYSICAL CONDITIONS: * Unusual noise and excessive vibration from pump * * WHO WAS NOTIFIED: * On-Site Engineering Team * * KNOWLEDGEABLE INDIVIDUALS: * On-Site Engineering Team * * REPEAT OR SIMILAR CONDITION: * No, this is the first occurrence of this kind * * IMMEDIATE ACTIONS AND RECOMMENDED ACTIONS: * Immediate halt of the pump is necessary to avoid any possible damage. Perform an in-depth investigation to identify the root cause of the issue and conduct requisite maintenance. * 05/12/2020 16:44:22 WILLIAM JOHNSON (INCIDENT) * The engineering team has performed a detailed examination of the pump, including its alignment and bearings, and discovered an alignment issue. The pump has been realigned and it is now functionally optimal. No bearing | What were the immediate actions and recommendations made after identifying the issue with the 8A pump? | Immediate halt of the pump is necessary to avoid any possible damage. Perform an in-depth investigation to identify the root cause of the issue and conduct requisite maintenance.
235 | 2022-07-01 | 30987456 | 80233456 | Lower coolant levels detected in 34B Pump | S4CW -4CWE2 | * **************Incident Description************** * Notification 000030985687 Details * *********************************************************** * 07/01/2022 13:45:00 INCIDENT REPORT (INCIDENT REPORT) * Report submitted by: Sam Green ENTITY\INCIDENT: * * CONDITION DESCRIPTION/LOCATION (THE INAPPROPRIATE ACTION AND ITS NEGATIVE EFFECT/INCLUDE A DETAILED LOCATION DESCRIPTION): * During the daily assessment, it was noted that the coolant levels in the 34B Pump were lower than usual. The coolant inspection performed revealed a reduction by 20%. This unexpected drop in coolant levels could not be accociated with recent operations or regular wear and tear from usage. * * ACTIVITIES, PROCESSES, PROCEDURES INVOLVED: * Regular coolant level check as part of daily operations. * * WHY DID CONDITION HAPPEN? * It is unclear at the moment. Potential issues could be a leak or an improper refill of coolant during the last maintenance cycle. Further investigation is necessary. * * CONSEQUENCES: * The lower coolant levels could lead to the motor running hotter, leading to potential damage and reduced lifespan of the pump. * * REQUIREMENTS IMPACTED: * Regular operation. Lower coolant levels could lead to potential motor overheating. * * ADVERSE PHYSICAL CONDITIONS: * Lower than acceptable coolant levels. * * WHO WAS NOTIFIED: * Operations Supervisor, Maintenance Team. * * KNOWLEDGEABLE INDIVIDUALS: * Operations Supervisor, Maintenance Team. * * REPEAT OR SIMILAR CONDITION: * There have been isolated incidents in the past, but those were typically associated with leaks. This is the first occurrence where no leak is immediately visible. * * IMMEDIATE ACTIONS AND RECOMMENDED ACTIONS: * Increase the frequency of coolant level checks for 34B Pump to once every shift until cause is determined. Maintenance team to conduct a thorough investigation to find the cause of the decrease in coolant levels. * 07/01/2022 16:23:45 SAM GREEN (INCIDENT) * The approval for increased supervision checks has been obtained. The maintenance team has been informed and is scheduled to take immediate action to determine | What was the observed issue with the 34B Pump and what could potentially cause it? | During the daily assessment, it was noted that the coolant levels in the 34B Pump were lower than usual. The coolant inspection performed revealed a reduction by 20%. This unexpected drop in coolant levels could not be accociated with recent operations or regular wear and tear from usage. It is unclear at the moment. Potential issues could be a leak or an improper refill of coolant during the last maintenance cycle. Further investigation is necessary.
236 | 2022-05-04 | 30987645 | 90234567 | Vibration from 10B Cooling Tower Fan | S4CW -4CWE3 | * **************Incident Description************** * Notification 000030987645 Details * *********************************************************** * 05/04/2022 14:57:12 INCIDENT REPORT (INCIDENT REPORT) * Report submitted by: Emma Wilson ENTITY\INCIDENT: * * CONDITION DESCRIPTION/LOCATION (THE INAPPROPRIATE ACTION AND ITS NEGATIVE EFFECT/INCLUDE A DETAILED LOCATION DESCRIPTION): * At 1340 on 5/4/22 during a routine walkdown, a distinct vibration from the 10B Cooling Tower Fan was reported. The fan was promptly shutdown and inspection was initiated. The vibration ceased upon shutdown. No visible damage or irregularities were noted on the fan blades. However, an unusual residual heat was detected on the fan motor. The incident led to initiation of procedure S4.OP-AB.CT-0001 for Abnormal Cooling Tower Fan operation. * * ACTIVITIES, PROCESSES, PROCEDURES INVOLVED: * S4.OP.AB-CT-0001, S4.OP-SO.CT-0001 * * WHY DID CONDITION HAPPEN: * Undetermined at this time, although similar incidents of fan vibration have been reported in the past. * * CONSEQUENCES: * Undetermined. Vibration could indicate potential misalignment or mechanical issues that may result in reduced fan efficiency or damage if not rectified. * * REQUIREMENTS IMPACTED: * Cooling Tower Fan operation * * ADVERSE PHYSICAL CONDITIONS: * Vibration and heat from 10B Cooling Tower Fan motor. * * WHO WAS NOTIFIED: * Control Room, Maintenance Team * * KNOWLEDGEABLE INDIVIDUALS: * Thompson, Davis, Wilson * * REPEAT OR SIMILAR CONDITION: * Yes, a few previous instances noted. * * IMMEDIATE AND RECOMMENDED ACTIONS: * Further investigation of 10B Cooling Tower Fan Motor is recommended. It is imperative to identify and rectify the cause of vibration and heat before the fan is put back into operation. * * Updated: Emma Wilson 05.04.2022 16:35:12 | What were the observed adverse physical conditions from the 10B Cooling Tower Fan incident? | Vibration and heat from 10B Cooling Tower Fan motor.
237 | 2018-12-16 | 30752186 | 80231445 | 24B Pump excessive vibration | S4CW -4CWE8 | * **************Incident Description************** * Notification 000030752186 Details * *********************************************************** * 12/16/2018 10:31:10 INCIDENT REPORT (INCIDENT REPORT) * Report submitted by: Ryan Thompson ENTITY\INCIDENT: * * CONDITION DESCRIPTION/LOCATION (THE INAPPROPRIATE ACTION AND ITS NEGATIVE EFFECT/INCLUDE A DETAILED LOCATION DESCRIPTION): * In the morning shift, unusual vibration was observed on the 24B Pump. The initial analysis showed that current and temperature were in normal limits. The excessive vibration was identified during the routine inspection and area was immediately secured. The pump was taken offline for further analysis. * * ACTIVITIES, PROCESSES, PROCEDURES INVOLVED: * S4.OP-AB-PUMP-0002, S4.OP-SO.PUMP-0003 * * WHY DID CONDITION HAPPEN? * The precise reason is unknown at this stage, possible pump or motor bearing failure. * * CONSEQUENCES: * Immediate shutdown and assessment of 24B Pump which could lead to loss of efficiency and potential pump damage. * * REQUIREMENTS IMPACTED: * Normal operation of the pump unit * * ADVERSE PHYSICAL CONDITIONS: * Excessive Vibration detected at the 24B Pump * * WHO WAS NOTIFIED: * Operational Manager, Safety Team * * KNOWLEDGEABLE INDIVIDUALS: * Operational Manager, Maintenance Team, Safety Team * * REPEAT OR SIMILAR CONDITION: * Yes, Stage 3 pump experienced similar vibration previously. * * IMMEDIATE ACTIONS AND RECOMMENDED ACTIONS: * Full inspection is required to investigate the unusual vibrations of 24B Pump. Bearings, shaft, impeller and coupling need to be checked. * 12/17/2018 10:36:04 RYAN THOMPSON (INCIDENT) * Parts are now inspected thoroughly, bearing failure detected. Replacement is underway and procedures for regular bearing checks will be implemented to avoid repetitive incidents. | What was the immediate response taken when the unusual vibration was observed on the 24B pump? | The area was immediately secured. The pump was taken offline for further analysis.
238 | 2017-09-19 | 30788901 | 80223457 | 18B Pump unexpected vibration | S3CW -3CWE9 | * **************Incident Description************** * Notification 000030788901 Details * *********************************************************** * 09/19/2017 15:30:12 INCIDENT REPORT (INCIDENT REPORT) * Report submitted by: Thomas Clarke ENTITY\INCIDENT: * * CONDITION DESCRIPTION/LOCATION (THE INAPPROPRIATE ACTION AND ITS NEGATIVE EFFECT/INCLUDE A DETAILED LOCATION DESCRIPTION): * Unexpected vibration began to occur at 18B Pump. Measures were taken to verify pump alignment and motor bearings. Vibration levels were considered acceptable under the procedure S3.OP-SO.CW-0004, but noting it on the higher end of the acceptable range. * * ACTIVITIES, PROCESSES, PROCEDURES INVOLVED: * Review of pump vibration and motor bearing measurements per S3.OP-SO.CW-0004 * * WHY DID CONDITION HAPPEN? * Unspecified. Pump vibrations can have many sources and require further investigation. * * CONSEQUENCES: * Excessive vibration can lead to rapid wear and failure of parts, reduced performance. * * REQUIREMENTS IMPACTED: * Optimum performance of the pump, Procedure S3.OP-SO.CW-0004 * * ADVERSE PHYSICAL CONDITIONS: * High vibration levels on 18B Pump motor * * WHO WAS NOTIFIED: * Supervisor, Engineering Team * * KNOWLEDGEABLE INDIVIDUALS: * Supervisor, Maintenance Team, Engineers * * REPEAT OR SIMILAR CONDITION: * Vibration issues are common in pumps, numerous incidents. * * IMMEDIATE ACTIONS AND RECOMMENDED ACTIONS: * Maintenance and Engineering Teams to investigate origin of the high vibration levels on the 18B pump for root cause assessment. Update of Procedure S3.OP-SO.CW-0004 if necessary. * 09/22/2017 10:45:03 THOMAS CLARKE (INCIDENT) * The source of the vibration was traced back to a misalignment issue. The pump was realigned under work order 80224790 and is currently operating within normal vibration levels. Amy additional | What immediate actions and recommended actions were taken following the incident of unexpected vibration in the 18B pump? | Maintenance and Engineering Teams to investigate origin of the high vibration levels on the 18B pump for root cause assessment. Update of Procedure S3.OP-SO.CW-0004 if necessary.
239 | 2017-04-12 | 30820345 | 80256831 | Humming noise from Air Handler unit 18X | S4HV -4HVE1-AC18 | * **************Incident Description************** * Notification 000030820345 Details * *********************************************************** * 04/12/2017 15:10:12 INCIDENT REPORT (INCIDENT REPORT) * Report submitted by: Donald Green ENTITY\INCIDENT: * * CONDITION DESCRIPTION/LOCATION (THE INAPPROPRIATE ACTION AND ITS NEGATIVE EFFECT/INCLUDE A DETAILED LOCATION DESCRIPTION): * At around 1500 hours on 4/12/17, the operator reported a persistent humming noise from the Air Handler Unit (AHU) 18X. Upon inspection, vibrations were also felt on the unit's casing. The 18X unit was temporarily shut down for a quick assessment. No visible damage was noted externally. However, the unusual humming and vibration raise concerns of potential internal component damage or misalignment. * * ACTIVITIES, PROCESSES, PROCEDURES INVOLVED: * Regular operation of AHU 18X, per S4.OP.AB-HV-0012, S4.OP-SO.HV-0021 * * WHY DID CONDITION HAPPEN?: * Not yet determined. Possibility of component wear or misalignment. * * CONSEQUENCES: * If unchecked, the condition could lead to equipment damage or failure, impacting the HVAC operation in the facility. * * REQUIREMENTS IMPACTED: * Continuous operation of AHU 18X * * ADVERSE PHYSICAL CONDITIONS: * Persistent humming noise and vibration from AHU 18X * * WHO WAS NOTIFIED: * Shift Supervisor, HVAC Maintenance Team * * KNOWLEDGEABLE INDIVIDUALS: * Perez, Henderson, Moore * * REPEAT OR SIMILAR CONDITION: * No past instances noted * * IMMEDIATE ACTIONS AND RECOMMENDED ACTIONS: * Engineering to conduct a detailed examination. If necessary, component realignment or replacement may be required. * 04/12/2017 18:20:38 DONALD GREEN (INCIDENT) * The evaluation of the AHU 18X has been scheduled for completion tomorrow morning. A temporary alternate air handler has been activated to maintain air quality | What could be the potential consequences if the issue with the Air Handler Unit (AHU) 18X is not addressed? | If unchecked, the condition could lead to equipment damage or failure, impacting the HVAC operation in the facility.
240 | 2019-09-18 | 30875401 | 80212249 | Leak detected at CW pump 16B | S4CW -4CWE8 | * **************Incident Description************** * Notification 000030875401 Details * *********************************************************** * 09/18/2019 08:37:37 INCIDENT REPORT (INCIDENT REPORT) * Report submitted by: Katherine Taylor ENTITY\INCIDENT: * * CONDITION DESCRIPTION/LOCATION (THE INAPPROPRIATE ACTION AND ITS NEGATIVE EFFECT/INCLUDE A DETAILED LOCATION DESCRIPTION): * During early morning checks, a small leak was detected at the base of CW pump 16B. A pool of liquid was found upon inspection which indicates a possible failure of the pump seal or a crack in the housing. Immediate shutdown of 16B pump was initiated to prevent further leakage and potential damage to internals. S4.OP-AB.CW-0005 Leak Abnormality was activated. * * ACTIVITIES, PROCESSES, PROCEDURES INVOLVED: * S4.OP.AB-CW-0005, S4.OP-SO.CW-0002 * * WHY DID CONDITION HAPPEN? * Unknown, inspection required to confirm potential causes. * * CONSEQUENCES: * Operational disruption, potential increase in maintenance and repair costs. * * REQUIREMENTS IMPACTED: * Leakage prevention measures * * ADVERSE PHYSICAL CONDITIONS: * Fluid Leak from 16B pump. * * WHO WAS NOTIFIED: * Supervisor, Control Room, Maintenance Team * * KNOWLEDGEABLE INDIVIDUALS: * White, Reynolds, Collins * * REPEAT OR SIMILAR CONDITION: * No, this is the first instance. * * IMMEDIATE ACTIONS AND RECOMMENDED ACTIONS: * Maintenance team to investigate the cause of leakage. All operations associated to pump 16B were halted until further inspection. * 09/19/2019 14:23:12 KATHERINE TAYLOR (INCIDENT) * Investigation confirmed a seal failure was the cause of the leak. Pump 16B was removed from its position and sent for repair. The area was cleaned and is ready for re-installation upon completion of repair works. | What was the immediate course of action taken when the leak was detected at the base of CW pump 16B? | Immediate shutdown of 16B pump was initiated to prevent further leakage and potential damage to internals. S4.OP-AB.CW-0005 Leak Abnormality was activated.
241 | 2018-09-04 | 30815037 | 80254920 | Overheating observed in 27B pump | S4CW -4CWE2 | * **************Incident Description************** * Notification 000030815037 Details * *********************************************************** * 09/04/2018 13:22:30 INCIDENT REPORT (INCIDENT REPORT) * Report submitted by: Robert Harris ENTITY\INCIDENT: * * CONDITION DESCRIPTION/LOCATION (THE INAPPROPRIATE ACTION AND ITS NEGATIVE EFFECT/INCLUDE A DETAILED LOCATION DESCRIPTION): * During routine monitoring, observed high temperature in the 27B Pump. The pump temperature exceeded normal operational limit by 12%. There were no external visible signs of damage or leakage. The increased temperature could potentially lead to wear out or failure of the pump. * * ACTIVITIES, PROCESSES, PROCEDURES INVOLVED: * S4.OP.AB.CW-0001, S4.OP-SO.CW-0001 * * WHY DID CONDITION HAPPEN: * The exact cause of overheating is undetermined. However, based on past incidents, possible reasons could be friction due to debris accumulation or a mechanical overhaul in the pump. A thorough analysis needs to be conducted to identify the exact cause. * * CONSEQUENCES: * Potential wear-out, pump failure which can impact routine operations. * * REQUIREMENTS IMPACTED: * Normal operation of pump, may require emergency shut down. * * ADVERSE PHYSICAL CONDITIONS: * High temperature at 27B Pump with unclear cause * * WHO WAS NOTIFIED: * Supervisor, Maintenance Team * * KNOWLEDGEABLE INDIVIDUALS: * Team Lead, Engineers * * REPEAT OR SIMILAR CONDITION: * No, this is the first time such incident is encountered with this pump. Monitoring other pumps to prevent similar occurrences. * * IMMEDIATE ACTIONS AND RECOMMENDED ACTIONS: * Shut off pump promptly and begin thorough checks to identify the cause of the anomaly, specifically looking into debris or mechanical issues. Further repair or part replacement might be needed based on findings. * 09/05/2018 10:48:30 JANE DOE (INCIDENT) * Technical analysis confirmed the overheating was caused by wear and tear of an internal component. Component was replaced and | What immediate and recommended actions were taken following the detection of high temperature in the 27B Pump? | Shut off pump promptly and begin thorough checks to identify the cause of the anomaly, specifically looking into debris or mechanical issues. Further repair or part replacement might be needed based on findings.
242 | 2019-05-25 | 30830204 | 90255567 | 34B Pump strange vibration | S4CW -4CWE7 | * **************Incident Description************** * Notification 000030830204 Details * *********************************************************** * 05/25/2019 14:11:35 INCIDENT REPORT (INCIDENT REPORT) * Report submitted by: James Wilson 987-654-3210 ENTITY\INCIDENT: * CONDITION DESCRIPTION/LOCATION (THE INAPPROPRIATE ACTION AND ITS NEGATIVE EFFECT/INCLUDE A DETAILED LOCATION DESCRIPTION): * During a preventive maintenance routine, it was observed that 34B Pump was generating an uncommon vibration. Even with standard pressure and temperature conditions, this vibration persisted. Past performance records did not indicate such anomalies for 34B Pump. * * ACTIVITIES, PROCESSES, PROCEDURES INVOLVED: * Regular preventive maintenance. * WHY DID CONDITION HAPPEN? * Cause unknown, possible internal damage or misalignment of the pump. * * CONSEQUENCES: * Potential for reduced efficiency and premature failure of the pump. * * REQUIREMENTS IMPACTED: * Regular maintenance and operation schedule. * * ADVERSE PHYSICAL CONDITIONS: * Special vibration at pump with no definite reason. * * WHO WAS NOTIFIED: * Maintenance Supervisor/ INCIDENT TEAM * * KNOWLEDGEABLE INDIVIDUALS: * Incident Team, Engineering * * REPEAT OR SIMILAR CONDITION: * No, first-time occurrence * * IMMEDIATE ACTIONS AND RECOMMENDED ACTIONS: * Advanced inspection of the pump, if the vibration persists, preventive shutdown and in-depth servicing may be necessary. * 05/25/2019 16:30:30 JAMES WILSON (INCIDENT) * On further investigation, it was found that the pump alignment was slightly off due to recent maintenance actions, which likely led to the vibration. Adjustments have been made to correct the alignment, and the pump is currently operating normally. | What was done to address the vibration issue of the 34B Pump? | On further investigation, it was found that the pump alignment was slightly off due to recent maintenance actions, which likely led to the vibration. Adjustments have been made to correct the alignment, and the pump is currently operating normally.
243 | 2017-09-15 | 30785293 | 80236915 | Unexpected power fluctuations in 18B Pump | S3CW -3CWE7-MTRD | * **************Incident Description************** * Notification 000030785293 Details * *********************************************************** * SUMMARY: REQUIRED TO ACKNOWLEDGE THE EFFICIENT HANDLING OF THIS ISSUE * ****LU-EE-513 "ISSUE OF UNEXPECTED POWER FLUCTUATIONS"****** * * 1) CONDITION DESCRIPTION/LOCATION (THE INAPPROPRIATE ACTION AND ITS NEGATIVE EFFECT/INCLUDE A DETAILED LOCATION DESCRIPTION): * At 13:47 on 9/15/17, the engineer reported unexpected power fluctuations in the 18B Pump. Temporary shutdown from Unit 3 Control Room was performed and power stabilized. Electrical Team inspection did not reveal a direct issue, but an inconsistent power supply was observed. The pump was restarted and appeared to operate normally. LU.EE.AB.SV-0002 Power instability was initiated due to the shutdown of 18B Pump. * * 2) ACTIVITIES, PROCESSES, PROCEDURES INVOLVED: * LU.EE.AB.SV-0002, LU.EE.SO.SV-0001 * * 3) WHY DID CONDITION HAPPEN: * Unclear, the exact cause of the power fluctuations are being investigated. * * 4) CONSEQUENCES: * Potential internal damage, loss of efficiency, and possible disruptions to Supply Chain. * * 5) REQUIREMENTS IMPACTED: * Unstable pump operation * * 6) ADVERSE PHYSICAL CONDITION: * Inconsistent power supply to 18B Pump Motor. * * 7) WHO WAS NOTIFIED: * Control Room, Electrical Team * * 8) KNOWLEDGEABLE INDIVIDUALS: * Parker, Grey, Taylor * * 9) REPEAT OR SIMILAR CONDITION: * Not encountered before * *10) IMMEDIATE AND RECOMMENDED ACTIONS: * Further inspection required of 18B Pump Motor and surrounding power sources * * Updated: JOHN MILLER 09.15.2017 18:26:11 * ------------------------------------------------------------ * 10/01/2017 10:47:15 J | What were the consequences of the unexpected power fluctuations in the 18B Pump? | Potential internal damage, loss of efficiency, and possible disruptions to Supply Chain.
244 | 2022-01-15 | 30980345 | 80256904 | Vibration from 30A Pump Motor | S4CW -4CWE8 | * **************Incident Description************** * Notification 000030980345 Details * *********************************************************** * 01/15/2022 07:19:42 INCIDENT REPORT (INCIDENT REPORT) * Report submitted by: David Green ENTITY\INCIDENT: * CONDITION DESCRIPTION/LOCATION (THE INAPPROPRIATE ACTION AND ITS NEGATIVE EFFECT/INCLUDE A DETAILED LOCATION DESCRIPTION): * During routine operations, unit control detected an unusual vibration from the 30A Pump motor. The vibration was sustained, prompting a system alert. The pump was brought offline safely, and a preliminary inspection was initiated. * ACTIVITIES, PROCESSES, PROCEDURES INVOLVED: * S4.OP.AB-CW-0003, S4.OP-SO.CW-0003, Routine system operation * WHY DID CONDITION HAPPEN? * The cause remains unclear at this time, although it is known that pumps may experience unusual vibrations due to mechanical imbalances or issues with the motor. * CONSEQUENCES: * Potential pump damage, interruption to cooling operations if not addressed swiftly. * REQUIREMENTS IMPACTED: * Normal pump functionality and system cooling * ADVERSE PHYSICAL CONDITIONS: * Unusual vibration from 30A Pump motor * WHO WAS NOTIFIED: * System Control Panel, Maintenance Department * KNOWLEDGEABLE INDIVIDUALS: * Simmons, Carter, Davis * REPEAT OR SIMILAR CONDITION: * No, this is a new occurrence. * IMMEDIATE ACTIONS AND RECOMMENDED ACTIONS: * Maintenance scheduled for a full check and condition analysis of the 30A Pump Motor * 01/16/2022 14:09:20 DAVID GREEN (INCIDENT) * The pump was inspected and was found that a mechanical imbalance caused the unusual vibrations. The issue has been resolved under work order 80256904, and no further vibrations have been detected since the repair. The pump motor is back online and working within normal ranges. | What was the cause of the unusual vibration from the 30A Pump motor? | The pump was inspected and was found that a mechanical imbalance caused the unusual vibrations.
245 | 2018-03-07 | 30745020 | 80230950 | Leaking coolant URV613 Pump | S4CW -4CWE5 | * **************Incident Description************** * Notification 000030745030 Details * *********************************************************** * 03/07/2018 07:46:03 INCIDENT REPORT (INCIDENT REPORT) * Report submitted by: Martin Williams ENTITY\INCIDENT: * * CONDITION DESCRIPTION/LOCATION (THE INAPPROPRIATE ACTION AND ITS NEGATIVE EFFECT/INCLUDE A DETAILED LOCATION DESCRIPTION): * During the night shift, operator noticed increasing coolant level fluctuation in the URV613 Pump with visible leakage evident. The pump was initially returned to service after routine maintenance on 02/26/2018 under work order 80230950. The pump seals and/or integrity may have been compromised during the service. Immediate shutdown implemented to prevent further damage. * * ACTIVITIES, PROCESSES, PROCEDURES INVOLVED: * S4.OP.SO.CW-0002 : Routine operation and checks * * WHY DID CONDITION HAPPEN? * Possible error during pump servicing. * * CONSEQUENCES: * Potential pump failure and critical shutdown during operation. * * REQUIREMENTS IMPACTED: * On-going operation of the pump. * * ADVERSE PHYSICAL CONDITIONS: * Visible coolant leakage and unsteady coolant level. * * WHO WAS NOTIFIED: * Shift Supervisor, Maintenance Team * * KNOWLEDGEABLE INDIVIDUALS: * Maintenance Team, Engineer, Hazardous Material Teams * * REPEAT OR SIMILAR CONDITION: * No * * IMMEDIATE ACTIONS AND RECOMMENDED ACTIONS: * Pump shutdown, seal integrity check, potential seal replacement. Encourage retraining on pump servicing procedures. * 03/07/2018 11:31:52 MARTIN WILLIAMS (INCIDENT) * Initiated pump shutdown and maintenance request. Hazmat team has cleaned the leakage. Await further instruction. | What immediate actions were recommended after the pump leakage was observed? | Pump shutdown, seal integrity check, potential seal replacement. Encourage retraining on pump servicing procedures.
246 | 2016-10-11 | 30741250 | 80188765 | Sudden pressure drop in Pump 18C | S3CW -3CWE9 | * **************Incident Description************** * Notification 000030741250 Details * *********************************************************** * 10/11/2016 14:48:00 INCIDENT REPORT (INCIDENT REPORT) * Report submitted by: Steve Richards ENTITY\INCIDENT: * CONDITION DESCRIPTION/LOCATION (THE INAPPROPRIATE ACTION AND ITS NEGATIVE EFFECT/INCLUDE A DETAILED LOCATION DESCRIPTION): * During routine monitoring, Pump 18C showed a sudden drop in delivery pressure. The usual pressure is around 25 psig, however, it dropped to 15 psig, which is highly unusual. All other parameters, including temperature and tidal conditions, were found normal. * ACTIVITIES, PROCESSES, PROCEDURES INVOLVED: * Regular pressure monitoring * WHY DID CONDITION HAPPEN: * The reason is uncertain, could be due to a blockage in the pump's delivery line or damage to the pump itself. * CONSEQUENCES: * Potential disruption in fluid flow rate leading to low yield, temporary shutdown of activities. * REQUIREMENTS IMPACTED: * Regular operation, throughput, efficiency * ADVERSE PHYSICAL CONDITIONS: * Drop in delivery pressure from Pump 18C * WHO WAS NOTIFIED: * Operations Supervisor, Maintenance Team * KNOWLEDGEABLE INDIVIDUALS: * Operations Manager, Maintenance Head * REPEAT OR SIMILAR CONDITION: * No, this is the first time such an incident has occurred with Pump 18C. * IMMEDIATE ACTIONS AND RECOMMENDED ACTIONS: * Initiated emergency stop, initiated inspection and maintenance. In case of major damage, replacement might be necessary. * 10/12/2016 15:52:42 STEVE RICHARDS (INCIDENT) * On thorough inspection, it was found a piece of rag was causing the blockage. The pump was cleaned and is now in normal operation. The pressure has also returned to the usual level. | What immediate and recommended actions were taken following the drop in delivery pressure from Pump 18C? | Initiated emergency stop, initiated inspection and maintenance. In case of major damage, replacement might be necessary.
247 | 2019-03-22 | 30787456 | 80256534 | Unusual Oil Leak from H4 compressor | S1CM -1CME4-CMPR | * **************Incident Description************** * Notification 000030787456 Details * *********************************************************** * 03/22/2019 07:59:30 INCIDENT REPORT (INCIDENT REPORT) * Report submitted by: Peter Taylor ENTITY\INCIDENT: * * CONDITION DESCRIPTION/LOCATION (THE INAPPROPRIATE ACTION AND ITS NEGATIVE EFFECT/INCLUDE A DETAILED LOCATION DESCRIPTION): * During maintenance shutdown, it was observed that the H4 compressor was leaking oil. This is unusual as the compressor was last serviced six months ago under work order 80234546 and no issue was reported post maintenance. A small pool of oil was seen under the compressor during the inspection round. * * ACTIVITIES, PROCESSES, PROCEDURES INVOLVED: * Regular maintenance scheduled for S1.OP-AB.CM-0001(Compressor Maintenance). * * WHY DID CONDITION HAPPEN? * Unknown, it could be due to seal failure or improper assembly during the last maintenance schedule. * * CONSEQUENCES: * If not attended promptly it could lead to equipment failure or shutdown. * * REQUIREMENTS IMPACTED: * Unavailable compressor for operation. * * ADVERSE PHYSICAL CONDITIONS: * Oil leak from H4 compressor, potential for equipment damage. * * WHO WAS NOTIFIED: * Supervisor, Maintenance Team * * KNOWLEDGEABLE INDIVIDUALS: * Supervisor, Maintenance Team, Smith, Johnson * * REPEAT OR SIMILAR CONDITION: * No * * IMMEDIATE ACTIONS AND RECOMMENDED ACTIONS: * Maintenance to investigate and rectify the oil leak from H4 compressor. * * Updated: PETER TAYLOR 03.22.2019 08:45:00 * ------------------------------------------------------------ * 03/25/2019 09:36:48 ANGELA JOHNSON (NUSER) * On investigation, it was found that the oil seal was damaged causing the leak. The seal was replaced and the compressor was tested with no further leaks. The compressor is now back in operation. | What was the cause of the oil leak from the H4 compressor? | On investigation, it was found that the oil seal was damaged causing the leak.
248 | 2016-09-12 | 30763289 | 80235401 | Vibrations in Pump 19Z | S7PW -7PWE4-RTRB | * **************Incident Description************** * Notification 000030763289 Details * *********************************************************** * 09/12/2016 18:10:35 INCIDENT REPORT (INCIDENT REPORT) * Report submitted by: Sam Williams ENTITY\INCIDENT: * * CONDITION DESCRIPTION/LOCATION (THE INAPPROPRIATE ACTION AND ITS NEGATIVE EFFECT/INCLUDE A DETAILED LOCATION DESCRIPTION): * During a routine operation, abnormal vibrations were detected in 19Z pump. The operator secured the pump, and the vibrations subsided. A detailed review revealed no external damage, but there were indications of internal misalignment or bearing issues. S7.OP-AB.RP-0002 Pump Vibrational Abnormality was initiated due to the abnormal operation of 19Z Pump. * * ACTIVITIES, PROCESSES, PROCEDURES INVOLVED: * S7.OP.AB-RP-0002, S7.OP-SO.RP-0001 * * WHY DID CONDITION HAPPEN?: * Unknown, previous maintenance work may not have been correctly done or components may be worn down. * * CONSEQUENCES: * Immediate shut down avoided any major incident, but potential internal damage might lead to more problems and downtime. * * REQUIREMENTS IMPACTED: * Regular operation of 19Z pump * * ADVERSE PHYSICAL CONDITIONS: * Increased vibrations in 19Z Pump, potential internal damage * * WHO WAS NOTIFIED: * Maintenance Supervisor, Incident Team * * KNOWLEDGEABLE INDIVIDUALS: * Robinson, Green, Anderson * * REPEAT OR SIMILAR CONDITION: * No, first incident of this nature * * IMMEDIATE AND RECOMMENDED ACTIONS: * Engineering team to investigate the 19Z pump and fix any internal misalignment or damage. * * Updated: SAM WILLIAMS 09.12.2016 19:30:47 * ------------------------------------------------------------ * 09/25/2016 13:35:24 JANE DOE (NUSER) * Post-detailed inspection, a misalignment was found in the internal components of the pump. The components were real | What was the initial problem observed with the 19Z pump during the routine operation? | During a routine operation, abnormal vibrations were detected in 19Z pump. The operator secured the pump, and the vibrations subsided. A detailed review revealed no external damage, but there were indications of internal misalignment or bearing issues.
249 | 2019-04-30 | 40071632 | 90226375 | 10B turbine high vibration | S4TR -4TRE2-TURB | * **************Incident Description************** * Notification 000040071632 Details * *********************************************************** * 04/30/2019 14:37:08 INCIDENT REPORT (INCIDENT REPORT) * Report submitted by: David Wilson ENTITY\INCIDENT: * * CONDITION DESCRIPTION/LOCATION (THE INAPPROPRIATE ACTION AND ITS NEGATIVE EFFECT/INCLUDE A DETAILED LOCATION DESCRIPTION): * At 1400 on 4/30/19, operator noticed high vibrations on 10B turbine. It was discovered during a regular inspection, that the turbine's vibrations were higher than the normal operating conditions. Subsequently, turbine was taken offline for immediate inspection and elimination of potential risks. Inspection did not reveal any visible signs of damage but the vibration issue remained. A detailed inspection was initiated under order 90226375. * * ACTIVITIES, PROCESSES, PROCEDURES INVOLVED: * S4.OP.AB-TR-0002, S4.OP-SO.TR-0003 * * WHY DID CONDITION HAPPEN? * Unknown, more detailed inspection needed. Turbines have had high vibration issues in the past. * * CONSEQUENCES: * Unforeseen downtime, potential damage to turbine, safety implications. * * REQUIREMENTS IMPACTED: * Normal operation of turbine 10B disrupted. * * ADVERSE PHYSICAL CONDITIONS: * High vibration levels in Turbine 10B; possible internal damage. * * WHO WAS NOTIFIED: * Control Room, Safety Team * * KNOWLEDGEABLE INDIVIDUALS: * Wilson, Martinez, Garcia * * REPEAT OR SIMILAR CONDITION: * Yes, similar issues with other turbines. * * IMMEDIATE ACTIONS AND RECOMMENDED ACTIONS: * Engineering Team to conduct detailed inspection and suggest further corrective measures. * 04/30/2019 17:04:28 DAVID WILSON (INCIDENT) * A detailed inspection has been initiated and we are in the process of diagnosing the actual cause behind the high vibrations. | Why was turbine 10B taken offline on 04/30/2019? | At 1400 on 4/30/19, operator noticed high vibrations on 10B turbine. It was discovered during a regular inspection, that the turbine's vibrations were higher than the normal operating conditions. Subsequently, turbine was taken offline for immediate inspection and elimination of potential risks.
250 | 2022-03-07 | 30987651 | 80245698 | High Voltage Alert in Generator 3C | S4GC -4GWE2 | * **************Incident Description************** * Notification 000030987651 Details * *********************************************************** * 03/07/2022 14:21:30 INCIDENT REPORT (INCIDENT REPORT) * Report submitted by: Thomas Jenkins 647-458-3957 * ENTITY/INCIDENT: * * CONDITION DESCRIPTION/LOCATION (THE INAPPROPRIATE ACTION AND ITS NEGATIVE EFFECT/INCLUDE A DETAILED LOCATION DESCRIPTION): * In a routine maintenance survey, 3C Generator showed a high voltage alert. The voltage level was observed to be 27% higher than the prescribed limit. Upon inspection, the generator's internal components showed no apparent damage, however, the system had been shut down instantly due to safety protocols. * * ACTIVITIES, PROCESSES, PROCEDURES INVOLVED: * Routine maintenance and emergency shutdown protocol S4.MA-SA.GC-0002 * * WHY DID CONDITION HAPPEN? * The root cause is still unknown. However, loose wiring or component failure are suspected. * * CONSEQUENCES: * Any prolonged operation at high voltage could risk equipment damage and operational downtime. * * REQUIREMENTS IMPACTED: * Normal operation, safety protocols * * ADVERSE PHYSICAL CONDITIONS: * High voltage alert in 3C Generator * * WHO WAS NOTIFIED: * Maintenance, Safety teams, and Supervision * * KNOWLEDGEABLE INDIVIDUALS: * Safety Team, Electrical Engineers * * REPEAT OR SIMILAR CONDITION: * No, this is the first instance of this kind. * * IMMEDIATE ACTIONS AND RECOMMENDED ACTIONS: * Inspect and repair the 3C generator. Safety and Electrical team to jointly evalute the root cause of the incident. Update preventive maintenance and inspection protocol if needed. * 03/08/2022 09:43:52 THOMAS JENKINS (INCIDENT) * The generator has been inspected and no visible damage was found. A detailed investigation into the cause of the high voltage alert is ongoing. Electical team is focusing on wiring connections and control unit. | What immediate actions were recommended after the high voltage alert in the 3C Generator? | Inspect and repair the 3C generator. Safety and Electrical team to jointly evalute the root cause of the incident. Update preventive maintenance and inspection protocol if needed.
251 | 2020-09-12 | 30987543 | 80287325 | 25B Pump Motor Breakdown | S4CW -4CWE2 | * **************Incident Description************** * Notification 000030987543 Details * *********************************************************** * 09/12/2020 14:58:02 INCIDENT REPORT (INCIDENT REPORT) * Report submitted by: Emily Williams 987-654-3210 ENTITY\INCIDENT: * CONDITION DESCRIPTION/LOCATION (THE INAPPROPRIATE ACTION AND ITS NEGATIVE EFFECT/INCLUDE A DETAILED LOCATION DESCRIPTION): * During the evening shift, 25B Pump motor stopped functioning. The 25B Pump was found to be offline due to internal motor faults. Immediate inspection did not reveal any visible signs of external damage or overheating. The sudden engine stoppage led to a temporary disruption in operations. * * ACTIVITIES, PROCESSES, PROCEDURES INVOLVED: * Daily operational check * * WHY DID CONDITION HAPPEN? * Unknown, possibly due to motor failure or an electrical fault. * * CONSEQUENCES: * Short-term operational disruption. Long-term consequences unknown until fault is identified. * * REQUIREMENTS IMPACTED: * Normal operation * * ADVERSE PHYSICAL CONDITIONS: * Sudden motor shutdown with no apparent cause * * WHO WAS NOTIFIED: * Supervisor, Operations Team, Electrical Maintenance Team * * KNOWLEDGEABLE INDIVIDUALS: * Supervisor, Operations Team, Electrical Maintenance Team * * REPEAT OR SIMILAR CONDITION: * No, this is the first incident of this kind * * IMMEDIATE ACTIONS AND RECOMMENDED ACTIONS: * Electrical Maintenance Team to investigate cause of motor shutdown. Operations to implement contingency plan for motor failure * 09/12/2020 18:32:56 EMILY WILLIAMS (INCIDENT) * Maintenance team is conducting an in-depth investigation into the pump motor failure. Further actions will be directed based on the findings. The contingency plan is efficiently addressing operational needs at this time. | What immediate actions were taken after the 25B Pump motor stopped functioning? | Electrical Maintenance Team to investigate cause of motor shutdown. Operations to implement contingency plan for motor failure.
252 | 2020-09-15 | 30827599 | 90241587 | High vibration in 9B Pump motor | S4CW -4CWE1 | * **************Incident Description************** * Notification 000030827599 Details * *********************************************************** * 09/15/2020 13:35:00 INCIDENT REPORT (INCIDENT REPORT) * Report submitted by: Henry Page ENTITY\INCIDENT: * * CONDITION DESCRIPTION/LOCATION (THE INAPPROPRIATE ACTION AND ITS NEGATIVE EFFECT/INCLUDE A DETAILED LOCATION DESCRIPTION): * During shift, we noticed an unusually high vibration coming from the 9B Pump motor in Basement 1. Immediate shutdown was initiated from Unit 4 Control Room. The Fire Department and Operational team did not find any visible damage. However, the vibration sensor showed readings much higher than the other pump motors currently in operation. * * ACTIVITIES, PROCESSES, PROCEDURES INVOLVED: * S4.OP.AB-CW-0002, S4.OP-SO.CW-0002 * * WHY DID CONDITION HAPPEN: * Unknown. The cause needs to be investigated by the maintenance team. * * CONSEQUENCES: * The consequence could involve potential pump damage if operation continues with high vibration levels. * * REQUIREMENTS IMPACTED: * Operating function of 9B Pump * * ADVERSE PHYSICAL CONDITION: * High vibration of 9B Pump motor * * WHO WAS NOTIFIED: * Overall Supervisor, and the Fire Department * * KNOWLEDGEABLE INDIVIDUALS: * Peterson, James, Blake * * REPEAT OR SIMILAR CONDITION: * Unavailable * * IMMEDIATE AND RECOMMENDED ACTIONS: * Terminate operation and conduct maintenance check on 9B Pump Motor * * Updated: HENRY PAGE 09.15.2020 15:30:55 * ------------------------------------------------------------ * 09/28/2020 09:17:32 LISA SMITH (MAINTENANCE) * Post shutdown check revealed that pump imbalance was causing the vibration. All pump components were inspected, rebalanced, and verified for proper operation. The pump is now back in service with normal vibration levels. | What was the identified cause of the unusually high vibration in the 9B Pump motor? | Post shutdown check revealed that pump imbalance was causing the vibration.
253 | 2020-04-25 | 30914756 | 80295647 | Unusual Vibration from 8B Pump Motor | S4CW -4CWE8-MTRD | * **************Incident Description************** * Notification 000030914756 Details * *********************************************************** * SUMMARY: FOLLOW REQUIREMENTS IN * ****PS-AA-150 "EQUIPMENT INSPECTION AND MAINTENANCE PROCEDURE"***** * * 1) Condition Description/Location (The inappropriate action and its negative effect/Include a detailed location description): * At 1615 on 4/25/20, the operator reported unusual vibration from the 8B Pump motor. 8B Pump was powered down as a precautionary measure from Unit 4 Control Room. No visible damage was present upon initial inspection. S4.OP-AB.CW-0003 Equipment Abnormality was initiated due to the unexpected vibration of 8B Pump. * * 2) ACTIVITIES, PROCESSES, PROCEDURES INVOLVED: * S4.OP.AB-CW-0003, S4.OP-SO.CW-0002 * * 3) WHY DID CONDITION HAPPEN: * The cause is currently unknown, insightful inspection of pump motor required. * * 4) CONSEQUENCES: * Downtime in pump operation, potential internal damage causing longer-term efficiency loss. * * 5) REQUIREMENTS IMPACTED: * Continuous operation of the 8B pump * * 6) ADVERSE PHYSICAL CONDITION: * Vibration from 8B Pump motor, potential internal damage. * * 7) WHO WAS NOTIFIED: * Control Room, Maintenance Team * * 8) KNOWLEDGEABLE INDIVIDUALS: * Jackson, Thompson, Davis * * 9) REPEAT OR SIMILAR CONDITION: * No past incidents noted * * 10) IMMEDIATE AND RECOMMENDED ACTIONS: * Dispatch maintenance for detailed investigation of 8B Pump Motor * * Updated: RICHARD JOHNSON 04.25.2020 19:13:07 * ------------------------------------------------------------ * 04/29/2020 08:53:36 SARAH BLACK (MAINTENANCE) * After inspection of the 8 | What was the immediate action taken following the notification of the unusual vibration from the 8B Pump motor? | 8B Pump was powered down as a precautionary measure from Unit 4 Control Room.
254 | 2022-03-05 | 30843712 | 80245457 | Unsteady Temperature in Boiler 7A | S5BW -5BWE19 | * **************Incident Description************** * Notification 000030843712 Details * *********************************************************** * 03/05/2022 07:15:00 INCIDENT REPORT (INCIDENT REPORT) * Report submitted by: Robert Stone ENTITY\INCIDENT: * * CONDITION DESCRIPTION/LOCATION (THE INAPPROPRIATE ACTION AND ITS NEGATIVE EFFECT/INCLUDE A DETAILED LOCATION DESCRIPTION): * Engineer reported unsteady temperature reading in Boiler 7A. Frequent temperature fluctuations causing concerns about operational stability and potential damage to the boiler system. Temperature readings remain within operation limits, but the constant change could reflect an underlying issue. * * ACTIVITIES, PROCESSES, PROCEDURES INVOLVED: * Regular temperature check, Boiler operation, Procedure S5.OP-AB.BW-0003 * * WHY DID CONDITION HAPPEN? * Potential factors include sensor errors, boiler insulation problems, or inadequate fuel burning. * * CONSEQUENCES: * Temperature instability could lead to operational inefficiencies, causing potential boiler damage and elevated operational costs. * * REQUIREMENTS IMPACTED: * Boiler operation continuity * * ADVERSE PHYSICAL CONDITIONS: * Fluctuating temperature at Boiler 7A * * WHO WAS NOTIFIED: * Process Supervisor, Operations Team * * KNOWLEDGEABLE INDIVIDUALS: * Stevens, Anderson, Hughes * * REPEAT OR SIMILAR CONDITION: * No * * IMMEDIATE ACTIONS AND RECOMMENDED ACTIONS: * Engineering to inspect the boiler and temperature controls system. Troubleshoot potential sensor issues. If issue persists, expand investigation to include the fuel system and boiler insulation. * 03/07/2022 15:33:47 ELIZABETH WILLIAMS (INCIDENT) * After investigation, it was found that the temperature fluctuation was due to an issue with the burner control system. The system was recalibrated and the temperature instability issue has been resolved. I recommend updating the procedure to include periodic checking and calibration of the burner control system. | What was the identified cause of the unsteady temperature readings in Boiler 7A and what was the proposed solution? | After investigation, it was found that the temperature fluctuation was due to an issue with the burner control system. The system was recalibrated and the temperature instability issue has been resolved. I recommend updating the procedure to include periodic checking and calibration of the burner control system.
255 | 2016-05-11 | 30701456 | 80212345 | Unstable pressure in pump 18D | S4CW -4CWE7 | * **************Incident Description************** * Notification 000030701456 Details * *********************************************************** * 05/11/2016 15:32:00 INCIDENT REPORT (INCIDENT REPORT) * Report submitted by: Emily Rodriguez ENTITY\INCIDENT: * * CONDITION DESCRIPTION/LOCATION (THE INAPPROPRIATE ACTION AND ITS NEGATIVE EFFECT/INCLUDE A DETAILED LOCATION DESCRIPTION): * At 1528 on 11/05/16 the operator reported unstable pressure in pump 18D. Based on the operator's notes, the problem could affect the efficiency and performance of the 18D Pump. The pump was not shut down and continues to run at a pressure lower than usual. Operation team's inspection did not reveal any leakages or external signs of damage; however, the readings on the pressure meter fluctuated. S4.OP-AB.CW-0002 Pump Abnormality was initiated. It appears the potential problem could be internal. * * ACTIVITIES, PROCESSES, PROCEDURES INVOLVED: * S4.OP.AB-CW-0002, S4.OP-SO.CW-0002 * * WHY DID CONDITION HAPPEN? * Uncertain, however, prior instances of this issue happened due to faulty pressure valves. * * CONSEQUENCES: * Efficiency being reduced, potential pump damage, possible shutdown if pressure becomes too low. * * REQUIREMENTS IMPACTED: * Normal pump operation * * ADVERSE PHYSICAL CONDITIONS: * Fluctuating pressure in 18D Pump, probable internal issue. * * WHO WAS NOTIFIED: * Supervisor, Operation's Team * * KNOWLEDGEABLE INDIVIDUALS: * Wilson, Davis, Patel * * REPEAT OR SIMILAR CONDITION: * No, this is the first reported case of this issue * * IMMEDIATE ACTIONS AND RECOMMENDED ACTIONS: * Engineering analysis requested, inspection scheduled for 18D Pump. If the issue persists or worsens, pump shutdown will be considered. * 05/14/2016 11:29:06 JOHN DOE (INSTANT) * Preliminary investigations suggest a | What was the consequence of the unstable pressure reported in pump 18D? | Efficiency being reduced, potential pump damage, possible shutdown if pressure becomes too low.
256 | 2022-03-02 | 30917234 | 80239561 | Unexpected Oil Leakage detected in 56B pump | S1CW -1CWE5 | * **************Incident Description************** * Notification 000030917234 Details * *********************************************************** * 03/02/2022 16:00:15 INCIDENT REPORT (INCIDENT REPORT) * Report submitted by: William Turner 987-654-3210 ENTITY\INCIDENT: * CONDITION DESCRIPTION/LOCATION: * During an unscheduled equipment inspection, an unexpected oil leakage was detected by the maintenance team from 56B Pump near Outlot 5. This is unusual because maintenance was performed on the same pump just weeks ago. The oil spread is currently contained, but continual leakage might pose an environmental hazard if unchecked. * * ACTIVITIES, PROCEDURES, PROCESSES INVOLVED: * Equipment inspection and maintenance - S1.OP.AB-OC-0002, S1.OP-EM.OC-0001 * * WHY DID CONDITION HAPPEN? * Unknown, as leakage is unexpected. Possible reasons could be erroneous sealing during the last maintenance or unexpected component failure. * * CONSEQUENCES: * Potential environmental hazard, reduced operational capacity. * * REQUIREMENTS IMPACTED: * Normal functionality of 56B Pump * * ADVERSE PHYSICAL CONDITIONS: * Oil leakage around pump * * WHO WAS NOTIFIED: * Environmental Response Team, Supervisor, Maintenance team * * KNOWLEDGEABLE INDIVIDUALS: * On-site maintenance team, Environmental Response Team * * REPEAT OR SIMILAR CONDITION: * No similar instances have been identified in recent history. * * IMMEDIATE ACTIONS AND RECOMMENDED ACTIONS: * Immediate containment of the oil spill, analysis of the oil leakage source, and repair work as needed. All activities should be documented and the procedure should be revised if necessary. * 03/02/2022 19:25:46 WILLIAM TURNER (INCIDENT REPORT) * The Environmental Response Team has contained the spill and the maintenance team has been notified to investigate the source of the leakage on priority. Further updates will be conveyed post investigation. | What actions were taken immediately after the oil leakage was detected from the 56B Pump? | Immediate containment of the oil spill, analysis of the oil leakage source, and repair work as needed. All activities should be documented and the procedure should be revised if necessary. The Environmental Response Team has contained the spill and the maintenance team has been notified to investigate the source of the leakage on priority.
257 | 2018-06-25 | 30848936 | 80258743 | Vibration in 33B Pump system | S4CW -4CWE7 | * **************Incident Description************** * Notification 000030848936 Details * *********************************************************** * 06/25/2018 10:17:49 INCIDENT REPORT (INCIDENT REPORT) * Report submitted by: David Harris ENTITY\INCIDENT: * * CONDITION DESCRIPTION/LOCATION (THE INAPPROPRIATE ACTION AND ITS NEGATIVE EFFECT/INCLUDE A DETAILED LOCATION DESCRIPTION): * During a routine inspection, abnormal vibration was detected in the 33B Pump system. Review of system operation parameters revealed normal current values, but the vibration was significantly higher than normal operating condition. It's unknown if this was due to a mechanical issue with the pump or something else. * * ACTIVITIES, PROCESSES, PROCEDURES INVOLVED: * S4.OP.AB-CW-0005, S4.OP-SO.CW-0005 * * WHY DID CONDITION HAPPEN? * The cause is uncertain, possible mechanical failure or foreign object interference. * * CONSEQUENCES: * Severe vibration might lead to equipment failure and downtime of operations. * * REQUIREMENTS IMPACTED: * Equipment malfunctions might affect normal operation. * * ADVERSE PHYSICAL CONDITIONS: * Abnormal vibration in 33B Pump system * * WHO WAS NOTIFIED: * Maintenance Supervisor, Safety Department * * KNOWLEDGEABLE INDIVIDUALS: * Maintenance Team, Safety Manager, Incident Team * * REPEAT OR SIMILAR CONDITION: * No known similar conditions reported * * IMMEDIATE ACTIONS AND RECOMMENDED ACTIONS: * Initiate S4.OP-AB.CW-0005 to halt operation and conduct a thorough inspection of the 33B pump system. If necessary, the pump should be taken out of service and repaired. * 06/27/2018 13:28:11 DAVID HARRIS (INCIDENT) * Maintenance completed the inspection. It was determined that a foreign object was causing the abnormal vibration. The pump has now been cleaned, inspected, and put back into service with normal vibration levels. Further monitoring will be conducted to ensure the condition | What was the initial abnormal condition detected in the 33B Pump system during the routine inspection? | During a routine inspection, abnormal vibration was detected in the 33B Pump system. Review of system operation parameters revealed normal current values, but the vibration was significantly higher than normal operating condition.
258 | 2017-09-25 | 40857329 | 90123456 | 33A Motor abnormal vibration | S1SW -1SWE8 | * **************Incident Description************** * Notification 000040857329 Details * *********************************************************** * 09/25/2017 14:18:23 INCIDENT REPORT (INCIDENT REPORT) * Report submitted by: David Gomez ENTITY\INCIDENT: * * CONDITION DESCRIPTION/LOCATION (THE INAPPROPRIATE ACTION AND ITS NEGATIVE EFFECT/INCLUDE A DETAILED LOCATION DESCRIPTION): * During usual surveillance, detected anomalous vibration on 33A Motor. Motor parameters showed higher load, which could lead to motor failure if unattended. Comparative analysis with other motors revealed the anomaly. * * ACTIVITIES, PROCESSES, PROCEDURES INVOLVED: * Routine Monitoring * * WHY DID CONDITION HAPPEN? * Probable worn-out bearings or misalignment. * * CONSEQUENCES: * Potential motor failure and disruption of operations. * * REQUIREMENTS IMPACTED: * Smooth operational efficiency * * ADVERSE PHYSICAL CONDITIONS: * Excessive vibration on 33A Motor * * WHO WAS NOTIFIED: * Supervisor, Operations Team * * KNOWLEDGEABLE INDIVIDUALS: * Maintenance Team * * REPEAT OR SIMILAR CONDITION: * Previous incidents of abnormal vibration, none specifically for 33A motor. * * IMMEDIATE ACTIONS AND RECOMMENDED ACTIONS: * Early intervention through detailed moter inspection. If problem persist, bearing replacement or realignment might be necessary. * 09/27/2017 10:56:44 DAVID GOMEZ (INCIDENT) * Initiated inspection process, and found worn-out bearings as suspected. Immediate changing of bearings is set in motion. | What was the identified cause of the excessive vibration on the 33A Motor, and what actions were recommended to address it? | Probable worn-out bearings or misalignment. Early intervention through detailed motor inspection. If problem persist, bearing replacement or realignment might be necessary. Initiated inspection process, and found worn-out bearings as suspected. Immediate changing of bearings is set in motion.
259 | 2018-12-10 | 30765890 | 80243511 | Odd vibration from 25A Compressor | S4AC -4ACE7-LTGD | * **************Incident Description************** * Notification 000030765890 Details * *********************************************************** * 12/10/2018 15:25:45 INCIDENT REPORT (INCIDENT REPORT) * Report submitted by: Lisa Thompson ENTITY\INCIDENT: * * CONDITION DESCRIPTION/LOCATION (THE INAPPROPRIATE ACTION AND ITS NEGATIVE EFFECT/INCLUDE A DETAILED LOCATION DESCRIPTION): * At approximately 1515 on 12/10/2018, the operator reported an odd vibration from the 25A Compressor. Based on the abnormal noise and vibration readings, 25A Compressor was taken offline and shut down to prevent potential damage. An immediate inspection did not reveal any external signs of damage. However, an internal investigation is required to determine the root cause of the vibration. * * ACTIVITIES, PROCESSES, PROCEDURES INVOLVED: * S4.OP.AB-AC-0002, S4.OP-SO.AC-0003 * * WHY DID CONDITION HAPPEN? * Undetermined, internal investigation is required. * * CONSEQUENCES: * Potential compressor damage that could result in a loss of capacity when brought back online. * * REQUIREMENTS IMPACTED: * Normal operation, potential availability of compressor * * ADVERSE PHYSICAL CONDITIONS: * Odd vibration from 25A Compressor * * WHO WAS NOTIFIED: * Maintenance Team, Supervisors * * KNOWLEDGEABLE INDIVIDUALS: * Patterson, Davis, Thompson * * REPEAT OR SIMILAR CONDITION: * No, first occurrence * * IMMEDIATE AND RECOMMENDED ACTIONS: * Initiate an investigation to determine the cause of the vibration, and required maintenance. Perform a thorough inspection of the unit before bringing it back online. * * Updated: LISA THOMPSON 12.10.2018 16:35:26 * * 12/20/2018 09:15:42 JOHN DOE (NUSER) * The internal investigation revealed an imbalance in the compressor's rotor. After rebalancing and performing a run test, the compressor is now | What was the issue reported with the 25A Compressor? | At approximately 1515 on 12/10/2018, the operator reported an odd vibration from the 25A Compressor. Based on the abnormal noise and vibration readings, 25A Compressor was taken offline and shut down to prevent potential damage.
260 | 2018-04-15 | 30837241 | 80244952 | Excessive vibration at 18A Pump | S4CW -4CWE6 | * **************Incident Description************** * Notification 000030837241 Details * *********************************************************** * 04/15/2018 11:10:23 INCIDENT REPORT (INCIDENT REPORT) * Report submitted by: David Rodriguez ENTITY\INCIDENT: * CONDITION DESCRIPTION/LOCATION (THE INAPPROPRIATE ACTION AND ITS NEGATIVE EFFECT/INCLUDE A DETAILED LOCATION DESCRIPTION): * Excessive vibration was identified on 18A Pump during a regular system check. The vibration sensor reading was 8.7mm/s and the pump was partially offline due to abnormal vibration. All other parameters, like the running current, were in normal range. * ACTIVITIES, PROCESSES, PROCEDURES INVOLVED: * S4.OP.AB-CW-0018, S4.OP-SO.CW-0017 * WHY DID CONDITION HAPPEN? * The cause of excessive vibration is still not determined; possible internal damage or worn bearings. * CONSEQUENCES: * Possible pump damage and reduced operational efficiency. * REQUIREMENTS IMPACTED: * Unit 4 Cooling Water Pump * ADVERSE PHYSICAL CONDITIONS: * Excessive vibration at 18A Pump. * WHO WAS NOTIFIED: * Maintenance Supervisor, Control Room * KNOWLEDGEABLE INDIVIDUALS: * Davis, Richard, Johnson * REPEAT OR SIMILAR CONDITION: * No, this is the first instance. * IMMEDIATE ACTIONS AND RECOMMENDED ACTIONS: * Conduct detailed inspection and maintenance of 18A Pump. * 04/16/2018 13:43:21 DAVID RODRIGUEZ (INCIDENT) * Maintenance team currently investigating the 18A Pump issue. Detailed inspection and maintenance will be conducted. | What was the identified issue with the 18A Pump? | Excessive vibration was identified on 18A Pump during a regular system check. The vibration sensor reading was 8.7mm/s and the pump was partially offline due to abnormal vibration.
261 | 2022-01-26 | 40923756 | 90502007 | Tank KZ4 Valve not properly sealed | S4WK -4WBZ1 | * **************Incident Description************** * Notification 000040923756 Details * *********************************************************** * 01/26/2022 14:32:12 INCIDENT REPORT (INCIDENT REPORT) * Report submitted by: Jacob Stevens 789-321-654 ENTITY\INCIDENT: * CONDITION DESCRIPTION/LOCATION (THE INAPPROPRIATE ACTION AND ITS NEGATIVE EFFECT/INCLUDE A DETAILED LOCATION DESCRIPTION): * During the periodic inspection, it was found that tank KZ4's outlet valve was not sealing properly. Leaking observed on the floor resulting in wet spots identified during the routine survey around the tank area. This tank typically operates leakage-free, hence leakage around valve indicates a malfunctioning seal. * * ACTIVITIES, PROCESSES, PROCEDURES INVOLVED: * S4.OP.AB-WB-0003, Routine inspection * * WHY DID CONDITION HAPPEN? * Could be due to the wearing out of the valve seal. * * CONSEQUENCES: * Potential loss of chemicals, safety risks due to spillage * * REQUIREMENTS IMPACTED: * Leak-free operation of tank KZ4 valve * * ADVERSE PHYSICAL CONDITIONS: * Leakage observed around the tank KZ4 * * WHO WAS NOTIFIED: * Shift supervisor, Safety & Incident Team * * KNOWLEDGEABLE INDIVIDUALS: * Jacob Stevens, Shift supervisors, Incident Team * * REPEAT OR SIMILAR CONDITION: * No * * IMMEDIATE ACTIONS AND RECOMMENDED ACTIONS: * Shut down tank KZ4, Replace valve seal urgently. Undergo complete inspection of the all valves * 01/26/2022 17:16:24 JACOB STEVENS (INCIDENT) * The team quickly responded to stop the leakage. The faulty seal was replaced and the tank is now back in safe operation. Proper documentation of valve seal change will be made. Monitoring will be continued to verify the success of the repair. | What was the observed problem with tank KZ4 during the periodic inspection? | During the periodic inspection, it was found that tank KZ4's outlet valve was not sealing properly. Leaking observed on the floor resulting in wet spots identified during the routine survey around the tank area.
262 | 2018-11-30 | 30852136 | 80236850 | Oil leak observed in Pump 17D | S4CW -4CWE7 | * **************Incident Description************** * Notification 000030852136 Details * *********************************************************** * 11/30/2018 14:35:10 INCIDENT REPORT (INCIDENT REPORT) * Report submitted by: David Smith ENTITY\INCIDENT: * * CONDITION DESCRIPTION/LOCATION (THE INAPPROPRIATE ACTION AND ITS NEGATIVE EFFECT/INCLUDE A DETAILED LOCATION DESCRIPTION): * During preventative maintenance, a small oil leak was observed on Pump 17D around the seal area. This leak wasn't there during the last inspection which suggests it may have occurred recently. The pump is currently operational but the oil leak could potentially cause mechanical failures in the future. * * ACTIVITIES, PROCESSES, PROCEDURES INVOLVED: * Preventative maintenance procedure S4.OP-SO.CW-0002. * * WHY DID CONDITION HAPPEN? * Possible wear and tear or a faulty oil seal. * * CONSEQUENCES: * Loss of motor efficiency due to potential mechanical failures. * * REQUIREMENTS IMPACTED: * Maintain operational integrity of Pump 17D. * * ADVERSE PHYSICAL CONDITIONS: * Oil leak from Pump 17D. * * WHO WAS NOTIFIED: * Supervisor, Maintenance Manager. * * KNOWLEDGEABLE INDIVIDUALS: * Maintenance Manager, Engineers. * * REPEAT OR SIMILAR CONDITION: * No, this is the first time an oil leak has been noticed on Pump 17D. * * IMMEDIATE ACTIONS AND RECOMMENDED ACTIONS: * Immediate shut down for Pump 17D, plant engineering to inspect and rectify any damage. Further, preventative maintenance procedure should reflect this issue to prevent recurrence. * 12/01/2018 11:44:17 DAVID SMITH (INCIDENT) * The oil leak was due to a faulty oil seal. The seal has been replaced and the pump is back online. I recommend updating the maintenance procedure to include closer inspection of seals. | What was the identified cause for the oil leak in Pump 17D? | The oil leak was due to a faulty oil seal.
263 | 2020-05-31 | 30720956 | 80234562 | Intermittent power failure 30A Relay | S4CW -4RLE1 | * **************Incident Description************** * Notification 000030720956 Details * *********************************************************** * 05/31/2020 14:45:00 INCIDENT REPORT (INCIDENT REPORT) * Report submitted by: Richard Harris ENTITY\INCIDENT: * * CONDITION DESCRIPTION/LOCATION (THE INAPPROPRIATE ACTION AND ITS NEGATIVE EFFECT/INCLUDE A DETAILED LOCATION DESCRIPTION): * The operator reported intermittent power failures of 30A Relay in Node 6 during regular inspection. The issue was first observed at 1345 hrs. The Relay control was flickering and it could impact the associated equipment function. Immediate isolation was performed and temporary workaround established. No damages to the associated equipment were observed. * * ACTIVITIES, PROCESSES, PROCEDURES INVOLVED: * Regular inspection, S4.OP-AB.RE-0001, S4.OP-SO.RE-0001 * * WHY DID CONDITION HAPPEN: * Unknown - suspected electrical issue or hardware failure. * * CONSEQUENCES: * Potential equipment breakdown or loss of system controls. * * REQUIREMENTS IMPACTED: * Unavailable Relay * * ADVERSE PHYSICAL CONDITIONS: * Flickering of 30A Relay, indicating possible internal dysfunction. * * WHO WAS NOTIFIED: * Control Room, Maintenance Department * * KNOWLEDGEABLE INDIVIDUALS: * Thompson, Miller, Davis * * REPEAT OR SIMILAR CONDITION: * No * * IMMEDIATE ACTIONS AND RECOMMENDED ACTIONS: * Troubleshoot and repair 30A Relay as per standard procedures. * 06/02/2020 08:25:19 RICHARD HARRIS (INCIDENT) * The technical team performed the troubleshooting, identified a faulty capacitor in the Relay. The defective component was replaced, Relay tested for appropriate functioning and restored back into operation. The system is now stable with no further irregularities noted. | What was the immediate action taken upon discovering the intermittent power failures of the 30A Relay? | Immediate isolation was performed and temporary workaround established.
264 | 2018-04-26 | 30890124 | 80250213 | Coolant leak in the 14B Pump system | S4CW -4CWE5 | * **************Incident Description************** * Notification 000030890124 Details * *********************************************************** * 04/26/2018 07:30:00 INCIDENT REPORT (INCIDENT REPORT) * Report submitted by: Robert White * ENTITY\INCIDENT: * * CONDITION DESCRIPTION/LOCATION (THE INAPPROPRIATE ACTION AND ITS NEGATIVE EFFECT/INCLUDE A DETAILED LOCATION DESCRIPTION): * Regular inspection revealed there's a minor but a consistent coolant leak in the 14B pump system. There was visible trace of coolant around the motor housing. Leak was not present in the last regular check 2 days ago. * * ACTIVITIES, PROCESSES, PROCEDURES INVOLVED: * Regular system check and maintenance overview, under procedure S4.OP-SO.CW-0004. * * WHY DID CONDITION HAPPEN? * The reason behind the leak remains unidentified; it could possibly be natural wear and tear due to operational demands, or a failure in the sealing system. * * CONSEQUENCES: * Consistent loss of coolant could lead to a higher stress on the pump and might eventually lead to complete pump failure. * * REQUIREMENTS IMPACTED: * Normal operation, pump stability, and heat regulation. * * ADVERSE PHYSICAL CONDITIONS: * Coolant leak in Pump 14B system * * WHO WAS NOTIFIED: * Site Supervisor, Maintenance Manager * * KNOWLEDGEABLE INDIVIDUALS: * Maintenance Team, Pump Specialists * * REPEAT OR SIMILAR CONDITION: * No previous instance of such an issue has been reported. * * IMMEDIATE ACTIONS AND RECOMMENDED ACTIONS: * Isolate the pump system and initiate containment procedures. A specialised maintenance team should carry out an immediate inspection to identify the exact source of the leak. If required, replace the impaired parts or entire unit to prevent any further leaks and damages. * 04/27/2018 09:14:30 ROBERT WHITE (INCIDENT) * The specialized maintenance team stopped the leak with a temporary patch. Further investigation showed that the leak was due to a cracked seal. Orders placed for seal replacement under work order | What immediate actions were recommended following the discovery of a coolant leak in the 14B pump system? | Isolate the pump system and initiate containment procedures. A specialised maintenance team should carry out an immediate inspection to identify the exact source of the leak. If required, replace the impaired parts or entire unit to prevent any further leaks and damages.
265 | 2018-02-26 | 30987230 | 90120057 | High vibration detected on 5A Pump Motor | S1CW -1CWE5 | * **************Incident Description************** * Notification 000030987230 Details * *********************************************************** * 02/26/2018 08:25:12 INCIDENT REPORT (INCIDENT REPORT) * Report submitted by: David Williams ENTITY\INCIDENT: * * 1) CONDITION DESCRIPTION/LOCATION (THE INAPPROPRIATE ACTION AND ITS NEGATIVE EFFECT/INCLUDE A DETAILED LOCATION DESCRIPTION): * During a routine inspection at 0800 hours on 02/26/18, high vibration level were detected on the 5A Pump Motor. The unit was immediately shut down to eliminate potential damage. Might be due to misalignment or bearing wear but this requires further investigation. * * 2) ACTIVITIES, PROCESSES, PROCEDURES INVOLVED: * S1.OP.AB-CW-0001, S1.OP-SO.CW-0001 * * 3) WHY DID CONDITION HAPPEN: * As per initial findings, the main cause remains uncertain. Bearing wear or misalignment could be possible causes. * * 4) CONSEQUENCES: * Shutdown of pump might affect system and process efficiency. Continued operation with high vibration could lead to severe mechanical damages. * * 5) REQUIREMENTS IMPACTED: * Pump shutdown would impact normal operation processes. * * 6) ADVERSE PHYSICAL CONDITION: * High vibration, potential mechanical damages or efficiency loss. * * 7) WHO WAS NOTIFIED: * Control Room, Maintenance Team * * 8) KNOWLEDGEABLE INDIVIDUALS: * Johansen, Arnold, Williams * * 9) REPEAT OR SIMILAR CONDITION: * Unknown * * 10) IMMEDIATE AND RECOMMENDED ACTIONS: * Inspection and maintenance team to investigate 5A Pump Motor for possible causes of vibration and perform the necessary corrective maintenance. * * Updated: DAVID WILLIAMS 02.26.2018 09:35:22 * ------------------------------------------------------------ * 03/04/2018 08:31:26 Eleanor Johnson (Maintenance) * After detailed investigation and inspection, it | What was the initial issue detected during the routine inspection? | During a routine inspection at 0800 hours on 02/26/18, high vibration level were detected on the 5A Pump Motor.
266 | 2018-04-27 | 30865432 | 80245910 | Unexpected vibration in 18A Pump | S4CW -4CWE7 | * **************Incident Description************** * Notification 000030865432 Details * *********************************************************** * 04/27/2018 14:56:17 INCIDENT REPORT (INCIDENT REPORT) * Report submitted by: Emily Turner 321-654-9870 ENTITY\INCIDENT: * CONDITION DESCRIPTION/LOCATION (THE INAPPROPRIATE ACTION AND ITS NEGATIVE EFFECT/INCLUDE A DETAILED LOCATION DESCRIPTION): * During routine inspection, an unexpected vibration was detected in the 18A Pump. The severity of vibration elevated beyond the normal baseline and was thus immediately shut down. An intense inspection was conducted but didn't show any visible signs of damage. Temperature and pressure readings were normal when compared to other pumps in operation. * * ACTIVITIES, PROCESSES, PROCEDURES INVOLVED: * Regular pump inspections, S4.OP-AB.CW-0011 * * WHY DID CONDITION HAPPEN? * Unknown, Suspected internal malfunction * * CONSEQUENCES: * Potential pump failure, possible delay in operation * * REQUIREMENTS IMPACTED: * Shutdown and inspection of 18A Pump * * ADVERSE PHYSICAL CONDITIONS: * Vibrations in 18A Pump * * WHO WAS NOTIFIED: * Control Room, Maintenance Team, Safety Officer * * KNOWLEDGEABLE INDIVIDUALS: * Green, Hopkins, Marshal * * REPEAT OR SIMILAR CONDITION: * No, new issue * * IMMEDIATE ACTIONS AND RECOMMENDED ACTIONS: * Engineering team to further scrutinize the pump for underlying defects. * * Updated: EMILY TURNER 04.27.2018 18:53:29 -------------------------------------- * 05/01/2018 10:23:21 JOHN DOE (NUSER) * The thorough inspection revealed a misalignment between the pump and motor which resulted in the vibration. The misalignment has been corrected, and the pump is now operating smoothly following its realignment. | What immediate action was recommended when the vibration in the 18A Pump was detected? | Engineering team to further scrutinize the pump for underlying defects.
267 | 2021-09-01 | 30999921 | 80234187 | Vibrations in 16A Split Pump | S4CW -4CWE1 | * **************Incident Description************** * Notification 000030999921 Details * *********************************************************** * 01/09/2021 14:30:04 INCIDENT REPORT (INCIDENT REPORT) * Report submitted by: Steven Rodriguez ENTITY\INCIDENT: * * CONDITION DESCRIPTION/LOCATION (THE INAPPROPRIATE ACTION AND ITS NEGATIVE EFFECT/INCLUDE A DETAILED LOCATION DESCRIPTION): * Elevated levels of vibration detected on the 16A Split Pump during initial operation post maintenance service. The vibration was not present before the scheduled maintenance. Maintenance was performed under work order 80234187. * * ACTIVITIES, PROCESSES, PROCEDURES INVOLVED: * Maintenance and startup procedures. S4.OP-AB.CW-0002, S4.OP-SO.CW-0003 * * WHY DID CONDITION HAPPEN? * The cause of the elevated vibration is unknown at this time. It may be due to improper assembly during maintenance or a faulty component. * * CONSEQUENCES: * Frequent and prolonged vibrations can lead to premature mechanical failure and potential breakdown of the split pump. * * REQUIREMENTS IMPACTED: * Optimal operation of 16A Split Pump * * ADVERSE PHYSICAL CONDITIONS: * Elevated vibrations on 16A Split Pump * * WHO WAS NOTIFIED: * Maintenance Supervisor, Vibration Analyst Team * * KNOWLEDGEABLE INDIVIDUALS: * Vibration Analyst Team, Maintenance Team, Supervisor * * REPEAT OR SIMILAR CONDITION: * No, this is the first instance * * IMMEDIATE ACTIONS AND RECOMMENDED ACTIONS: * Immediate maintenance check and detailed vibration analysis are necessary. * 09/02/2021 08:19:00 JOHN DOE (INCIDENT) * After a detailed analysis, it was found that improper reassembly after maintenance caused the elevated vibration. Corrective action has been initiated and the pump is now operating within normal vibration limits. | What was the incident that occurred with the 16A Split Pump? | Elevated levels of vibration detected on the 16A Split Pump during initial operation post maintenance service. The vibration was not present before the scheduled maintenance.
268 | 2017-04-23 | 30900214 | 80231245 | Unusual Vibration in 33B Pump | S4CW -4CWE5 | * **************Incident Description************** * Notification 000030900214 Details * *********************************************************** * 04/23/2017 07:30:10 INCIDENT REPORT (INCIDENT REPORT) * Report submitted by: Richard Green ENTITY\INCIDENT: * * CONDITION DESCRIPTION/LOCATION (THE INAPPROPRIATE ACTION AND ITS NEGATIVE EFFECT/INCLUDE A DETAILED LOCATION DESCRIPTION): * During scheduled maintenance 33B Pump was exhibiting an unusual vibration. System parameters such as pressure, temperature, and current were reviewed and found to be normal. However the excessive vibration is not a known behavior for this pump experiencing such parameters. * * ACTIVITIES, PROCESSES, PROCEDURES INVOLVED: * Routine calibration and maintenance S4.OP.SO.CW-0021, S4.OP.AB.CW-0003 * * WHY DID CONDITION HAPPEN? * Unknown, a comprehensive diagnosis will be carried out to establish cause. * * CONSEQUENCES: * Unpredictable pump behavior, possible damage or failure * * REQUIREMENTS IMPACTED: * Scheduled maintenance, normal operation * * ADVERSE PHYSICAL CONDITIONS: * Excessive pump vibration * * WHO WAS NOTIFIED: * Maintenance Head, Control Room * * KNOWLEDGEABLE INDIVIDUALS: * Richard Green, Nicole Hughes, Albert Ross * * REPEAT OR SIMILAR CONDITION: * No, this situation is not previously recorded for 33B Pump. * * IMMEDIATE ACTIONS AND RECOMMENDED ACTIONS: * Initiate Abnormality Procedure S4.OP.AB.CW-0003, diagnostic check and vibration analysis to be done. * 04/26/2017 14:48:26 RICHARD GREEN (INCIDENT) * On completion of the diagnostic and vibration analysis, it was revealed that the cause of the vibration was alignment related. The pump has been serviced, realigned and tested successfully. It is now back in normal operation. | What was the identified cause of the unusual vibration of the 33B Pump? | The cause of the vibration was alignment related.
269 | 2017-03-21 | 30912345 | 80245321 | Unusual vibration from 16B Pump | S4CW -4CWE7 | * **************Incident Description************** * Notification 000030912345 Details * *********************************************************** * 03/21/2017 13:15:24 INCIDENT REPORT (INCIDENT REPORT) * Report submitted by: Emily Thompson ENTITY\INCIDENT: * * CONDITION DESCRIPTION/LOCATION (THE INAPPROPRIATE ACTION AND ITS NEGATIVE EFFECT/INCLUDE A DETAILED LOCATION DESCRIPTION): * During regular monitoring and functional test, substantial vibration was observed from 16B Pump. The vibration measurements were noted as higher than the normal threshold. However, the pump was operating within other normal parameters. Corrective actions need to be identified to mitigate the risk of potential pump failure. * * ACTIVITIES, PROCESSES, PROCEDURES INVOLVED: * Regular Functional Test and Monitoring Process: S4.OP-AB.CW-0003 * * WHY DID CONDITION HAPPEN? * Uncertain, though excessive vibration generally indicates a mechanical issue, such as misalignment or loose parts. * * CONSEQUENCES: * If not addressed, excessive vibration could result in catastrophic pump failure leading to unexpected downtime. * * REQUIREMENTS IMPACTED: * Expected pump operation and longevity. * * ADVERSE PHYSICAL CONDITIONS: * Excessive vibration at 16B Pump. * * WHO WAS NOTIFIED: * Supervisor, Maintenance Team * * KNOWLEDGEABLE INDIVIDUALS: * Mechanical Team, Wilson, Green, Taylor * * REPEAT OR SIMILAR CONDITION: * No, this is the first observation of such condition in current operating conditions. * * IMMEDIATE ACTIONS AND RECOMMENDED ACTIONS: * Initiated S4.OP-AB.CW-0003 Pump Abnormality investigation, increased monitoring frequency and planned for an urgent maintenance inspection. * 03/21/2017 15:30:57 EMILY THOMPSON (INCIDENT) * Maintenance inspection scheduled for 03/22/2017 – adjusting operations to account for potential downtime. | What immediate actions were taken in response to the excessive vibration at the 16B Pump? | Initiated S4.OP-AB.CW-0003 Pump Abnormality investigation, increased monitoring frequency and planned for an urgent maintenance inspection.
270 | 2020-12-10 | 30983045 | 90435678 | Anomaly in 30A motor vibrations post calibration | S4CW -4CWE1 | * **************Incident Description************** * Notification 000030983045 Details * *********************************************************** * 12/10/2020 16:48:46 INCIDENT REPORT (INCIDENT REPORT) * Report submitted by: Diane Williams ENTITY\INCIDENT: * * CONDITION DESCRIPTION/LOCATION (THE INAPPROPRIATE ACTION AND ITS NEGATIVE EFFECT/INCLUDE A DETAILED LOCATION DESCRIPTION): * In 09/2020, calibration of 30A Motor was performed under work order 90435262. Post-calibration checks were normal, however, the operations team has started to notice an anomaly in the vibration levels. Though the motor operation has been stable, the increased vibrations require further assessments to check for any unresolved issues during calibration or possible internal damage. * * ACTIVITIES, PROCESSES, PROCEDURES INVOLVED: * S4.OP-AB.MTR-0011, S4.OP-SO.MTR-0002 concerning regular calibration and operation of the Motor 30A. * * WHY DID CONDITION HAPPEN? * Unclear, potential calibration issues or unnoticed internal damage. * * CONSEQUENCES: * Potential wear and tear due to constant vibrations, decrease in operational efficiency, potential component failure. * * REQUIREMENTS IMPACTED: * Equipment integrity related to vibration parameters * * ADVERSE PHYSICAL CONDITIONS: * Increased vibrations from 30A Motor * * WHO WAS NOTIFIED: * Operations Supervisor, Maintenance Team * * KNOWLEDGEABLE INDIVIDUALS: * Operations Team, Maintenance Team * * REPEAT OR SIMILAR CONDITION: * No * * IMMEDIATE ACTIONS AND RECOMMENDED ACTIONS: * Perform a detailed assessment of the 30A Motor to identify the cause of vibrations. Maintenance Team needs to cross-verify the calibration implemented during the last servicing. If necessary, re-calibration may be required. * 12/13/2020 10:13:31 DIANE WILLIAMS (INCIDENT) * Thorough investigation is underway. The Maintenance Team is implementing enhanced checks to find out the cause. An update will be provided once a conclusion is reached. | What immediate actions were recommended following the abnormal vibration levels of the 30A Motor? | Perform a detailed assessment of the 30A Motor to identify the cause of vibrations. Maintenance Team needs to cross-verify the calibration implemented during the last servicing. If necessary, re-calibration may be required.
271 | 2019-04-10 | 30871128 | 80245663 | Strange vibration from 9C pump | S4CW -4CWE5 | * **************Incident Description************** * Notification 000030871128 Details * *********************************************************** * 04/10/2019 15:35:36 INCIDENT REPORT (INCIDENT REPORT) * Report submitted by: David Evans 789-123-456 ENTITY\INCIDENT: * CONDITION DESCRIPTION/LOCATION (THE INAPPROPRIATE ACTION AND ITS NEGATIVE EFFECT/INCLUDE A DETAILED LOCATION DESCRIPTION): * At approximately 1530 hours, during my shift on 04/10/2019, I noticed the 9C Pump had a noticeable vibration. The pump was running at 36 psig and a flow rate of 34%. The pump is not typically vibrating at these operational parameters. * * ACTIVITIES, PROCESSES, PROCEDURES INVOLVED: * Standard operation of pump, S4.OP-AB.CW-0002, S4.OP-SO.CW-0002. * * WHY DID CONDITION HAPPEN? * Not immediately clear, possibly due to misalignment, worn bearings or imbalances. * * CONSEQUENCES: * Vibration could accelerate wear and tear on the pump leading to possible damage or failure in the long term. * * REQUIREMENTS IMPACTED: * Normal operation of equipment. * * ADVERSE PHYSICAL CONDITIONS: * Vibration in 9C Pump detected, potential internal damage. * * WHO WAS NOTIFIED: * Shift Supervisor, Maintenance Crew * * KNOWLEDGEABLE INDIVIDUALS: * David Evans, Shift Supervisor, Engineering Staff * * REPEAT OR SIMILAR CONDITION: * No, this is the first time this condition has been reported. * * IMMEDIATE ACTIONS AND RECOMMENDED ACTIONS: * Maintenance to check pump alignment, balance and bearing condition. If no issues found, further investigation may be required. * 04/11/2019 10:21:03 DAVID EVANS (INCIDENT) * The maintenance crew inspected the pump and determined that the issue was due to worn out bearings. Bearing replacement has been scheduled. | What was the detected issue with the 9C Pump and what actions were taken as a result? | At approximately 1530 hours, during my shift on 04/10/2019, I noticed the 9C Pump had a noticeable vibration. The maintenance crew inspected the pump and determined that the issue was due to worn out bearings. Bearing replacement has been scheduled.
272 | 2018-11-28 | 30955741 | 80562789 | Elevated vibration in 10B Pump | S1CW -1CWE2 | * **************Incident Description************** * Notification 000030955741 Details * *********************************************************** * 11/28/2018 14:35:10 INCIDENT REPORT (INCIDENT REPORT) * Report submitted by: William Green ENTITY\INCIDENT: * * CONDITION DESCRIPTION/LOCATION (THE INAPPROPRIATE ACTION AND ITS NEGATIVE EFFECT/INCLUDE A DETAILED LOCATION DESCRIPTION): * During normal operation, the 10B Pump exhibited abnormal behavior indicating elevated vibration levels. This abnormal vibration was detected during routine checks and there were no external signs of damage on the 10B Pump and no previous records of similar issues. * * ACTIVITIES, PROCESSES, PROCEDURES INVOLVED: * Routine operation and check * WHY DID CONDITION HAPPEN? * The exact cause is currently unknown. Potential reasons could be operational strain, an internal malfunction, or age-related wear and tear. * * CONSEQUENCES: * The elevated vibration could lead to component fatigue and potential failure. This could disrupt normal operations and lead to costly repairs. * * REQUIREMENTS IMPACTED: * Safe operation, reliability and longevity of the pump. * * ADVERSE PHYSICAL CONDITIONS: * Elevated vibration level. * * WHO WAS NOTIFIED: * Shift Manager , Maintenance Team. * * KNOWLEDGEABLE INDIVIDUALS: * Maintenance Staff, Operations Manager. * * REPEAT OR SIMILAR CONDITION: * No, this is the first time this issue has been reported. * * IMMEDIATE ACTIONS AND RECOMMENDED ACTIONS: * The pump should be monitored closely and analyzed further to determine the cause of this elevated vibration. If the situation continues, the pump may need to be shut down for inspection and repair. * 11/29/2018 09:24:14 WILLIAM GREEN (INCIDENT) * The vibration analysis is scheduled for 30th Nov. In case the levels are above norm, the pump will be taken offline for further inspection and repairs. | What immediate and recommended actions were suggested due to the abnormal behavior of the 10B Pump? | The pump should be monitored closely and analyzed further to determine the cause of this elevated vibration. If the situation continues, the pump may need to be shut down for inspection and repair.
273 | 2018-10-22 | 30774561 | 80264907 | Unplanned 9B High Temp Alarm tripped | S4CW -4CWE5 | * **************Incident Description************** * Notification 000030774561 Details * *********************************************************** * 10/22/2018 14:46:17 INCIDENT REPORT (INCIDENT REPORT) * Report submitted by: Emily White ENTITY\INCIDENT: * * CONDITION DESCRIPTION/LOCATION (THE INAPPROPRIATE ACTION AND ITS NEGATIVE EFFECT/INCLUDE A DETAILED LOCATION DESCRIPTION): * During normal operations today, the 9B High Temp Alarm tripped unexpectedly, leading to an automatic shutdown of the 9B Pump. Upon initial inspection, a high temperature condition was confirmed on the pump motor. Despite this, no visible signs of heat damage were apparent on the external casing of the motor. * * ACTIVITIES, PROCESSES, PROCEDURES INVOLVED: * Emergency shutdown procedure in S4.OP-AB.CW-0007, Planned maintenance procedure S4.OP-PM.CW-0003. * * WHY DID CONDITION HAPPEN? * It is unclear at this time why this issue arose; the 9B pump had recently been serviced under work order 80243218 and had been operating within normal parameters until today's incident. * * CONSEQUENCES: * Potential motor damage which can lead to a reduced operational efficiency, and unplanned down time of the motor. * * REQUIREMENTS IMPACTED: * Operation of the 9B pump, cooling water system operation. * * ADVERSE PHYSICAL CONDITIONS: * High temperature alarms, possible unnoticed internal damage to pump motor. * * WHO WAS NOTIFIED: * Engineering Department, Maintenance Supervisor. * * KNOWLEDGEABLE INDIVIDUALS: * Maintenance Supervisor, Engineering team. * * REPEAT OR SIMILAR CONDITION: * Not Known, This is the first issue with the 9B pump since the last maintenance event. * * IMMEDIATE ACTIONS AND RECOMMENDED ACTIONS: * Investigate the root cause of high temperature alarm. Verification required to validate sensor operation, and detailed inspection of motor internals. Update S4.OP-AB.CW-0007 and S4.OP-PM.CW-0003 accordingly based on findings. * 10/26/ | Why did the 9B High Temp Alarm of the pump trip unexpectedly? | It is unclear at this time why this issue arose; the 9B pump had recently been serviced under work order 80243218 and had been operating within normal parameters until today's incident.
274 | 2019-03-17 | 30903175 | 90251911 | Unusual vibration in 11B Pump Motor | S4CW -4CWE5 | * **************Incident Description************** * Notification 000030903175 Details * *********************************************************** * 03/17/2019 14:32:47 INCIDENT REPORT (INCIDENT REPORT) * Report submitted by: David Greene ENTITY\INCIDENT: * CONDITION DESCRIPTION/LOCATION (THE INAPPROPRIATE ACTION AND ITS NEGATIVE EFFECT/INCLUDE A DETAILED LOCATION DESCRIPTION): * On 03/17/2019, during a scheduled monitoring, an unusual vibration was detected in the 11B Pump Motor. The vibration levels were recorded, which were higher than the acceptable levels. The Pump was temporarily shut down to avoid any potential damage or adverse event. * ACTIVITIES, PROCESSES, PROCEDURES INVOLVED: * Routine vibration monitoring activity under S4.OP-AB.CW-0003. * WHY DID CONDITION HAPPEN? * Not known at this point. This kind of vibration could be due to misalignment, imbalance, bearing failure or looseness. * CONSEQUENCES: * Possible Motor damage, reduced efficiency, risk of failure during operation. * REQUIREMENTS IMPACTED: * Regular operation, pump availability * ADVERSE PHYSICAL CONDITIONS: * High Vibration levels on pump * WHO WAS NOTIFIED: * Operations Supervisor, Maintenance Team * KNOWLEDGEABLE INDIVIDUALS: * Clark, Watson, Rodriguez * REPEAT OR SIMILAR CONDITION: * Not Known. * IMMEDIATE ACTIONS AND RECOMMENDED ACTIONS: * Initiated pump abnormality report under S4.OP-AB.CW-0003. Further investigation is required to identify the root-cause. Maintenance team should check for possible mechanical issues like misalignment, imbalance or bearing failure. * 03/20/2019 09:24:23 DAVID GREENE (INCIDENT) * The pump has been inspected and no significant mechanical issues were found. The motor has been re-balanced and is now running with normal vibration levels. The cause of the vibration could not be definitively determined. Scheduled more frequent vibration monitoring. | What immediate and recommended actions were taken after the unusual vibrations in the 11B Pump Motor were detected? | Initiated pump abnormality report under S4.OP-AB.CW-0003. Further investigation is required to identify the root-cause. Maintenance team should check for possible mechanical issues like misalignment, imbalance or bearing failure.
275 | 2018-09-13 | 30963410 | 80214391 | PIPE LEAK AT UNIT 1 TOWER | S1CW -1CWE4-PIP | * **************Incident Description************** * Notification 000030936410 Details * *********************************************************** * 09/13/2018 10:32:26 INCIDENT REPORT (INCIDENT REPORT) * Report submitted by: Jeff Thompson 234-567-8910 ENTITY\INCIDENT: * CONDITION DESCRIPTION/LOCATION (THE INAPPROPRIATE ACTION AND ITS NEGATIVE EFFECT/INCLUDE A DETAILED LOCATION DESCRIPTION): * At 0830 on 9/13/18 the control room reported an unexpected water leakage at the unit 1 cooling tower. The leak was from a pipe section supplying water to the tower. Immediate action taken was to bypass the pipe route and mitigate the leakage. * * ACTIVITIES, PROCESSES, PROCEDURES INVOLVED: * S1.OP.MA.CW-0002, S1.PR.SO.CW-0007 * * WHY DID CONDITION HAPPEN? * Unknown, further investigation required to determine the cause. * * CONSEQUENCES: * Potential reduction in cooling efficiency and damage to surrounding infrastructure. * * REQUIREMENTS IMPACTED: * Normal operation of the cooling tower. * * ADVERSE PHYSICAL CONDITIONS: * Leak from pipe * * WHO WAS NOTIFIED: * Control Room, Maintenance Team * * KNOWLEDGEABLE INDIVIDUALS: * Staff Engineer, Jones, Williams * * REPEAT OR SIMILAR CONDITION: * No * * IMMEDIATE ACTIONS AND RECOMMENDED ACTIONS: * Reroute water supply, isolate and repair the leak. * 09/15/2018 15:52:00 JEFF THOMPSON (INCIDENT) * Further investigation revealed a crack in the pipe leading to water leakage. Recommend replacing the faulty pipe. | What was the immediate action taken when the unexpected water leakage at the unit 1 cooling tower was reported? | Immediate action taken was to bypass the pipe route and mitigate the leakage.
276 | 2019-04-19 | 31048136 | 80516249 | Unexpected Voltage Drop in Motor 3C | S4CW -4CWE2 | * **************Incident Description************** * Notification 000031048136 Details * *********************************************************** * 04/19/2019 14:16:45 INCIDENT REPORT (INCIDENT REPORT) * Report submitted by: Kim Reynolds 987-654-3210 ENTITY\INCIDENT: * CONDITION DESCRIPTION/LOCATION (THE INAPPROPRIATE ACTION AND ITS NEGATIVE EFFECT/INCLUDE A DETAILED LOCATION DESCRIPTION): * During morning operations, the motor designated 3C exhibited an unexpected drop in supply voltage. Preliminary checks on other motors showed stable voltage. Power supply for 3C Motor situated in Unit 4 Control Room needs evaluation and rectification. * * ACTIVITIES, PROCESSES, PROCEDURES INVOLVED: * Daily monitoring and equipment check * WHY DID CONDITION HAPPEN? * Potentially due to an internal issue or deformity in circuitry wiring. * * CONSEQUENCES: * Possible motor failure, potential electrical hazards, impact on plant safety and efficiency. * * REQUIREMENTS IMPACTED: * Safety and operational efficiency of the plant * * ADVERSE PHYSICAL CONDITIONS: * Sudden drop in supply voltage * * WHO WAS NOTIFIED: * Supervisor/System Analyst Team * * KNOWLEDGEABLE INDIVIDUALS: * System Analyst Team * * REPEAT OR SIMILAR CONDITION: * No, this is the first-time occurrence of such a situation * * IMMEDIATE ACTIONS AND RECOMMENDED ACTIONS: * Immediate isolation of motor 3C, comprehensive electrical and functionality audit, rectification as required. * 04/22/2019 10:22:27 KIM REYNOLDS (INCIDENT) * The audit report confirms internal wiring issue was the cause. Corrections were implemented and motor 3C is topping expected performance parameters. Regular checks recommended. | What was the cause of the sudden drop in supply voltage in motor 3C? | The audit report confirms internal wiring issue was the cause.
277 | 2019-09-30 | 30837561 | 80245836 | R3CB High Pressure Sensor Failure | S3CB -3CBE5 | * **************Incident Description************** * Notification 000030837561 Details * *********************************************************** * 09/30/2019 07:15:03 INCIDENT REPORT (INCIDENT REPORT) * Report submitted by: Emily Wilson 124-567-8912 ENTITY\INCIDENT: * CONDITION DESCRIPTION/LOCATION (THE INAPPROPRIATE ACTION AND ITS NEGATIVE EFFECT/INCLUDE A DETAILED LOCATION DESCRIPTION): * During routine operational checks, R3CB Pump's high pressure sensor failed to show any readings. The pump was immediately shut down and an unusual increase in pump temperature was reported. This is unanticipated as sensor was replaced just a month ago under work order 80238702. * * ACTIVITIES, PROCESSES, PROCEDURES INVOLVED: * Daily operational maintenance check * * WHY DID CONDITION HAPPEN? * Cause is not immediately known. Speculations range from a faulty replacement sensor to possible pump internal malfunctions leading to pressuring failures. * * CONSEQUENCES: * Inability to measure pressure could result in pump failure and hazards. Delay in regular operations due to investigation and maintenance. * * REQUIREMENTS IMPACTED: * Normal operation * * ADVERSE PHYSICAL CONDITIONS: * Failed pressure sensor, abnormal temperature increase in pump. * * WHO WAS NOTIFIED: * Supervisor, Maintenance and Quality Control Team * * KNOWLEDGEABLE INDIVIDUALS: * Quality Control Team, Maintenance Team * * REPEAT OR SIMILAR CONDITION: * No * * IMMEDIATE ACTIONS AND RECOMMENDED ACTIONS: * Immediate replacement of the sensor. Complete systems check on the pump followed by rigorous testing before putting it back in operation. * 09/30/2019 11:30:47 EMILY WILSON (INCIDENT) * Maintenance team has replaced the sensor and complete checks are being performed. Pump is anticipated to be operational within the next 5 hours. We have initiated an investigation to ascertain the exact cause of the sensor failure. | What immediate actions were recommended following the R3CB Pump incident? | Immediate replacement of the sensor. Complete systems check on the pump followed by rigorous testing before putting it back in operation.
278 | 2018-11-25 | 30946231 | 80251791 | High power consumption by 33B pump | S6CW -6CWE7 | * **************Incident Description************** * Notification 000030946231 Details * *********************************************************** * 11/25/2018 07:30:00 INCIDENT REPORT (INCIDENT REPORT) * Report submitted by: David Taylor ENTITY\INCIDENT: * * CONDITION DESCRIPTION/LOCATION (THE INAPPROPRIATE ACTION AND ITS NEGATIVE EFFECT/INCLUDE A DETAILED LOCATION DESCRIPTION): * At 0730 on 11/25/18, it was observed that 33B Pump was consuming much more power than usual. This could indicate an underlying issue like clogging or seal leakage. S6.OP-AB.CW-0001 Pump Power Consumption Tracking was initiated to monitor the abnormality. * * ACTIVITIES, PROCESSES, PROCEDURES INVOLVED: * S6.OP.AB-CW-0001, S6.OP-SO.CW-0001 * * WHY DID CONDITION HAPPEN: * The exact cause is not known at this time, further investigation required. Previous incidents involved clogging and seal leakage. * * CONSEQUENCES: * High power consumption, risk of pump failure * * REQUIREMENTS IMPACTED: * Increased energy consumption, potential disruption of normal operation * * ADVERSE PHYSICAL CONDITION: * High power consumption of 33B Pump * * WHO WAS NOTIFIED: * Control Room, Maintenance Department * * KNOWLEDGEABLE INDIVIDUALS: * Williams, Green, Taylor * * REPEAT OR SIMILAR CONDITION: * Not known at this time * * IMMEDIATE AND RECOMMENDED ACTIONS: * Activate SOP S6.OP.AB-CW-0001, continue with power consumption monitoring, perform internal inspection to ascertain cause. * * Updated: DAVID TAYLOR 11.25.2018 10:15:28 * ------------------------------------------------------------ * 11/29/2018 07:30:43 LUCY PARKER (NUSER) * Upon investigation, it was revealed that seal leakage was causing the higher power consumption. The Pump 33B was shut down for maintenance and the defective seals replaced. The pump is now back to | What was the observed problem with the Pump 33B and what action was taken? | At 0730 on 11/25/18, it was observed that 33B Pump was consuming much more power than usual. This could indicate an underlying issue like clogging or seal leakage. S6.OP-AB.CW-0001 Pump Power Consumption Tracking was initiated to monitor the abnormality. Upon investigation, it was revealed that seal leakage was causing the higher power consumption. The Pump 33B was shut down for maintenance and the defective seals replaced.
279 | 2019-09-15 | 30854762 | 80258712 | 25C Pump sudden pressure drop | S5CW -5CWE8 | * **************Incident Description************** * Notification 000030854762 Details * *********************************************************** * 09/15/2019 15:34:20 INCIDENT REPORT (INCIDENT REPORT) * Report submitted by: Emily Johnson ENTITY\INCIDENT: * * CONDITION DESCRIPTION/LOCATION (THE INAPPROPRIATE ACTION AND ITS NEGATIVE EFFECT/INCLUDE A DETAILED LOCATION DESCRIPTION): * During a routine operational check, a sudden drop in pressure was noted at the 25C Pump. This is unexpected and does not align with normal operational parameters. This condition had been identified before as a potential for pump damage if not serviced immediately. * * ACTIVITIES, PROCESSES, PROCEDURES INVOLVED: * Regular operational checks. * * WHY DID CONDITION HAPPEN? * The cause is not confirmed yet, possible issues could be a valve malfunction or clogged pipelines. * * CONSEQUENCES: * Potential risk of pump failure leading to operational downtime. * * REQUIREMENTS IMPACTED: * Continual operation, Maintenance intervention required. * * ADVERSE PHYSICAL CONDITIONS: * Drop in pump pressure, potential pump damage * * WHO WAS NOTIFIED: * Control Room, Maintenance Team * * KNOWLEDGEABLE INDIVIDUALS: * Peterson, McDonald, Emily Johnson * * REPEAT OR SIMILAR CONDITION: * Yes, It was identified before in a similar condition. * * IMMEDIATE ACTIONS AND RECOMMENDED ACTIONS: * Isolate the pump, Inform maintanace team for immediate inspection * 09/15/2019 17:34:45 EMILY JOHNSON (INCIDENT) * Based on operational data, the drop in pressure is not related to valve operation, Believe to be due to blockage in the pipeline. Immediate action is taken by the maintenance team to replace blocked segment. Now, pump is back in operation. Recommend increased frequency checks to monitor the condition. | What was the initial suspected cause of the drop in pressure at the 25C Pump, and what was the actual cause? | The cause is not confirmed yet, possible issues could be a valve malfunction or clogged pipelines. Based on operational data, the drop in pressure is not related to valve operation, Believe to be due to blockage in the pipeline.
280 | 2019-12-16 | 30987251 | 90123105 | Vibration detected in 10D Pump | S4CW -4CWE8 | * **************Incident Description************** * Notification 000030987251 Details * *********************************************************** * 12/16/2019 14:31:22 INCIDENT REPORT (INCIDENT REPORT) * Report submitted by: Laura Smith 987-654-3210 ENTITY\INCIDENT: * CONDITION DESCRIPTION/LOCATION (THE INAPPROPRIATE ACTION AND ITS NEGATIVE EFFECT/INCLUDE A DETAILED LOCATION DESCRIPTION): * During routine checks, it was noticed that the 10D Pump was showing signs of unusual vibration during operations. The vibrations were causing an increase in noise levels at the site. Further analysis of the operational data showed no significant overloads or dips, which could suggest an internal fault or debris caught within the pump mechanism. * * ACTIVITIES, PROCESSES, PROCEDURES INVOLVED: * Routine check, Vibration analysis, noise level analysis * * WHY DID CONDITION HAPPEN? * Unconfirmed, possible internal damage or debris. * * CONSEQUENCES: * Possible damage to pump, decreased efficiency, disturbance due to increased noise. * * REQUIREMENTS IMPACTED: * Noise level standards, efficient pump operation * * ADVERSE PHYSICAL CONDITIONS: * High noise level, increased pump vibration * * WHO WAS NOTIFIED: * Maintenance supervisor, INCIDENT TEAM * * KNOWLEDGEABLE INDIVIDUALS: * Jeff Martin, Mike Ross, Sarah Thompson * * REPEAT OR SIMILAR CONDITION: * No, this is the first occurrence on this pump. * * IMMEDIATE ACTIONS AND RECOMMENDED ACTIONS: * Proceed with a maintenance inspection of pump to ascertain the cause of vibrations, conduct a detailed analysis to identify the issue. If necessary, replace or repair pump components. * 12/16/2019 16:34:55 LAURA SMITH (INCIDENT) * Based on initial inspection, the pump has been temporarily shut down for safety and further investigation on the vibrations is in progress. Plan for detailed investigation has been submitted. | What were the immediate actions taken after noticing the unusual vibration in the pump? | Proceed with a maintenance inspection of pump to ascertain the cause of vibrations, conduct a detailed analysis to identify the issue. If necessary, replace or repair pump components. Based on initial inspection, the pump has been temporarily shut down for safety and further investigation on the vibrations is in progress. Plan for detailed investigation has been submitted.
281 | 2022-01-08 | 30987623 | 80234567 | Excessive Vibration in 16B Pump Motor | S4CW -4CWE2 | * **************Incident Description************** * Notification 000030987623 Details * *********************************************************** * 01/08/2022 14:35:21 INCIDENT REPORT (INCIDENT REPORT) * Report submitted by: Edward Gomez ENTITY\INCIDENT: * * CONDITION DESCRIPTION/LOCATION (THE INAPPROPRIATE ACTION AND ITS NEGATIVE EFFECT/INCLUDE A DETAILED LOCATION DESCRIPTION): * On 1/8/22 at 1420 hrs, the operator reported excessive vibration in the 16B Pump motor. The pump was immediately shut down from Unit 4 Control Room. System inspection revealed no external sign of damage but the improper vibration could cause internal mechanical issues. Maintenance personnel was notified and S4.OP-AB.CW-0002 Pump Abnormality was initiated promptly. * * ACTIVITIES, PROCESSES, PROCEDURES INVOLVED: * S4.OP.AB-CW-0002, S4.OP-SO.CW-0001 * * WHY DID CONDITION HAPPEN: * Unknown, initial checks did not indicate any visible mechanical issue. * * CONSEQUENCES: * Potential mechanical damage could reduce the operational efficiency of the unit. * * REQUIREMENTS IMPACTED: * Pump availability * * ADVERSE PHYSICAL CONDITION: * Excessive vibration from 16B Pump motor * * WHO WAS NOTIFIED: * Control Room, Maintenance Department * * KNOWLEDGEABLE INDIVIDUALS: * Martinez, Davis, Thompson * * REPEAT OR SIMILAR CONDITION: * Unknown * * IMMEDIATE ACTIONS AND RECOMMENDED ACTIONS: * Thorough inspection and possibly complete overhauling of 16B Pump Motor if necessary. * * Updated: EDWARD GOMEZ 01.08.2022 15:15:34 * ----------------------------------------------------------- * 01/18/2022 09:20:31 JOHN DOE (NUSER) * The inspection revealed a misalignment of the motor shaft. Minor repairs followed by reassembly was conducted. A routine check indicated the pump is now running smoothly with no excessive vibration. | What immediate action was recommended after the detection of excessive vibration from the 16B Pump motor? | Thorough inspection and possibly complete overhauling of 16B Pump Motor if necessary.
282 | 2019-09-17 | 30778965 | 80233457 | Fluctuating voltage in 17D Motor | S3CW -3CWE7-MTRF | * **************Incident Description************** * Notification 000030778965 Details * *********************************************************** * 09/17/2019 11:30:00 INCIDENT REPORT (INCIDENT REPORT) * Report submitted by: Thomas Gray ENTITY\INCIDENT: * * CONDITION DESCRIPTION/LOCATION (THE INAPPROPRIATE ACTION AND ITS NEGATIVE EFFECT/INCLUDE A DETAILED LOCATION DESCRIPTION): * During the daily operational check, the 17D Motor showed varying voltage readings. Typically, the voltage should remain steady as it's regulated by its circuits. The fluctuation was detected at around 1115 hours and further on-site inspection was immediately initiated. * * ACTIVITIES, PROCESSES, PROCEDURES INVOLVED: * Daily Monitoring and inspection. * WHY DID CONDITION HAPPEN? * The exact cause is yet unknown. Potentially due to worn-out circuits or faulty wiring. * * CONSEQUENCES: * The system may fail to function optimally. This can affect operations and potentially damage the motor if left unattended. * * REQUIREMENTS IMPACTED: * Operational Standards of Machinery * * ADVERSE PHYSICAL CONDITIONS: * Erratic voltage readings, potential circuit malfunction. * * WHO WAS NOTIFIED: * Supervisor and Maintenance Team * * KNOWLEDGEABLE INDIVIDUALS: * Supervisor, Maintenance Team, Johnson, Rita * * REPEAT OR SIMILAR CONDITION: * First occurrence of such a condition in this motor. Earlier, a similar incident was detected in 8A Motor. * * IMMEDIATE ACTIONS AND RECOMMENDED ACTIONS: * System to be under close monitoring and immediate inspection required by the maintenance team. A potential shutdown and complete systems check might be needed if the issue persists. * 09/19/2019 15:27:40 TOM GRAY (INCIDENT) * The maintenance team conducted a detailed inspection and identified the cause of the voltage fluctuation as a faulty capacitor in the circuit board. The capacitor was replaced, and the voltages are now steady. Further monitoring will be taken up to ensure stability. | What was the solution implemented to fix the fluctuating voltage readings of the 17D Motor? | The maintenance team conducted a detailed inspection and identified the cause of the voltage fluctuation as a faulty capacitor in the circuit board. The capacitor was replaced, and the voltages are now steady.
283 | 2018-12-14 | 30978542 | 90231587 | 8A PC malfunction detected | S4PC -4PCB1 | * **************Incident Description************** * Notification 000030978542 Details * *********************************************************** * 12/14/2018 14:35:18 INCIDENT REPORT (INCIDENT REPORT) * Report submitted by: Emily Hill * * 1) CONDITION DESCRIPTION/LOCATION (THE INAPPROPRIATE ACTION AND ITS NEGATIVE EFFECT/INCLUDE A DETAILED LOCATION DESCRIPTION): * During a routine system status check at 1435 hours, PC 8A was found to have a malfunctioning indicator light. Subsequent system diagnostics revealed that the malfunctioning light was due to a potential fan failure. The malfunction could lead to system overheating and, subsequently, potential shutdown of PC 8A. * * 2) ACTIVITIES, PROCESSES, PROCEDURES INVOLVED: * Routine System Check * * 3) WHY DID CONDITION HAPPEN: * Unplanned equipment failure, reasons for which are being investigated. * * 4) CONSEQUENCES: * Potential shutdown of 8A PC, loss of system capabilities. * * 5) REQUIREMENTS IMPACTED: * Continued uninterrupted operation of PC 8A. * * 6) ADVERSE PHYSICAL CONDITIONS: * Fan failure leading to potential overheating and shutdown of 8A PC. * * 7) WHO WAS NOTIFIED: * System Supervisors, IT department * * 8) KNOWLEDGEABLE INDIVIDUALS: * Emily Hill, Ryan Foster - IT Supervisor * * 9) REPEAT OR SIMILAR CONDITION: * No * * 10) IMMEDIATE ACTIONS AND RECOMMENDED ACTIONS: * Team is currently conducting detailed investigation of the root cause, in order to repair or replace the fan, if required. * 12/14/2018 16:47:10 EMILY HILL (INCIDENT) * IT department is engaged and will take over investigation and repair. 8A PC remains offline as a safety measure until the situation is rectified. | Who was notified about the malfunctioning of PC 8A? | System Supervisors, IT department
284 | 2022-12-16 | 30994515 | 90035464 | 5A Valve failure | S3CW -3CWE5 | * **************Incident Description************** * Notification 000030994515 Details * *********************************************************** * 12/16/2022 11:23:50 INCIDENT REPORT (INCIDENT REPORT) * Report submitted by: Olivia King ENTITY\INCIDENT: * * CONDITION DESCRIPTION/LOCATION (THE INAPPROPRIATE ACTION AND ITS NEGATIVE EFFECT/INCLUDE A DETAILED LOCATION DESCRIPTION): * The 5A Valve was detected with failure during regular maintenance check. The valve was stuck and it was not responding to the input from control room. The valve was manually shut down, and a noticeable quantity of fluid was observed near the valve. Valve malfunction appeared to be mechanical and not electrical. Inspection continued to identify any other abnormalities. * * ACTIVITIES, PROCESSES, PROCEDURES INVOLVED: * S3.OP.AB-CW-0005, S3.OP-SO.CW-0002 * * WHY DID CONDITION HAPPEN: * Unknown. No previous record of similar failure for 5A Valve. * * CONSEQUENCES: * Potential fluid leakage, loss of valve control and possible impact on system efficiency. * * REQUIREMENTS IMPACTED: * Proper valve operation is key to system continuity and performance. * * ADVERSE PHYSICAL CONDITIONS: * Potential internal damage to valve, fluid leakage * * WHO WAS NOTIFIED: * Control Room, Maintenance Department * * KNOWLEDGEABLE INDIVIDUALS: * Green, Cox, Nielson * * REPEAT OR SIMILAR CONDITION: * No * * IMMEDIATE ACTIONS AND RECOMMENDED ACTIONS: * 5A Valve requires full inspection and maintenance service. If the situation is not improved, valve replacement should be considered. * 12/16/2022 15:35:10 OLIVIA KING (INCIDENT) * Further examination of 5A Valve is necessary. Until full diagnostic is achieved, the valve should remain manually shut down to prevent any potential hazard. | What immediate actions were recommended following the incident with the 5A valve? | 5A Valve requires full inspection and maintenance service. If the situation is not improved, valve replacement should be considered.
285 | 2018-09-10 | 30733050 | 80211245 | Unexpected pressure drop in 13B pump | S1PW -1PWE7-EVGD | * **************Incident Description************** * Notification 000030733050 Details * *********************************************************** * 09/10/2018 07:24:17 INCIDENT REPORT (INCIDENT REPORT) * Report submitted by: Emily Wilson ENTITY\INCIDENT: * * CONDITION DESCRIPTION/LOCATION (THE INAPPROPRIATE ACTION AND ITS NEGATIVE EFFECT/INCLUDE A DETAILED LOCATION DESCRIPTION): * During the 6 am inspection, the operator identified an unexpected pressure drop in the 13B pump. The pump was shut down for imminent inspection. The shutdown process followed was in accordance with S1.OP-AB.PW-0002 Pump Emergency Shutdown. Upon checking other output parameters, no obvious mechanical defects or leaks were noted. * * ACTIVITIES, PROCESSES, PROCEDURES INVOLVED: * Regular inspection, S1.OP-AB.PW-0002 * * WHY DID CONDITION HAPPEN? * Unidentified, possibly due to internal wear or valve malfunction. * * CONSEQUENCES: * An unexpected drop in pressure might lead to inefficient operations and potential system failure if not addressed swiftly. * * REQUIREMENTS IMPACTED: * Regular operation and system efficiency * * ADVERSE PHYSICAL CONDITIONS: * Sudden pressure drop in 13B pump * * WHO WAS NOTIFIED: * Supervisor, Maintenance Team * * KNOWLEDGEABLE INDIVIDUALS: * Maintenance Team, Technical Engineer * * REPEAT OR SIMILAR CONDITION: * No, this is the first report of such an incident on this pump. * * IMMEDIATE AND RECOMMENDED ACTIONS: * Thorough inspection of the 13B pump, specifically focusing on the internal components and the valves. * 09/12/2018 15:24:48 EMILY WILSON (INCIDENT) * Upon inspection, it was found that a valve was faulty, causing the pressure drop. The faulty valve has been replaced and the pump is now functioning at normal pressure levels. | What was the cause of the unexpected pressure drop in the 13B pump during the inspection? | Upon inspection, it was found that a valve was faulty, causing the pressure drop. The faulty valve has been replaced and the pump is now functioning at normal pressure levels.
286 | 2019-04-10 | 30857263 | 80256390 | Elevated cooling tower vibration detected | S3CW -3CWE9 | * **************Incident Description************** * Notification 000030857263 Details * *********************************************************** * 04/10/2019 15:31:10 INCIDENT REPORT (INCIDENT REPORT) * Report submitted by: Patrick Harris ENTITY\INCIDENT: * * CONDITION DESCRIPTION/LOCATION (THE INAPPROPRIATE ACTION AND ITS NEGATIVE EFFECT/INCLUDE A DETAILED LOCATION DESCRIPTION): * On 4/10/19, escalated vibration detection observed in Cooling Tower module by automated monitoring system. Tower was operating at normal parameters. Engineering inspection did not reveal any visible damage on tower structure or motor. * * ACTIVITIES, PROCESSES, PROCEDURES INVOLVED: * S3.OP.AB-CW-0001, S3.OP-SO.CW-0001 * * WHY DID CONDITION HAPPEN? * Unknown, further investigation is required to determine root cause. * * CONSEQUENCES: * Potential damage to tower and/or motor, reduced efficiency, possible shutdown * * REQUIREMENTS IMPACTED: * Cooling tower operation * * ADVERSE PHYSICAL CONDITIONS: * High vibration level from cooling tower motor * * WHO WAS NOTIFIED: * Supervisor, Engineering team, Incident response team * * KNOWLEDGEABLE INDIVIDUALS: * Supervisor, Murphy, Green, Foster * * REPEAT OR SIMILAR CONDITION: * No * * IMMEDIATE ACTIONS AND RECOMMENDED ACTIONS: * Suspended operation of tower until further investigation can be conducted. Engineering team tasked to assess and determine root cause. * 04/12/2019 10:00:45 PATRICK HARRIS (INCIDENT) * Preliminary assessment indicates vibration may have been due to misalignment of motor couplings. Engineering team currently performing complete assessment to confirm. | What immediate actions were taken following the detection of increased vibrations in the cooling tower? | Suspended operation of tower until further investigation can be conducted. Engineering team tasked to assess and determine root cause.
287 | 2016-12-15 | 30760158 | 80293746 | Unusual vibrations from 30B Pump | S4CW -4CWE7 | * **************Incident Description************** * Notification 000030760158 Details * *********************************************************** * 12/15/2016 11:35:00 INCIDENT REPORT (INCIDENT REPORT) * Report submitted by: Daniel Wilson ENTITY\INCIDENT: * * CONDITION DESCRIPTION/LOCATION (THE INAPPROPRIATE ACTION AND ITS NEGATIVE EFFECT/INCLUDE A DETAILED LOCATION DESCRIPTION): * At 1117hrs, the 30B Pump showed unusual vibrations during the routine check by operations personnel. The pump was immediately shut down and a notification was made to the control room. Initial inspection did not show any signs of mechanical failure. S4.OP.AB.CW-0007 pump shut-off protocol was initiated due to the abnormal vibration of 30B Pump. * * ACTIVITIES, PROCESSES, PROCEDURES INVOLVED: * S4.OP-AF.CW-0007, S4.OP.BO.CW-0015 * * WHY DID CONDITION HAPPEN: * Unknown, however similar incidents with high vibration have been noted with other pumps. * * CONSEQUENCES: * High vibrations can cause wear and tear resulting in reduced efficiency or total failure of the pump. * * REQUIREMENTS IMPACTED: * Pump operation and process continuity * * ADVERSE PHYSICAL CONDITIONS: * Unusual vibrations from 30B Pump * * WHO WAS NOTIFIED: * Control Room, Maintenance Team, Safety Officer * * KNOWLEDGEABLE INDIVIDUALS: * Wilson, Gomez, Kowalski * * REPEAT OR SIMILAR CONDITION: * Yes, but in different pump models * * IMMEDIATE ACTIONS AND RECOMMENDED ACTIONS: * Maintenance team to investigate 30B Pump, consider inspection of similar pump models for potential issues. * * Updated: DAVID SMITH 12.15.2016 14:45:27 * ------------------------------------------------------------ * 12/19/2016 08:36:51 AMY LEE (INCIDENT) * Investigation revealed the excessive vibration was due to an improperly balanced impeller. The pump was serviced, the | What was the cause of the unusual vibrations in the 30B Pump? | The excessive vibration was due to an improperly balanced impeller.
288 | 2016-10-05 | 30765028 | 80256623 | Vibration Issue in A3 Motor Pump | S1CWE -3CWJ5 | * **************Incident Description************** * Notification 000030765028 Details * *********************************************************** * 10/05/2016 14:22:11 INCIDENT REPORT (INCIDENT REPORT) * Report submitted by: Thomas Smith ENTITY\INCIDENT: * * CONDITION DESCRIPTION/LOCATION (THE INAPPROPRIATE ACTION AND ITS NEGATIVE EFFECT/INCLUDE A DETAILED LOCATION DESCRIPTION): * At 1315 on 10/05/16, operators witnessed a high vibration alarm on A3 Motor Pump. There was no significant change in the equipment load or operational parameters during this time. The maintenance crew was called immediately to inspect and possibly troubleshoot the issue. The equipment was later gradually powered down after confirming no critical service from the unit. * * ACTIVITIES, PROCESSES, PROCEDURES INVOLVED: * The maintenance team followed S1.OP.AB-EM-0005 Procedure under such scenarios. * * WHY DID CONDITION HAPPEN? * The root cause of high vibrations in A3 Motor Pump is yet to be determined. Initial inspection hinted at possible alignment issues. * * CONSEQUENCES: * Unexpected shutdown of the unit. Increase in operational risk and Maintenance corrective actions. * * REQUIREMENTS IMPACTED: * Routine operation was impacted due to sudden shutdown. * * ADVERSE PHYSICAL CONDITIONS: * High vibrations in the A3 Motor Pump. * * WHO WAS NOTIFIED: * Operations Manager, and the Maintenance team. * * KNOWLEDGEABLE INDIVIDUALS: * Mark Robins and the Maintenance team. * * REPEAT OR SIMILAR CONDITION: * Never before. The A3 unit has been operating smoothly without any historical issues of high vibrations. * * IMMEDIATE ACTIONS AND RECOMMENDED ACTIONS: * Alignments checks, internal inspections for any mechanical failure are recommended. * 10/08/2016 10:08:35 JOHN DOE (INCIDENT) * Conducted a thorough investigation. The root cause was found to be an improper rotor alignment during the last servicing. The alignment was corrected, and the unit is now back online with no | What was the immediate action taken when the high vibration alarm was observed in the A3 Motor Pump? | The maintenance crew was called immediately to inspect and possibly troubleshoot the issue. The equipment was later gradually powered down after confirming no critical service from the unit.
289 | 2021-07-20 | 31001287 | 81031299 | 32B Pump Motor Vibration | S4CW -4CWE10 | * **************Incident Description************** * Notification 000031001287 Details * *********************************************************** * 07/20/2021 14:45:00 INCIDENT REPORT (INCIDENT REPORT) * Report submitted by: Mark Hampton ENTITY\INCIDENT: * * CONDITION DESCRIPTION/LOCATION (THE INAPPROPRIATE ACTION AND ITS NEGATIVE EFFECT/INCLUDE A DETAILED LOCATION DESCRIPTION): * During 12:00 observation rounds, the field operator noticed an increased vibration on the 32B pump motor. Assessment of the vibration level revealed it was comparatively higher than other pumps. 32B pump was shut down for immediate inspection. A slight increase in operating temperature was also noted. * * ACTIVITIES, PROCESSES, PROCEDURES INVOLVED: * Routine operational review and S4.OP-AB.CW-0007, S4.OP-SO.CW-0008. * * WHY DID CONDITION HAPPEN? * The cause of the increased vibration is unknown. Potential causes can be wear and tear or internal mechanical issues. * * CONSEQUENCES: * Potential for the motor to fail. Temporary unavailability of pump for operation would impact the process. * * REQUIREMENTS IMPACTED: * Operational requirement for all pumps are to remain within regulatory tolerance levels of vibration. * * ADVERSE PHYSICAL CONDITIONS: * Increased motor's vibration. * * WHO WAS NOTIFIED: * Operations supervisor, maintenance team. * * KNOWLEDGEABLE INDIVIDUALS: * Maintenance team, Operations supervisor, Field Engineer. * * REPEAT OR SIMILAR CONDITION: * No, this specific issue has not been identified before. * * IMMEDIATE ACTIONS AND RECOMMENDED ACTIONS: * Shut down of 32B pump motor. Maintenance team to conduct an investigation into the cause of increase in vibration. * 07/23/2021 09:34:48 LUCY HART (INCIDENT) * Investigation determined that the vibration came from an imbalance in the rotor. The motor was rebalanced, inspected and tested properly. The pump has been returned to service with normal operation. | What was done as an immediate response to the increased vibration of the 32B pump motor? | Shut down of 32B pump motor. Maintenance team to conduct an investigation into the cause of increase in vibration.
290 | 2017-10-30 | 30978520 | 80255834 | Vibration detected in 20B compressor | S1AC -1ACE7 | * **************Incident Description************** * Notification 000030978520 Details * *********************************************************** * 10/30/2017 08:29:00 INCIDENT REPORT (INCIDENT REPORT) * Report submitted by: George Williams INCIDENT\COMPRESSION TEST: * * CONDITION DESCRIPTION/LOCATION (THE INAPPROPRIATE ACTION AND ITS NEGATIVE EFFECT/INCLUDE A DETAILED LOCATION DESCRIPTION): * During a routine health check at 0820 hrs, an unusual vibration was detected from the 20B compressor. Early condition monitoring has indicated a deviation in vibration spectral data. In comparison with other compressors in operation, the vibration seems abnormal. * * ACTIVITIES, PROCESSES, PROCEDURES INVOLVED: * Condition monitoring * * WHY DID CONDITION HAPPEN? * Unclear as of now, could be due to wearing of components or possible misalignment. * * CONSEQUENCES: * Vibrations may result in equipment failure over time. This could disrupt regular operations. * * REQUIREMENTS IMPACTED: * Potential disruption in operation. * * ADVERSE PHYSICAL CONDITIONS: * Unusual vibrational spectrum and amplitude in 20B Compressor * * WHO WAS NOTIFIED: * Maintenance Supervisor, Incident Team * * KNOWLEDGEABLE INDIVIDUALS: * Senior Engineer, Mechanic, Incident Team * * REPEAT OR SIMILAR CONDITION: * No similar condition noted in the past. * * IMMEDIATE ACTIONS AND RECOMMENDED ACTIONS: * Call the maintenance team for further inspection. An alignment check or internal inspection could be required based on their diagnosis. * * 10/30/2017 12:03:43 GEORGE WILLIAMS (INCIDENT) * Initial inspection couldn't determine the exact cause. Recommending a comprehensive investigation involving mechanical team and further condition monitoring. | What immediate and recommended actions were taken following the detection of an unusual vibration in the 20B compressor? | Call the maintenance team for further inspection. An alignment check or internal inspection could be required based on their diagnosis.
291 | 2016-03-14 | 30731582 | 80562018 | 10B Pressure pump failure | S4CW -4CWE9 | * **************Incident Description************** * Notification 000030731582 Details * *********************************************************** * 03/14/2016 19:32:28 INCIDENT REPORT (INCIDENT REPORT) * Report submitted by: Linda Baker ENTITY\INCIDENT: * * CONDITION DESCRIPTION/LOCATION (THE INAPPROPRIATE ACTION AND ITS NEGATIVE EFFECT/INCLUDE A DETAILED LOCATION DESCRIPTION): * At 1920 on 03/14/16 during routine inspection, the 10B pressure pump failed, causing sudden drop in pressure. The pump was immediately shut down from the Unit Control Room and back up was activated. A quick inspection showed signs of internal damage. S4.OP-AB.MW-0002 Pressure Pump Failure was initiated due to the failure of 10B pressure pump. * * ACTIVITIES, PROCESSES, PROCEDURES INVOLVED: * S4.OP.AB-MW-0002, S4.OP-SO.MW-0002 * * WHY DID CONDITION HAPPEN: * Unknown, although similar issues have been recorded with other pressure pumps. * * CONSEQUENCES: * Potential equipment damage, inefficiency in pumping operation. * * REQUIREMENTS IMPACTED: * Operations impeded due to sudden pump failure. * * ADVERSE PHYSICAL CONDITION: * Failure of 10B Pressure pump, potential internal damage * * WHO WAS NOTIFIED: * Control Room, Maintenance Room * * KNOWLEDGEABLE INDIVIDUALS: * Davis, Thompson, Parks * * REPEAT OR SIMILAR CONDITION: * Yes, with pump 8B and 6B. * * IMMEDIATE ACTIONS AND RECOMMENDED ACTIONS: * Maintenance team dispatched to investigate pressure pump 10B. * * Updated: LINDA BAKER 03.14.2016 20:08:43 * ------------------------------------------------------------ * 03/16/2016 11:31:27 ROB DOUGLAS (MUSER) * After the investigation, it was determined that the primary issue was a valve failure, causing the pump to overwork. The valve and the pump were both replaced | What was the immediate response when the 10B pressure pump failed? | The pump was immediately shut down from the Unit Control Room and back up was activated.
292 | 2018-08-05 | 30720487 | 80204527 | B2A Pump malfunction | S1CW -1CWE1 | * **************Incident Description************** * Notification 000030720487 Details * *********************************************************** * 08/05/2018 15:13:46 INCIDENT REPORT (INCIDENT REPORT) * Report submitted by: Elizabeth Green ENTITY\INCIDENT: * * CONDITION DESCRIPTION/LOCATION (THE INAPPROPRIATE ACTION AND ITS NEGATIVE EFFECT/INCLUDE A DETAILED LOCATION DESCRIPTION): * During a regular maintenance check, B2A Pump was found with a sudden drop in efficiency. Investigation revealed a malfunction inside the pump mechanism which caused a reduction in flow rate. The system automatically initiated the standby pump, preventing an immediate production impact. * * ACTIVITIES, PROCESSES, PROCEDURES INVOLVED: * S1.OP.AB-CW-0003, S1.OP-SO.CW-0004 * * WHY DID CONDITION HAPPEN? * It appears that a component failure within the pump mechanism led to this condition. The specific cause is still uncertain. * * CONSEQUENCES: * Production efficiency may be reduced if the standby pump fails as well. * * REQUIREMENTS IMPACTED: * Daily operation of the system, as B2A Pump is currently out of commission. * * ADVERSE PHYSICAL CONDITIONS: * B2A Pump failure, potential internal damage. * * WHO WAS NOTIFIED: * Operations Supervisor, Maintenance Crew * * KNOWLEDGEABLE INDIVIDUALS: * Thompson, Anderson, Clark * * REPEAT OR SIMILAR CONDITION: * No, this is the first occurrence of this nature. * * IMMEDIATE ACTIONS AND RECOMMENDED ACTIONS: * Immediate internal investigation of the pump, replacement of faulty components if any, intense monitoring of the standby pump. * 08/06/2018 10:37:28 ELIZABETH GREEN (INCIDENT) * The failed component within the B2A Pump has been identified and replaced. The pump is now back online and functioning normally. Regular monitoring in place to prevent similar incidents in the future. | What was the immediate action taken after the incident involving the B2A Pump and what was the subsequent outcome? | Immediate internal investigation of the pump, replacement of faulty components if any, intense monitoring of the standby pump. The failed component within the B2A Pump has been identified and replaced. The pump is now back online and functioning normally. Regular monitoring in place to prevent similar incidents in the future.
293 | 2020-02-16 | 30998304 | 80236592 | Elevated temperature from 5B motor pump | S5CW -5CWE2 | * **************Incident Description************** * Notification 000030998304 Details * *********************************************************** * 02/16/2020 13:25:01 INCIDENT REPORT (INCIDENT REPORT) * Report submitted by: Hannah Ward ENTITY\INCIDENT: * CONDITION DESCRIPTION/LOCATION (THE INAPPROPRIATE ACTION AND ITS NEGATIVE EFFECT/INCLUDE A DETAILED LOCATION DESCRIPTION): * At around 1300 on 02/16/20, an elevated temperature was detected from the 5B pump motor during routine maintenance check. An emergency shutdown sequence was initiated and the pump was allowed to cool down. Post-shutdown observation showed no signs of external damage or fire - although a slight, unusual smell was noted, similar to burnt material. * * ACTIVITIES PROCESSES, PROCEDURES INVOLVED: * Normal routine check, S5.OP-AB-CW-0001, S5.OP-SO.CW-0001 * * WHY DID CONDITION HAPPEN? * The exact cause is unknown, though similar pump motor overheating has occurred previously. * * CONSEQUENCES: * Potential motor damage, potential loss of efficiency when the unit is back online * * REQUIREMENTS IMPACTED: * Routine maintenance, operation of the pump * * ADVERSE PHYSICAL CONDITIONS: * Overheating of 5B pump motor * * WHO WAS NOTIFIED: * Supervisor, Maintenance Team, Safety Department * * KNOWLEDGEABLE INDIVIDUALS: * Supervisor, Maintenance Team, Safety Department * * REPEAT OR SIMILAR CONDITION: * Yes, notice of overheating was released previously * * IMMEDIATE ACTIONS AND RECOMMENDED ACTIONS: * A complete inspection of the 5B pump motor is to be carried out; testing of the internal components is recommended. * 02/17/2020 09:53:35 HANNAH WARD (INCIDENT) * A thorough inspection of the motor was performed - no significant issues were found. The motor's internal components have been tested and passed all tests. The motor is currently in the process of being reassembled. | What was the immediate action and recommendation following the overheating of the 5B pump motor? | A complete inspection of the 5B pump motor is to be carried out; testing of the internal components is recommended.
294 | 2020-09-30 | 40012345 | 90025963 | 33B valve failure post-maintenance | S4CW -4CWE5 | * **************Incident Description************** * Notification 000040012345 Details * *********************************************************** * 09/30/2020 08:35:00 INCIDENT REPORT (INCIDENT REPORT) * Report submitted by: Emily Jacobs ENTITY\INCIDENT: * * CONDITION DESCRIPTION/LOCATION (THE INAPPROPRIATE ACTION AND ITS NEGATIVE EFFECT/INCLUDE A DETAILED LOCATION DESCRIPTION): * Post maintenance, 33B Valve began to display signs of failure. There was a moderate leakage observed during operation. Valve had been repaired in February 2020 under work order 90021150. The leakage suggests that the replacement parts or maintenance procedure could be faulty. * * ACTIVITIES, PROCESSES, PROCEDURES INVOLVED: * Post-maintenance inspection, operation, and abnormality identification. * * WHY DID CONDITION HAPPEN? * Uncertain, possible faulty components or lack of proper maintenance procedure enforcement. * * CONSEQUENCES: * Inefficient operation, potential hazard in the working environment, need for early replacement or repair. * * REQUIREMENTS IMPACTED: * Continuity in operation, Safety standards. * * ADVERSE PHYSICAL CONDITIONS: * Moderate leakage from 33B Valve. * * WHO WAS NOTIFIED: * Supervisor, Maintenance and Safety Team * * KNOWLEDGEABLE INDIVIDUALS: * Supervisor, Inspection Crew, Maintenance Team * * REPEAT OR SIMILAR CONDITION: * No, this is the first instance reported for the 33B Valve. * * IMMEDIATE ACTIONS AND RECOMMENDED ACTIONS: * Cease operation, create a safe work boundary, coordinate with maintenance for immediate repair or replacement. * 09/30/2020 12:55:10 EMILY JACOBS (INCIDENT) * The maintenance team finished their preliminary check and has concluded that the leakage is due to a faulty seal in the valve. A new seal has been ordered and will be replaced in the scheduled downtime tomorrow. | What was the immediate and recommended action taken post observing the valve leakage incident? | Cease operation, create a safe work boundary, coordinate with maintenance for immediate repair or replacement.
295 | 2019-09-30 | 30956237 | 90362519 | 30D Heat exchanger coolant leak | S4HE -4HES1 | * **************Incident Description************** * Notification 000030956237 Details * *********************************************************** * 09/30/2019 15:42:15 INCIDENT REPORT (INCIDENT REPORT) * Report submitted by: William Stewart ENTITY\INCIDENT: * * CONDITION DESCRIPTION/LOCATION (THE INAPPROPRIATE ACTION AND ITS NEGATIVE EFFECT/INCLUDE A DETAILED LOCATION DESCRIPTION): * Found coolant leak from 30D Heat exchanger during proactive system inspection. Approximately 10 gallons of coolant lost. No immediate impact to plant operations, but continued operation could damage heat exchanger and reduce efficiency. * * ACTIVITIES, PROCESSES, PROCEDURES INVOLVED: * Procedure S4.OP-HE-0003 was initiated. Heat Exchanger Shut Down and Leak Isolation Procedure. * * WHY DID CONDITION HAPPEN? * Leak source not identified. Further investigation required. Possible fatigue or corrosion. * * CONSEQUENCES: * Potential impact on heat exchanger efficiency, possible damage to other components and increased operating cost. * * REQUIREMENTS IMPACTED: * Reactor coolant system * * ADVERSE PHYSICAL CONDITIONS: * Coolant leak, potential internal damage to heat exchanger * * WHO WAS NOTIFIED: * Plant Supervisor, Maintenance Department. * * KNOWLEDGEABLE INDIVIDUALS: * Procedure Team, Maintenance, Zimmerman, Rogers, Singh * * REPEAT OR SIMILAR CONDITION: * No, first occurrence * * IMMEDIATE ACTIONS AND RECOMMENDED ACTIONS: * SOP HE-0003 implemented. Further inspections required to identify source of leak, evaluate extent of current damage, determine best repair process, and assess for preventive measures. * 10/02/2019 10:48:02 WILLIAM STEWART (INCIDENT) * Cooling system isolated and drained. Leak source identified as faulty seal. Replacement seal fitted and system refilled and tested. No leaks detected. System returned to service. Recommend monitoring new seal and investigating whether different seal material might prove more robust. | What was the immediate action taken after discovering the coolant leak from the 30D Heat Exchanger? | SOP HE-0003 implemented. Further inspections required to identify source of leak, evaluate extent of current damage, determine best repair process, and assess for preventive measures.
296 | 2018-10-10 | 30785233 | 80190151 | 14F Motor intermittent power loss | S4CA -4CWW1 | * **************Incident Description************** * Notification 000030785233 Details * *********************************************************** * 10/10/2018 14:15:30 INCIDENT REPORT (INCIDENT REPORT) * Report submitted by: Jessica Miller ENTITY\INCIDENT: * * CONDITION DESCRIPTION/LOCATION (THE INAPPROPRIATE ACTION AND ITS NEGATIVE EFFECT/INCLUDE A DETAILED LOCATION DESCRIPTION): * At approximately 1305, operator noted intermittent power loss in 14F Motor. 14F Motor was managed and monitored by Unit 2 Control Room. Stability returned after 5 minutes but reoccurrence was noticed after an additional 10 minutes. Engineering and Operations inspection did not reveal any significant power anomalies. However, there was an unexpected discharged capacitor noted which may have caused the flapping. S4.OP-AC.AC-0010 Abnormal Power Cycle was initiated due to the repeated power loss experiences from 14F Motor. * * ACTIVITIES, PROCESSES, PROCEDURES INVOLVED: * S4.OP.AC-AC-0010, S2.OP-SO.AC-0004 * * WHY DID CONDITION HAPPEN: * Potential electrical fault - Specific root is yet to be confirmed * * CONSEQUENCES: * Unpredictable operations - Potential premature deterioration of 14F Motor * * REQUIREMENTS IMPACTED: * Motor's Reliability and Longevity * * ADVERSE PHYSICAL CONDITION: * Intermittent power loss in 14F Motor * * WHO WAS NOTIFIED: * Control Room, Engineering Department * * KNOWLEDGEABLE INDIVIDUALS: * Davis, Kelly, Carter * * REPEAT OR SIMILAR CONDITION: * No * * IMMEDIATE AND RECOMMENDED ACTIONS: * Engineering to evaluate 14F Motor's power loss * * Updated: REBECCA WATSON 10.10.2018 16:10:20 * ------------------------------------------------------------ * 10/11/2018 08:19:37 JASON COOPER (NUSER) * The investigation revealed a voltage spike in the power supply that caused the capacitor to | What were the consequences of the intermittent power loss in the 14F Motor? | Unpredictable operations - Potential premature deterioration of 14F Motor
297 | 2018-11-07 | 30785211 | 80233791 | 33B pump pressure drop | S3CW -3CWE5 | * **************Incident Description************** * Notification 000030785211 Details * *********************************************************** * 11/07/2018 16:10:00 INCIDENT REPORT (INCIDENT REPORT) * Report submitted by: Danny Irvine ENTITY\INCIDENT: * * CONDITION DESCRIPTION/LOCATION (THE INAPPROPRIATE ACTION AND ITS NEGATIVE EFFECT/INCLUDE A DETAILED LOCATION DESCRIPTION): * During routine inspection, it was noted that the 33B Pump was not maintaining pressure effectively. Inspection showed a sudden drop in pressure, impacting the efficiency of the unit. * * ACTIVITIES, PROCESSES, PROCEDURES INVOLVED: * Regular operation and monitoring of 33B Pump * * WHY DID CONDITION HAPPEN? * Potential mechanical failure in the pump system, besides issues in the tide level or temperature difference might have contributed to the pressure drop. * * CONSEQUENCES: * Impacts pump efficiency and may lead to prolonged system downtime if not addressed. * * REQUIREMENTS IMPACTED: * Reduced system efficiency, potential impacts on downstream processes. * * ADVERSE PHYSICAL CONDITIONS: * Unexpected pressure drop on 33B Pump * * WHO WAS NOTIFIED: * Maintenance Team, Operations Supervisor * * KNOWLEDGEABLE INDIVIDUALS: * Maintenance Team, Lead Engineers * * REPEAT OR SIMILAR CONDITION: * No, this is the first instance of pressure drop on this scale. * * IMMEDIATE ACTIONS AND RECOMMENDED ACTIONS: * Investigate the root cause of the pressure drop, implement repairs and preventative measures to avoid recurrence. * 11/08/2018 10:30:23 MARK ALLEN (INCIDENT) * Root cause investigation has begun, pressure issues seem to be related to potential fault in one of the pump seals. Replacement parts ordered, repairs scheduled to commence immediately. Operations team informed about the potential downtime. | What were the consequences of the pressure drop in the 33B Pump, and who was notified? | Impacts pump efficiency and may lead to prolonged system downtime if not addressed. Maintenance Team, Operations Supervisor
298 | 2019-09-18 | 30760774 | 80234594 | Leak in Transformer 18B | S4TR -4TRF6 | * **************Incident Description************** * Notification 000030760774 Details * *********************************************************** * 09/18/2019 09:04:45 INCIDENT REPORT (INCIDENT REPORT) * Report submitted by: David Thompson * * CONDITION DESCRIPTION/LOCATION (THE INAPPROPRIATE ACTION AND ITS NEGATIVE EFFECT/INCLUDE A DETAILED LOCATION DESCRIPTION): * On September 18th, 2019, at 0910 hours, a leak was observed in the Transformer 18B. Upon inspection, oil had actively been dripping from the lower half of the transformer. The leak had been contained and cleanup was initiated under work order 80234594. * * ACTIVITIES, PROCESSES, PROCEDURES INVOLVED: * Regular safety inspection revealed the leak. S4.OP.AB.TR-0011, S4.OP-SO.TR-0003. * * WHY DID CONDITION HAPPEN? * Possible seal or gasket failure in the transformer housing. * * CONSEQUENCES: * Potential electrical and fire hazard if the leak is not addressed promptly. Possible transformer failure. * * REQUIREMENTS IMPACTED: * Electrical supply to Unit 4 * * ADVERSE PHYSICAL CONDITIONS: * Leak from Transformer 18B * * WHO WAS NOTIFIED: * Control Room, Maintenance Team and Electrical Department Supervisor * * KNOWLEDGEABLE INDIVIDUALS: * Wilson, Rogers, Sullivan * * REPEAT OR SIMILAR CONDITION: * No previous leakage reported on this transformer. * * IMMEDIATE ACTIONS AND RECOMMENDED ACTIONS: * Immediate repair to identify the source and fix the leak, followed by routine monitoring. * 09/19/2019 14:04:45 DAVID THOMPSON (INCIDENT) * The leak was due to a failure in the gasket. Gasket has been repaired, transformer has been cleaned and is now back to operation. | What immediate actions were taken after the leak was observed in the transformer? | Immediate repair to identify the source and fix the leak, followed by routine monitoring.
299 | 2021-11-06 | 30999025 | 80501017 | Excessive vibrations from 33B Pump unit | S4CW -4CWE5 | * **************Incident Description************** * Notification 000030999025 Details * *********************************************************** * 11/06/2021 13:21:35 INCIDENT REPORT (INCIDENT REPORT) * Report submitted by: Louis McRoy * ENTITY\INCIDENT: * * CONDITION DESCRIPTION/LOCATION (THE INAPPROPRIATE ACTION AND ITS NEGATIVE EFFECT/INCLUDE A DETAILED LOCATION DESCRIPTION): * During the afternoon inspection, 33B Pump unit started showing unusual vibration. The vibration sensor reading recorded was 0.45 inch/sec, much higher than the normal 0.05 inch/sec. No pressure or temperature irregularities were observed. The pump operates within the 4th Cold Water extraction Unit. * * ACTIVITIES, PROCESSES, PROCEDURES INVOLVED: * Regular inspection * * WHY DID CONDITION HAPPEN? * The exact cause is still unknown. Possible indications towards worn out internal pump components. * * CONSEQUENCES: * If not addressed, the excessive vibration could cause premature damage to the pump, affecting the normal functioning of the extraction unit. * * REQUIREMENTS IMPACTED: * Regular operation and maintenance * * ADVERSE PHYSICAL CONDITIONS: * High vibration levels from the 33B Pump unit. * * WHO WAS NOTIFIED: * Supervisor, Maintenance team * * KNOWLEDGABLE INDIVIDUALS: * Supervisor, Maintenance team * * REPEAT OR SIMILAR CONDITION: * No prior incidents of similar nature. * * IMMEDIATE ACTIONS AND RECOMMENDED ACTIONS: * A detailed investigation is to be initiated for the 33B Pump unit. In case high vibration continues, a potential shutdown and overhaul may be required. * * 11/07/2021 10:31:47 LOUIS MCROY (INCIDENT) * A closer inspection identified a possible imbalance in the pump impeller. Preparing for an immediate temporary shut down and corrective maintenance. The pump components would be further inspected during the shutdown. | What immediate action was recommended for the irregular vibration in the 33B Pump unit? | A detailed investigation is to be initiated for the 33B Pump unit. In case high vibration continues, a potential shutdown and overhaul may be required.
300 | 2018-12-28 | 31012560 | 91255348 | Hydraulic leak detected on 50B Pump | S2CW -2CWE7-MTRD | * **************Incident Description************** * Notification 000031012560 Details * *********************************************************** * SUMMARY: VERIFY CURRENT REQUIREMENTS CONTAINED IN * ****PS-AA-121 "ISSUE IDENTIFICATION AND MAINTENANCE PROCEDURE"***** * * 1) Condition Description/Location (The inappropriate action and its negative effect/Include a detailed location description): * At 1330 on 12/28/18, maintenance technician reported a hydraulic leak on the 50B Pump located in Unit 2. Immediate shut down was performed and the leak ceased. Inspection showed hydraulic fluid on the floor, but the source was not immediately visible. PS-AA-121 "Leak Assessment and Management" was initiated. * * 2) ACTIVITIES, PROCESSES, PROCEDURES INVOLVED: * S4.OP.AB-CS-0002, S4.OP-SO.CS-0002 * * 3) WHY DID CONDITION HAPPEN: * Unknown. Leak source not immediately visible, further investigation required. * * 4) CONSEQUENCES: * If not addressed, could potentially lead to reduced performance, environmental impact and fire hazard. * * 5) REQUIREMENTS IMPACTED: * Immediate shutdown affecting unit operation * * 6) ADVERSE PHYSICAL CONDITION: * Hydraulic leak from 50B Pump, environment impact due to hydraulic fluid on floor. * * 7) WHO WAS NOTIFIED: * Control Room, Maintenance Supervisor * * 8) KNOWLEDGEABLE INDIVIDUALLY: * Johnson, Adams, Miller * * 9) REPEAT OR SIMILAR CONDITION: * No * * 10) IMMEDIATE AND RECOMMENDED ACTIONS: * Maintenance to investigate the source of hydraulic leak, clean up the spilled fluid and resume operation once the pump is fixed. * * Updated: JOHN DOE 12.28.2018 15:00:18 * ------------------------------------------------------------ * 01/10/2019 13:43:17 JANE DOE (REPAIR) * Investigation completed. Leak source was from a degraded seal. Seal has been replaced, local area cleaned and | What actions were taken upon discovering the hydraulic leak on the 50B Pump? | Immediate shut down was performed and the leak ceased. Inspection showed hydraulic fluid on the floor, but the source was not immediately visible. PS-AA-121 "Leak Assessment and Management" was initiated.
301 | 2016-09-07 | 30780452 | 80222134 | 18B compressor failure indication | S3CW -3CWE7 | * **************Incident Description************** * Notification 000030780452 Details * *********************************************************** * 09/07/2016 14:34:56 INCIDENT REPORT (INCIDENT REPORT) * Report submitted by: William Parker ENTITY\INCIDENT: * * CONDITION DESCRIPTION/LOCATION (THE INAPPROPRIATE ACTION AND ITS NEGATIVE EFFECT/INCLUDE A DETAILED LOCATION DESCRIPTION): * At 1420 on 9/7/16, an alarm was triggered indicating a potential failure in the 18B Compressor. On-site inspection revealed signs of mechanical distress - oil leakage and excessive vibration. The unit was brought offline and an emergency inspection was initiated. The rest of the system remains in normal operation. * * ACTIVITIES, PROCESSES, PROCEDURES INVOLVED: * Normal operation, response to alarm. * * WHY DID CONDITION HAPPEN? * Initial indications suggest a seal failure, although this is yet to be confirmed. * * CONSEQUENCES: * Immediate consequences include interruption to normal operations. Prolonged failure may impact efficiency and system deliverables. * * REQUIREMENTS IMPACTED: * Normal relay of pressures throughout the system. * * ADVERSE PHYSICAL CONDITIONS: * Excessive vibration, oil leak * * WHO WAS NOTIFIED: * Control Room, Maintenance Team * * KNOWLEDGEABLE INDIVIDUALS: * Johnson, Adams, Miller * * REPEAT OR SIMILAR CONDITION: * No, this is a first for the 18B Compressor. * * IMMEDIATE ACTIONS AND RECOMMENDED ACTIONS: * Full inspection of 18B Compressor, identify source of oil leak and excessive vibration, undertake necessary repairs. * 09/08/2016 10:27:45 WILLIAM PARKER (INCIDENT) * Maintenance identified a defective seal on the 18B Compressor. The seal has been replaced and the unit returned to normal operations. Recommendations for routine check for similar defects on all compressor units. | What immediate actions were taken following the alarm triggered by the 18B Compressor in the incident reported on 09/07/2016? | Full inspection of 18B Compressor, identify source of oil leak and excessive vibration, undertake necessary repairs.
302 | 2018-11-04 | 30910234 | 90247856 | Unusual vibration detected in 40B Pump | S4W -4CWE8 | * **************Incident Description************** * Notification 000030910234 Details * *********************************************************** * 11/04/2018 08:30:10 INCIDENT REPORT (INCIDENT REPORT) * Report submitted by: Ethan Patel ENTITY\INCIDENT: * CONDITION DESCRIPTION/LOCATION (THE INAPPROPRIATE ACTION AND ITS NEGATIVE EFFECT/INCLUDE A DETAILED LOCATION DESCRIPTION): * During the morning shift, operators detected unusual vibration from 40B Pump. The vibration indicator showed an increase of 15% from normal levels. No significant change in temperature or pressure was noted at that time. The 40B Pump was taken offline to avoid potential damage and emergency procedure was initiated. * ACTIVITIES, PROCESSES, PROCEDURES INVOLVED: * Device check, Emergency operating procedures S4.OP.AB-CW-0031, S4.OP.SO.CW-0032 * WHY DID CONDITION HAPPEN? * The root cause of the excessive vibration is yet to be known, possibly misaligned rotor or bearings wear could be the factor, which was observed in similar incidents before. * CONSEQUENCES: * If left unaddressed, could result in severe damage to the pump and the unit downtime. * REQUIREMENTS IMPACTED: * Pump availability * ADVERSE PHYSICAL CONDITIONS: * Excessive vibrations from 40B Pump * WHO WAS NOTIFIED: * Shift Manager, Incident Team * KNOWLEDGEABLE INDIVIDUALS: * Incident Team, George, Hopkins * REPEAT OR SIMILAR CONDITION: * Yes, in multiple occasions * IMMEDIATE ACTIONS AND RECOMMENDED ACTIONS: * Investigation should be initiated to understand the root cause of vibration. Based on the findings appropriate maintenance activity should be performed. * 11/05/2018 14:40:23 ETHAN PATEL (INCIDENT) * Engineering team performed analysis on the pump. Identified few soft foot issues, indications of bearing wear and rotor imbalance. Immediate maintenance was performed to addresses these issues and 40B Pump is now back in operation with normal vibration levels. | What immediate and recommended actions were taken after the excessive vibration from the 40B Pump was detected? | Investigation should be initiated to understand the root cause of vibration. Based on the findings appropriate maintenance activity should be performed. Engineering team performed analysis on the pump. Identified few soft foot issues, indications of bearing wear and rotor imbalance. Immediate maintenance was performed to addresses these issues and 40B Pump is now back in operation with normal vibration levels.
303 | 2022-04-01 | 30998745 | 80245632 | Overheating of generator G3A | S3ES-3ESE3 | * **************Incident Description************** * Notification 000030998745 Details * *********************************************************** * 04/01/2022 15:30:00 INCIDENT REPORT (INCIDENT REPORT) * Report Submitted by: William Gray NST\ACCIDENT * * CONDITION DESCRIPTION/LOCATION (THE INAPPROPRIATE ACTION AND ITS NEGATIVE EFFECT/INCLUDE A DETAILED LOCATION DESCRIPTION): * During the standard inspection at 1540, it was found that generator G3A was overheating. Cooling systems were immediately activated, dropping the temperature gradually. A strong odor was detected, indicating potential damage. * * ACTIVITIES, PROCESSES, PROCEDURES INVOLVED: * Normal operation, Immediate implementation of cooling systems * * WHY DID CONDITION HAPPEN? * Unknown. Prior incidents of overheating have been linked to debris in cooling vents or system malfunctions. * * CONSEQUENCES: * Potential generator failure, Disruption to electrical grid * * REQUIREMENTS IMPACTED: * Routine operations, Safety protocol * * ADVERSE PHYSICAL CONDITIONS: * High temperature, Odor indicating potential internal damage * * WHO WAS NOTIFIED: * Control Room, Engineering Team * * KNOWLEDGEABLE INDIVIDUALS: * Ross, Thomson, Adams * * REPEAT OR SIMILAR CONDITION: * Yes, similar incidents have occurred, although root cause is not always the same * * IMMEDIATE ACTIONS AND RECOMMENDED ACTIONS: * Engineering team to conduct an investigation, System checks to be performed, possible replacement if significant damage found * * Update: WILLIAM GRAY 04.01.2022 18:20:39 * ------------------------------------------------------------ * 04/02/2022 08:00:45 JOHN MILTON (QUIP) * Initial inspections indicate a potential system blockage. Further investigation needed to confirm and to determine next steps. No significant damage observed to necessitate immediate replacement of generator. | What immediate measures were taken when the generator G3A was found overheating? | Cooling systems were immediately activated, dropping the temperature gradually.
304 | 2020-09-14 | 30800910 | 80215610 | Anomaly in 30A CWS motor vibration | S4CW -4CWE4 | * **************Incident Description************** * Notification 000030800910 Details * *********************************************************** * 09/14/2020 06:57:15 INCIDENT REPORT (INCIDENT REPORT) * Report submitted by: Michael Steward ENTITY\INCIDENT: * * CONDITION DESCRIPTION/LOCATION (THE INAPPROPRIATE ACTION AND ITS NEGATIVE EFFECT/INCLUDE A DETAILED LOCATION DESCRIPTION): * At 06:55 hours on 09/14/2020, during a standard operation check, abnormal vibration was detected on 30A Pump Motor. Upon examination, no visual defect was identified on the motor, and no discernible noise accompanying the vibration. Vibration levels were higher as compared to other operation motors. No immediate corrective action was taken as the motor has not shown any loss of operational effectiveness. * * ACTIVITIES, PROCESSES, PROCEDURES INVOLVED: * Standard operational checks and routine assessment. * * WHY DID CONDITION HAPPEN? * Unknown, structural integrity of the supporting base or motor internal issues could be potential causes. * * CONSEQUENCES: * If not addressed, long-term damage could be inflicted on the motor leading to operational inefficiencies. * * REQUIREMENTS IMPACTED: * Regular pump operation and maintenance scheduling. * * ADVERSE PHYSICAL CONDITIONS: * High vibration levels in 30A Pump motor. * * WHO WAS NOTIFIED: * Supervisor, Maintenance Team, Engineering Unit * * KNOWLEDGEABLE INDIVIDUALS: * Supervisor, Maintenance Team, Engineering Unit * * REPEAT OR SIMILAR CONDITION: * No, first instance. * * IMMEDIATE ACTIONS AND RECOMMENDED ACTIONS: * A comprehensive review of internal motor parts and supportive base to be initiated. Engineering team to inspect and ascertain the cause of vibration. If not resolved, replacement options to be considered. * 09/15/2020 10:45:17 MICHAEL STEWARD (INCIDENT) * An investigation into the 30A motor revealed the vibration may have resulted from functional wear and tear. Further, the examination revealed a distorted supporting base likely contributing to the anomaly. A temporary | What was the initial finding when the abnormal vibration was detected on the 30A Pump Motor? | At 06:55 hours on 09/14/2020, during a standard operation check, abnormal vibration was detected on 30A Pump Motor. Upon examination, no visual defect was identified on the motor, and no discernible noise accompanying the vibration. Vibration levels were higher as compared to other operation motors. No immediate corrective action was taken as the motor has not shown any loss of operational effectiveness.
305 | 2020-10-10 | 40702856 | 90128540 | 30C Pump clogging frequently | S4CW -4CWE4 | * ************Incident Description**************** * Notification 000040702856 Details * ********************************************************************** * 10/10/2020 10:35:23 INCIDENT REPORT (INCIDENT REPORT) * Report submitted by: Sarah Ford ENTITY\INCIDENT: * * CONDITION DESCRIPTION/LOCATION (THE INAPPROPRIATE ACTION AND ITS NEGATIVE EFFECT/INCLUDE A DETAILED LOCATION DESCRIPTION): * During the routine inspections, it has been observed that 30C pump gets clogged frequently. This is hampering the functioning of the entire system and has led to increased downtime. * * ACTIVITIES, PROCESSES, PROCEDURES INVOLVED: * Regular maintenance of the pump area, S4.OP-AB.CW-0002 * * WHY DID CONDITION HAPPEN? * This is unclear. The issue might be recurring due to the buildup of debris or due to a potential issue with the pump design or operation. Further investigation required. * * CONSEQUENCES: * Frequent clogs leading to increased downtime and less efficiency in operation. * * REQUIREMENTS IMPACTED: * Pump operation and maintenance schedule, Need for additional resources for cleanup * * ADVERSE PHYSICAL CONDITIONS: * Clogging of the 30C Pump area * * WHO WAS NOTIFIED: * The maintenance department and the incident team * * KNOWLEDGEABLE INDIVIDUALS: * Maintenance department, Clark, Lopez, Richards * * REPEAT OR SIMILAR CONDITION: * Yes, this issue has surfaced multiple times in the past three months. * * IMMEDIATE ACTIONS AND RECOMMENDED ACTIONS: * The area needs to be cleaned immediately. The pump operation and pump design will need to be examined for possible modifications. * 10/10/2020 14:26:52 SARAH FORD (INCIDENT) * Proper investigation should be launched by the team in order to find the root cause and take preventive measures to avoid reoccurrence. Issue forwarded to engineering department for review. | Why is the 30C pump clogging frequently? | The issue might be recurring due to the buildup of debris or due to a potential issue with the pump design or operation. Further investigation required.
306 | 2017-04-20 | 30739105 | 80245606 | Sudden power cut in 16A VC Circuit Pump | S4CV -4CVE2 | * **************Incident Description************** * Notification 000030739105 Details * *********************************************************** * 04/20/2017 08:43:00 INCIDENT REPORT (INCIDENT REPORT) * Report submitted by: David Santos ENTITY\INCIDENT: * * CONDITION DESCRIPTION/LOCATION (THE INAPPROPRIATE ACTION AND ITS NEGATIVE EFFECT/INCLUDE A DETAILED LOCATION DESCRIPTION): * Around 0745 on 4/20/17, while performing routine observation, 16A VC Circuit Pump experienced a sudden power cut. The pump was immediately shut down from the Control Room, and Fire Department and Operations inspection were carried out. There was no sign of fire or damage, but the pump power supply needs to be verified and any potential faults rectified. * S4.OP-AB.CV-0001 Pump Unavailability was initiated to address the situation. * * ACTIVITIES, PROCESSES, PROCEDURES INVOLVED: * S4.OP.AB-CV-0001, S4.OP-SO.CV-0001 * * WHY DID CONDITION HAPPEN? * Unknown - there may possibly be an issue with the power supply. * * CONSEQUENCES: * Loss of pump availability and potential delay in production. * * REQUIREMENTS IMPACTED: * Pump operation and reliability * * ADVERSE PHYSICAL CONDITIONS: * Possible internal damage or fault in power supply system to 16A VC Circuit Pump * * WHO WAS NOTIFIED: * Control Room, Operations Team, Fire Department * * KNOWLEDGEABLE INDIVIDUALS: * Robinson, Martin, Davis * * REPEAT OR SIMILAR CONDITION: * No known past incidents. * * IMMEDIATE ACTIONS AND RECOMMENDED ACTIONS: * Engineering to investigate power supply of 16A VC Circuit Pump * * 04/21/2017 18:32:00 DAVID SANTOS (INCIDENT) * Investigation regarding loss of power supply is ongoing. Temporary power source setup enabled the pump to resume operations. Long term solution will be implemented post final report of the incident. | What immediate actions were taken following the incident with the 16A VC Circuit Pump? | Engineering to investigate power supply of 16A VC Circuit Pump.
307 | 2017-04-10 | 30822359 | 80251874 | 33E Pump high vibration | S4CW -4CWE8 | * **************Incident Description************** * Notification 000030822359 Details * *********************************************************** * 04/10/2017 08:35:21 INCIDENT REPORT (INCIDENT REPORT) * Report submitted by: Stanley Hudson ENTITY\INCIDENT: * * CONDITION DESCRIPTION/LOCATION (THE INAPPROPRIATE ACTION AND ITS NEGATIVE EFFECT/INCLUDE A DETAILED LOCATION DESCRIPTION): * At 0835 on 4/10/17, control room assessment detected an unusually high vibration on the 33E Pump. Following the procedures, the pump was manually shut down from Unit 4 Control Room. No immediate damage was noted, however a intense vibration was felt before and after shutdown. S4.OP-AB.CW-0004 Pump Abnormality was initiated due to the elevated vibration reading on 33E Pump. * * ACTIVITIES, PROCESSES, PROCEDURES INVOLVED: * S4.OP.AB-CW-0004, S4.OP-SO.CW-0004 * * WHY DID CONDITION HAPPEN? * The exact cause is unclear, however misalignment or bearing failure could be suspected. * * CONSEQUENCES: * Potential pump failure and loss of efficiency. * * REQUIREMENTS IMPACTED: * Standby pump * * ADVERSE PHYSICAL CONDITIONS: * High vibration reading on 33E Pump * * WHO WAS NOTIFIED: * Control Room, Maintenance Department * * KNOWLEDGEABLE INDIVIDUALS: * Stanley, Jones, Thompson * * REPEAT OR SIMILAR CONDITION: * Yes, notification 30794236 occurred previously on different pump. * * IMMEDIATE ACTIONS AND RECOMMENDED ACTIONS: * Maintenance Department to inspect and troubleshoot 33E Pump. * 04/13/2017 14:46:12 JOHN DOE (INCIDENT) * The pump was dismantled and inspected. It was found that the bearing had indeed failed causing the high vibration. The bearing was replaced, the pump was aligned and put back into operation with normal vibration levels recorded. Continuous monitoring is recommended. | What was the initial action taken when the high vibration was detected in the 33E Pump? | Following the procedures, the pump was manually shut down from Unit 4 Control Room.
308 | 2018-01-10 | 30752884 | 80234610 | Observed vibration in 18B Pump Motor | S4CW -4CWE5 | * **************Incident Description************** * Notification 000030752884 Details * *********************************************************** * 01/10/2018 08:12:55 INCIDENT REPORT (INCIDENT REPORT) * Report submitted by: Victor Harris ENTITY\INCIDENT: * * CONDITION DESCRIPTION/LOCATION (THE INAPPROPRIATE ACTION AND ITS NEGATIVE EFFECT/INCLUDE A DETAILED LOCATION DESCRIPTION): * During a routine walkthrough, 6955 identified that excessive vibration was originating from 18B Pump Motor. Immediate shutdown was performed for the safety of the personnel and equipment. After the shutdown, the vibration ceased, and an initial inspection was conducted, which involved checking the alignment and balance of the pump, but no significant discrepancies were noted. * * ACTIVITIES, PROCESSES, PROCEDURES INVOLVED: * Routine Inspection, Motor Shutdown Procedure. * * WHY DID CONDITION HAPPEN? * Unclear. However, causes could include bearing issues, alignment problems, or mechanical defects within the pump. * * CONSEQUENCES: * Potential failure of the pump, which could disrupt normal operations and pose safety hazards. * * REQUIREMENTS IMPACTED: * Normal operation. * * ADVERSE PHYSICAL CONDITIONS: * Excessive vibration in the 18B Pump Motor. * * WHO WAS NOTIFIED: * Supervisor, Maintenance Team * * KNOWLEDGEABLE INDIVIDUALS: * Maintenance Team, Technical Support * * REPEAT OR SIMILAR CONDITION: * Yes, similar conditions have occurred multiple times in the past. * * IMMEDIATE ACTIONS AND RECOMMENDED ACTIONS: * Maintenance personnel will perform a thorough inspection of the 18B Pump Motor, checking for potential issues with bearings, alignment, and possible internal pump defects. Pending their findings, corrective actions will be taken accordingly. * 01/10/2018 16:21:29 VICTOR HARRIS (INCIDENT) * The detailed inspection found a fault in the bearings, causing the excessive vibration. The faulty part has been replaced, and the motor is again functioning within normal parameters. Necessary adjustments have been made to the maintenance schedule to prevent recurrence. | What was the cause of the excessive vibration in the 18B Pump Motor? | The detailed inspection found a fault in the bearings, causing the excessive vibration.
309 | 2020-03-17 | 30975030 | 80231289 | Overheating in compressor 3C | S4CW -4CWE5 | * **************Incident Description************** * Notification 000030975030 Details * *********************************************************** * 03/17/2020 10:54:35 INCIDENT REPORT (INCIDENT REPORT) * Report submitted by: Daniel Evans ENTITY\INCIDENT: * * CONDITION DESCRIPTION/LOCATION (THE INAPPROPRIATE ACTION AND ITS NEGATIVE EFFECT/INCLUDE A DETAILED LOCATION DESCRIPTION): * At 10:20 on 3/17/2020, the operator detected an increase temperature in Compressor 3C. The heat rise was noted during routine checks and it was immediately shut down to prevent any possible damage. Fire Suppression Team and Operations review found no fire evidence but a smell of burning insulation was in the air. After cooling down, the compressor’s temperatures were similar to other running units and no external damage was observed. * * ACTIVITIES, PROCESSES, PROCEDURES INVOLVED: * Routine operational checks, S4.OP-AC.CW-0005, S4.OP-SO.CW-0003 * * WHY DID CONDITION HAPPEN? * The exact reason for the sudden heat rise is yet to be identified; although, similar instances related to worn-out bearings have occurred * * CONSEQUENCES: * Potential damage to the compressor, deteriorated operational efficiency when placed back on service * * REQUIREMENTS IMPACTED: * Unavailable compressor for operation * * ADVERSE PHYSICAL CONDITIONS: * Overheating Compressor 3C, potential internal damage * * WHO WAS NOTIFIED: * Supervisor, Fire Suppression Team * * KNOWLEDGEABLE INDIVIDUALS: * Adams, Rodriguez, Williams * * REPEAT OR SIMILAR CONDITION: * Yes, past instances noted * * IMMEDIATE ACTIONS AND RECOMMENDED ACTIONS: * Maintenance department to inspect and probe the reason for overheating in Compressor 3C * * Updated: DANIEL EVANS 03.17.2020 12:45:37 * ------------------------------------------------------------ * 03/27/2020 16:22:13 JEFF DOE (NUSER) * | What immediate action was recommended following the incident with Compressor 3C? | Maintenance department to inspect and probe the reason for overheating in Compressor 3C
310 | 2020-12-12 | 30952617 | 80255449 | Oil Leak in 17B Booster Pump | S4HW -4HWE7-BSTR | * **************Incident Description************** * Notification 000030952617 Details * *********************************************************** * 12/12/2020 16:43:56 INCIDENT REPORT (INCIDENT REPORT) * Report submitted by: Rachel Green 321-654-0987 ENTITY\INCIDENT: * CONDITION DESCRIPTION/LOCATION (THE INAPPROPRIATE ACTION AND ITS NEGATIVE EFFECT/INCLUDE A DETAILED LOCATION DESCRIPTION): * At 1630 on 12/12/2020, during the routine inspection, an oil leak was observed from the 17B Booster Pump. The pump was immediately shut down from Unit 4 Control Room. No significant drop in pressure or unusual noises were noted before the shutdown. Inspection revealed the leakage was from the pump's seal area. The maintenance and spill response team were alerted, and they handled the situation promptly. * * ACTIVITIES, PROCESSES, PROCEDURES INVOLVED: * Routine inspection, S4.OP-SO.HW-0001, S4.OP-AB.HW-0003 * * WHY DID CONDITION HAPPEN? * Preliminary inspection suggests the failure of the pump seal. * * CONSEQUENCES: * An unplanned shut down of the 17B booster pump. Risk of environment pollution due to oil spill. * * REQUIREMENTS IMPACTED: * Safe operation, Environment safety criteria * * ADVERSE PHYSICAL CONDITIONS: * Oil leakage from the 17B booster pump * * WHO WAS NOTIFIED: * Supervisor, Maintenance Team, Spill Response Team * * KNOWLEDGEABLE INDIVIDUALS: * Controller, Thompson, Miller, and Harris from the maintenance team * * REPEAT OR SIMILAR CONDITION: * No * * IMMEDIATE ACTIONS AND RECOMMENDED ACTIONS: * The pump is scheduled for repair and potential seal replacement. Further investigation is to be conducted to identify and mitigate any possible causes that may lead to a similar issue. * 12/15/2020 10:02:31 RACHEL GREEN (INCIDENT) * The pump was put into maintenance schedule. The seal was identified to be the issue and | What caused the oil leak in the 17B Booster Pump during the routine inspection? | Preliminary inspection suggests the failure of the pump seal.
311 | 2018-10-09 | 30790297 | 80246123 | 35B Pump Unusual Vibration | S3CW -3CWE7 | * **************Incident Description************** * Notification 000030790297 Details * *********************************************************** * 10/09/2018 10:38:00 INCIDENT REPORT (INCIDENT REPORT) * Report submitted by: Thomas Green ENTITY\INCIDENT: * * CONDITION DESCRIPTION/LOCATION (THE INAPPROPRIATE ACTION AND ITS NEGATIVE EFFECT/INCLUDE A DETAILED LOCATION DESCRIPTION): * During the daily walkdown, abnormal vibration was detected on the pump 35B. The frequency of the vibration was unusual compared the normal operation condition. There were no significant changes in temperature or pressure readings. Pump data, including vibration frequencies, needs to be evaluated against baselines. * * ACTIVITIES, PROCESSES, PROCEDURES INVOLVED: * Daily walkdown * * WHY DID CONDITION HAPPEN? * Unknown, could possibly be due to worn out bearings or imbalance in the rotor assembly. * * CONSEQUENCES: * Mechanical failure if not mitigated & potential damage to associated systems. * * REQUIREMENTS IMPACTED: * Operational Requirements * * ADVERSE PHYSICAL CONDITIONS: * Excessive vibration at the pump * * WHO WAS NOTIFIED: * Supervisor, Maintenance Department * * KNOWLEDGEABLE INDIVIDUALS: * Maintenance Manager, Pump Operations Engineer * * REPEAT OR SIMILAR CONDITION: * No * * IMMEDIATE ACTIONS AND RECOMMENDED ACTIONS: * Evaluate pump data, and initiate maintenance inspection. If the vibration persists, a detailed analysis is required to assess the health of the pump. * 10/10/2018 15:56:10 THOMAS GREEN (INCIDENT) * Recommended actions have been initiated. Detailed inspection scheduled for next week. | What was the abnormal condition detected during the daily walkdown? | During the daily walkdown, abnormal vibration was detected on the pump 35B. The frequency of the vibration was unusual compared the normal operation condition.
312 | 2021-05-18 | 30785091 | 80202445 | 17B PUMP vibration Increase | S4CW -4CWE5 | * **************Incident Description************** * Notification 000030785091 Details * *********************************************************** * 05/18/2021 14:52:14 INCIDENT REPORT (INCIDENT REPORT) * Report submitted by: Richard Johnson ENTITY\INCIDENT: * * CONDITION DESCRIPTION/LOCATION (THE INAPPROPRIATE ACTION AND ITS NEGATIVE EFFECT/INCLUDE A DETAILED LOCATION DESCRIPTION): * During the morning checks on 05/18/2021, increased vibration was noticed in 17B Pump. Initial inspection could not identify the exact cause, however, there was a significant increase in vibration compared to the baseline data. The pump was taken offline and the maintenance team was notified for further investigation. * * ACTIVITIES, PROCESSES, PROCEDURES INVOLVED: * Daily operation checks and vibration monitoring * * WHY DID CONDITION HAPPEN? * Unknown at present, further inspection is required. * * CONSEQUENCES: * Prolonged operation in this condition could lead to pump damage or failure * * REQUIREMENTS IMPACTED: * Normal operation, risk to reliability * * ADVERSE PHYSICAL CONDITIONS: * Increased vibration in the 17B pump, potential internal damage * * WHO WAS NOTIFIED: * Maintenance Team, Supervising Manager * * KNOWLEDGEABLE INDIVIDUALS: * Maintenance Team, Pump Operators * * REPEAT OR SIMILAR CONDITION: * No, first such issue on this pump. * * IMMEDIATE ACTIONS AND RECOMMENDED ACTIONS: * Have Maintenance inspect the pump and underlying system to diagnose the cause of increased vibration * Jacqueline Stone (INCIDENT) * The initial investigation suggests unbalanced impeller could be the cause for increased vibration. The pump has been scheduled for immediate maintenance and inspection. | What was noticed during the daily operation checks and vibration monitoring on 05/18/2021? | During the morning checks on 05/18/2021, increased vibration was noticed in 17B Pump. Initial inspection could not identify the exact cause, however, there was a significant increase in vibration compared to the baseline data. The pump was taken offline and the maintenance team was notified for further investigation.
313 | 2019-11-15 | 30987246 | 90231578 | 33B Pump check valve failure | S4CW -4CWE7-MTRD | * **************Incident Description************** * Notification 000030987246 Details * *********************************************************** * SUMMARY: OPERATIONAL IRREGULARITIES OBSERVED IN * ****SS-BA-210 "PUMP MAINTENANCE AND INSPECTION PROCESS"***** * * 1) Condition Description/Location (The inappropriate action and its negative effect/Include a detailed location description): * At 0937 on 11/15/19, during pump inspection, it was observed that the 33B Pump's check valve was not holding. Immediate shutdown of 33B Pump was executed from Unit 4 Control Room. Maintenance personnel reported no evident external damage but noted a failure to hold pressure. SS-BA-210 Pump Maintenance Procedure was initiated due to the failure of 33B Pump check valve. * * 2) ACTIVITIES, PROCESSES, PROCEDURES INVOLVED: * SS-BA-210, S4.OP-AB.CW-0007 * * 3) WHY DID CONDITION HAPPEN: * Possible valve wear or damage. Prior instances of valve failures. * * 4) CONSEQUENCES: * Reduced pump efficiency, potential pump damage and downtime. * * 5) REQUIREMENTS IMPACTED: * Pump cannot maintain required pressure. * * 6) ADVERSE PHYSICAL CONDITION: * Failure of 33B Pump check valve, possible resultant damage. * * 7) WHO WAS NOTIFIED: * Control Room, Maintenance Department * * 8) KNOWLEDGEABLE INDIVIDUALS: * Anderson, Patel, Roberts * * 9) REPEAT OR SIMILAR CONDITION: * Yes, previously occurred events of valve failures. * * 10) IMMEDIATE AND RECOMMENDED ACTIONS: * Maintenance to perform detailed inspection and fix of 33B Pump Check Valve. * * Updated: DAVID WILLIAMS 11.15.2019 16:15:40 * ------------------------------------------------------------ * 11/25/2019 07:55:30 LISA SMITH (NUSER) * Upon inspection, valve wear was confirmed as the | What immediate actions were recommended after the failure of 33B Pump check valve? | Maintenance to perform detailed inspection and fix of 33B Pump Check Valve.
314 | 2021-07-20 | 30985236 | 80235698 | Excessive pressure in valve 10C | S4CW -4CWE3 | * **************Incident Description************** * Notification 000030985236 Details * *********************************************************** * 07/20/2021 14:25:00 INCIDENT REPORT (INCIDENT REPORT) * Report submitted by: Dominic Green ENTITY\INCIDENT: * CONDITION DESCRIPTION/LOCATION (THE INAPPROPRIATE ACTION AND ITS NEGATIVE EFFECT/INCLUDE A DETAILED LOCATION DESCRIPTION): * The normal operating pressure for valve 10C was noticed to be consistently higher. The pressure was over the acceptable limit during a routine check. The incident led to temporary disruption of normal work activities while the valve was isolated and reduced the pressure. * * ACTIVITIES, PROCESSES, PROCEDURES INVOLVED: * Valve monitoring and handling procedure under S4.OP-SO.CW-0003. * * WHY DID CONDITION HAPPEN? * Unknown at this time, the valve might have become faulty or there could be an obstruction causing the elevated pressure. * * CONSEQUENCES: * Risk of equipment damage or failure if the pressure wasn't reduced on time. * * REQUIREMENTS IMPACTED: * Normal operation of the valve and connected systems. * * ADVERSE PHYSICAL CONDITIONS: * Overpressure condition in Valve 10C. * * WHO WAS NOTIFIED: * Supervising team, Maintenance Unit * * KNOWLEDGEABLE INDIVIDUALS: * Supervising team, Maintenance Unit, Engineering Team * * REPEAT OR SIMILAR CONDITION: * No * * IMMEDIATE ACTIONS AND RECOMMENDED ACTIONS: * Maintenance Unit to carry out thorough inspection and rectification procedures on Valve 10C. An update in valve pressure monitoring procedures possibly needed. * * 07/25/2021 11:01:13 ALEX RICHARD (INCIDENT) * The valve has been inspected and repaired. No obstruction was found. We suspect a fault within the valve was the cause of the pressure rise. Work order 80235698 was closed off and Valve 10C is back on line. The monitoring procedures have been revised accordingly. | What immediate actions were recommended after the overpressure condition was detected in Valve 10C? | Maintenance Unit to carry out thorough inspection and rectification procedures on Valve 10C. An update in valve pressure monitoring procedures possibly needed.
315 | 2017-05-03 | 30765605 | 80323529 | Abnormal vibration in 30A Pump | S3CW -3CWE5-MTRD | * **************Incident Description************** * Notification 000030765605 Details * *********************************************************** * 05/03/2017 10:24:43 INCIDENT REPORT (INCIDENT REPORT) * Report submitted by: Mark Johnson ENTITY\INCIDENT: * * CONDITION DESCRIPTION/LOCATION (THE INAPPROPRIATE ACTION AND ITS NEGATIVE EFFECT/INCLUDE A DETAILED LOCATION DESCRIPTION): * During normal operation, abnormal vibration was noticed on 30A pump. Cooling Tower 3 indicates that the vibration level was higher than normal operating range of the pump. Vibration monitoring system in S3CW -3CWE5-MTRD indicated potential issue. * * ACTIVITIES, PROCESSES, PROCEDURES INVOLVED: * S3.OP.MO.CW-0001, Standard operation and maintenance procedures * * WHY DID CONDITION HAPPEN? * Cause remains unknown but might be due to potential mechanical failure or wear of parts. * * CONSEQUENCES: * Potential system failure or damage to pump if not resolved. * * REQUIREMENTS IMPACTED: * Normal operation of pump * * ADVERSE PHYSICAL CONDITIONS: * Higher than normal operating range vibration in 30A Pump * * WHO WAS NOTIFIED: * Operations Supervisor, Maintenance Team * * KNOWLEDGEABLE INDIVIDUALS: * Clark, Jenkins, Adams * * REPEAT OR SIMILAR CONDITION: * No similar condition reported earlier * * IMMEDIATE ACTIONS AND RECOMMENDED ACTIONS: * Temporary shutdown and immediate inspection of 30A Pump. If issue persists, detailed maintenance investigation may be required. * * Updated: MARK JOHNSON 05.03.2017 15:35:27 * ------------------------------------------------------------ * 05/05/2017 08:54:45 LUCY GREEN (INCIDENT) * Inspection of 30A pump revealed slight damage in the impeller, which was likely causing the vibration. Parts have been replaced, pump has been reassembled and vibration levels are back in the normal range. System is back online. | What was the initial condition reported about the 30A pump? | During normal operation, abnormal vibration was noticed on 30A pump. Cooling Tower 3 indicates that the vibration level was higher than normal operating range of the pump.
316 | 2020-07-22 | 40750302 | 90193866 | Unexpected voltage drop in 16B Pump | S4CW -4CWE7 | * **************Incident Description************** * Notification 000040750302 Details * *********************************************************** * 07/22/2020 18:31:44 INCIDENT REPORT (INCIDENT REPORT) * Report submitted by: Sarah Green ENTITY\INCIDENT: * * CONDITION DESCRIPTION/LOCATION (THE INAPPROPRIATE ACTION AND ITS NEGATIVE EFFECT/INCLUDE A DETAILED LOCATION DESCRIPTION): * While conducting routine monitoring, noted an unexpected voltage drop in 16B pump. The voltage drop was significant, from 400V to 320V, but the pump was still on. Based on historical data, there has never been such a voltage drop in this pump. * * ACTIVITIES, PROCESSES, PROCEDURES INVOLVED: * Routine monitoring * * WHY DID CONDITION HAPPEN? * Cause not immediately known. Potential electrical supply issue or internal pump malfunction. * * CONSEQUENCES: * Potential motor damage and reduction in operational efficiency. * * REQUIREMENTS IMPACTED: * Normal pumping operation * * ADVERSE PHYSICAL CONDITIONS: * Significant voltage drop in 16B Pump * * WHO WAS NOTIFIED: * Electrician Team/ INCIDENT TEAM * * KNOWLEDGEABLE INDIVIDUALS: * Incident Team, Electrical Engineer * * REPEAT OR SIMILAR CONDITION: * No, this is the first incident of this nature * * IMMEDIATE ACTIONS AND RECOMMENDED ACTIONS: * Electrician Team to investigate the 16B Pump and rectify any faults detected. * 07/23/2020 09:24:57 SARAH GREEN (INCIDENT) * After investigation, it was found that one of the phases of supply was faulty. The electrician team repaired it and the pump is now functioning normally. | What immediate action was taken in response to the unexpected voltage drop in the pump? | Electrician Team to investigate the 16B Pump and rectify any faults detected.
317 | 2019-02-11 | 30788543 | 80223435 | 13B Due to oil leakage, pump motor replacement required | S4CW -4CWE4-MTRD | * **************Incident Description************** * Notification 000030788543 Details * *********************************************************** * SUMMARY: ATTENTION TO THE "MAINTENANCE PROCEDURE FOR MOTOR REPLACEMENT" * * 1) CONDITION DESCRIPTION/LOCATION (THE UNDESIRABLE ACTION AND ITS NEGATIVE EFFECT/INCLUDED A DETAILED LOCATION DESCRIPTION): * On 02/11/19 at 0750, during a maintenance operation on 13B pump, there was an unusually high volume of oil leakage. The Pump was shut down immediately and the area was properly cleaned up. Upon further inspection, a crack in the oil reservoir was found indicating the need for a motor replacement. * * 2) ACTIVITIES, PROCESSES, PROCEDURES INVOLVED: * S4.OP.AB-CW-0001, S4.OP-SO.CW-0002 * * 3) WHY DID CONDITION HAPPEN? * The anticipated reason could be due to the pump's high operating age, causing wear and tear. * * 4) CONSEQUENCES: * This incident could potentially cause a temporary decrease in overall output and increased maintenance costs. * * 5) REQUIREMENTS IMPACTED: * Pump replacement needed * * 6) ADVERSE PHYSICAL CONDITION: * Cracked motor oil reservoir on the 13B Pump, oil leakage observed. * * 7) WHO WAS NOTIFIED: * Maintenance Supervisor, Safety Department * * 8) KNOWLEDGEABLE INDIVIDUALS: * Williams, Harris, And Roberts * * 9) REPEAT OR SIMILAR CONDITION: * No, this is not a repeated issue. * * 10) IMMEDIATE AND RECOMMENDED ACTIONS: * Order and replace motor for 13B Pump. * Assess other pumps for a preventive maintenance schedule. * * Updated: ROBERT JOHNSON 02.11.2019 15:27:34 * ----------------------------------------------------------- * 02/21/2019 11:25:35 WILLIAM HOWARD (MUSER) * A new pump | What was the main issue encountered with the 13B pump during the maintenance operation? | On 02/11/19 at 0750, during a maintenance operation on 13B pump, there was an unusually high volume of oil leakage. The Pump was shut down immediately and the area was properly cleaned up. Upon further inspection, a crack in the oil reservoir was found indicating the need for a motor replacement.
318 | 2020-12-24 | 308935769 | 90253470 | Unstable readings from Pump 3A | S4CW -4CWE2 | * **************Incident Description************** * Notification 0000308935769 Details * *********************************************************** * 12/24/2020 10:56:15 INCIDENT REPORT (INCIDENT REPORT) * Report submitted by: Regina Williams ENTITY\INCIDENT: * * CONDITION DESCRIPTION/LOCATION (THE INAPPROPRIATE ACTION AND ITS NEGATIVE EFFECT/INCLUDE A DETAILED LOCATION DESCRIPTION): * On 12/24/20 during a routine status check, it was noted that Pump 3A was exhibiting unstable pressure readings. The fluctuations were not consistent with standard operational patterns. This could indicate internal mechanical issues or a malfunctioning sensor. * * ACTIVITIES, PROCESSES, PROCEDURES INVOLVED: * S4.OP.AB-CW-0001, S4.OP-SO.CW-0002 * * WHY DID CONDITION HAPPEN? * The cause for the unstable readings is currently unknown. There is a need for further investigation. * * CONSEQUENCES: * If left unattended, this could lead to serious mechanical issues or sensor failure. * * REQUIREMENTS IMPACTED: * Standard operational pressure readings * * ADVERSE PHYSICAL CONDITIONS: * Unstable pressure readings from Pump 3A * * WHO WAS NOTIFIED: * Supervisor, Maintenance Team, Control Room * * KNOWLEDGEABLE INDIVIDUALS: * Thompson, Davis, Ross * * REPEAT OR SIMILAR CONDITION: * No, this is the first incident of unstable readings from this pump. * * IMMEDIATE ACTIONS AND RECOMMENDED ACTIONS: * Technicians to prioritize investigation and inspection of Pump 3A. Check both mechanical components and monitoring sensors for any irregularities. * 12/27/2020 14:17:30 REGINA WILLIAMS (INCIDENT) * Investigation has been completed. Results indicated a faulty sensor causing the unstable pressure readings. The sensor has now been replaced, and the pump is operating normally. Further monitoring has been recommended to ensure stability. | What was the immediate action taken after the incident involving unstable pressure readings from Pump 3A? | Technicians to prioritize investigation and inspection of Pump 3A. Check both mechanical components and monitoring sensors for any irregularities.
319 | 2018-11-30 | 30748102 | 80230589 | Noise from 20C Pump Motor | S3CW -3CWE7 | * **************Incident Description************** * Notification 000030748102 Details * *********************************************************** * 11/30/2018 18:25:13 INCIDENT REPORT (INCIDENT REPORT) * Report submitted by: Dave Miller 123-789-4560 * ENTITY\INCIDENT: * CONDITION DESCRIPTION/LOCATION (THE INAPPROPRIATE ACTION AND ITS NEGATIVE EFFECT/INCLUDE A DETAILED LOCATION DESCRIPTION): * During regular inspection, excessive mechanical noise was heard from the 20C Pump motor. The noise threshold for the 20C Pump has always been steady, but there was a distinct elevation in the noise level noticeable at the time of observation. Immediate shut down and inspection were initiated. * * ACTIVITIES, PROCESSES, PROCEDURES INVOLVED: * Regular inspection and emergency shutdown * * WHY DID CONDITION HAPPEN? * Initial investigation points towards wear and tear, but detailed inspection to follow. * * CONSEQUENCES: * If not addressed, could lead to loss of pump functionality and efficiency. * * REQUIREMENTS IMPACTED: * Potential future maintenance shutdown and repair could cause pump downtime. * * ADVERSE PHYSICAL CONDITIONS: * Increased noise from the 20C pump motor * * WHO WAS NOTIFIED: * Control Room, Maintenance Team, Supervisor * * KNOWLEDGEABLE INDIVIDUALS: * Chambers, Watson, Green * * REPEAT OR SIMILAR CONDITION: * The first instance of such a condition for 20C pump. * * IMMEDIATE ACTIONS AND RECOMMENDED ACTIONS: * Investigation into the exact cause of increased noise, potential maintenance and repair if necessary. * * Updated: DAVE MILLER 11.30.2018 20:45:12 * ------------------------------------------------------------ * 12/03/2018 09:02:19 JANE SMITH (NUSER) * The inspection revealed a worn-out bearing causing the excessive noise. The faulty part was replaced and the pump is back in full operation. Early detection helped in quick resolution without any major impact. | What was the identified cause for the increased mechanical noise from the 20C Pump motor? | The inspection revealed a worn-out bearing causing the excessive noise.
320 | 2019-04-30 | 30832569 | 80232456 | 25B elevator motor unresponsiveness | S4EL -4ELE4 | * **************Incident Description************** * Notification 000030832569 Details * *********************************************************** * 04/30/2019 10:35:15 INCIDENT REPORT (INCIDENT REPORT) * Report submitted by: Elizabeth Taylor ENTITY\INCIDENT: * * CONDITION DESCRIPTION/LOCATION (THE INAPPROPRIATE ACTION AND ITS NEGATIVE EFFECT/INCLUDE A DETAILED LOCATION DESCRIPTION): * During the morning shift while initiating Elevator 25B, the motor didn't respond. Attempted reset but still unresponsive. No visible external damage was identified. This behavior is not typical for Elevator 25B. * * ACTIVITIES, PROCESSES, PROCEDURES INVOLVED: * S4.OP-AB.EL-0002, S4.OP-SO.EL-0001 * * WHY DID CONDITION HAPPEN? * Unknown at this time. Possibly due to electrical issues or internal component failure. * * CONSEQUENCES: * Temporary loss of elevator. Impact on time efficiency. * * REQUIREMENTS IMPACTED: * Normal elevator operation. * * ADVERSE PHYSICAL CONDITIONS: * Unresponsiveness of 25B elevator motor. * * WHO WAS NOTIFIED: * Maintenance Team, Supervisor. * * KNOWLEDGEABLE INDIVIDUALS: * Maintenance Team, Supervisor. * * REPEAT OR SIMILAR CONDITION: * No, this is an unprecedented incident. * * IMMEDIATE ACTIONS AND RECOMMENDED ACTIONS: * Technical team to investigate and rectify the issue with Elevator 25B motor. * 04/30/2019 15:24:50 ELIZABETH TAYLOR (INCIDENT) * The maintenance team identified a fault in the circuit breaker associated with the motor. This was replaced and the elevator is now back in service. Follow up checks will be required to watch for any further complications. | What immediate actions were taken after the failure of Elevator 25B motor? | Technical team to investigate and rectify the issue with Elevator 25B motor.
321 | 2022-02-15 | 30980012 | 90081523 | 7D pump decreased pressure post-servicing | S4CW -4CWE7 | * **************Incident Description************** * Notification 000030980012 Details * *********************************************************** * 02/15/2022 17:29:00 INCIDENT REPORT (INCIDENT REPORT) * Report submitted by: Liam Richardson ENTITY\INCIDENT: * * CONDITION DESCRIPTION/LOCATION (THE INAPPROPRIATE ACTION AND ITS NEGATIVE EFFECT/INCLUDE A DETAILED LOCATION DESCRIPTION): * In 12/2021, notification 30902123 identified that 7C Pump returned from maintenance with a decreased pressure level. The issue was resolved under work order 90012390 and procedure revision was issued in January 2022 for S4.OP-SO.CW-0002 to update the guidance for lower pressure levels. This change was based on data from work order 90011722 which was used to replace the 7C pump motor. However, recently, 7D pump was serviced in February 2022 under work order 90081450 and returned to service with decreased pressure. It seems that updates to the pump components may be altering the normal pressure values exhibited by the motors. This calls for clear identification of the alterations made to the pumps and motors to help develop proper guidance and update procedures. * * ACTIVITIES, PROCESSES, PROCEDURES INVOLVED: * Observation of motor pressure differences and review of existing procedure guidance in S4.OP-SO.CW-0002. * * WHY DID CONDITION HAPPEN? * Uncertain why procedure changes were not identified prior to field changes. * * CONSEQUENCES: * Insufficient guidelines in CW procedures for pressure limits. * * REQUIREMENTS IMPACTED: * Equipment reliability needs to be ensured by maintaining appropriate pressure margins for motors in operation. * * ADVERSE PHYSICAL CONDITIONS: * No * * WHO WAS NOTIFIED: * Supervisor, Maintenance Team * * KNOWLEDGEABLE INDIVIDUALS: * Supervisor, Maintenance Team, Engineers * * REPEAT OR SIMILAR CONDITION: * Yes, appears similar to notification 30902123 which was resolved but similar event arose. * * IMMEDIATE ACTIONS AND RE | What was the issue identified with the 7C and 7D pumps? | In 12/2021, notification 30902123 identified that 7C Pump returned from maintenance with a decreased pressure level. However, recently, 7D pump was serviced in February 2022 under work order 90081450 and returned to service with decreased pressure. It seems that updates to the pump components may be altering the normal pressure values exhibited by the motors.
322 | 2019-10-30 | 30974203 | 90112345 | Increase in 17B pump vibration post maintenance | S4CW -4CWE7 | * **************Incident Description************** * Notification 000030974203 Details * *********************************************************** * 10/30/2019 15:22:00 INCIDENT REPORT (INCIDENT REPORT) * Report submitted by: William Green ENTITY\INCIDENT: * * CONDITION DESCRIPTION/LOCATION (THE INAPPROPRIATE ACTION AND ITS NEGATIVE EFFECT/INCLUDE A DETAILED LOCATION DESCRIPTION): * The 17B Pump, serviced under work order 90112345, has shown increased vibration levels since its return to service. While not exceeding allowable limits, the figures are unusual compared to historical data available for this unit, and have the potential to contribute to faster wear and tear of the equipment. * * ACTIVITIES, PROCESSES, PROCEDURES INVOLVED: * Regular maintenance and vibration monitoring procedures followed as per S4.OP-SO.CW-0001. * * WHY DID CONDITION HAPPEN? * The direct cause of the increased vibration is unknown. It may be due to imbalances in the pump or motor, or changes made during the maintenance activity. * * CONSEQUENCES: * If unchecked, increased vibration can lead to premature equipment damage or failure. * * REQUIREMENTS IMPACTED: * Normal pump operation that might need to be adjusted to compensate for increased vibration. * * ADVERSE PHYSICAL CONDITIONS: * Increased vibrations in the 17B Pump. * * WHO WAS NOTIFIED: * Maintenance Supervisor, Vibration Analysis Team * * KNOWLEDGEABLE INDIVIDUALS: * Maintenance Supervisor, Vibration Analysis Team Members * * REPEAT OR SIMILAR CONDITION: * No, this is the first observed instance for the 17B Pump. * * IMMEDIATE ACTIONS AND RECOMMENDED ACTIONS: * Vibration Analysis Team to investigate the cause of the increased vibrations and recommend the appropriate adjustment or repair as required. * 11/01/2019 10:20:21 JAMES DOE (INCIDENT) * Vibration analysis indicates harmonics from the motor may be causing the vibrations. Team is investigating if motor and pump balance needs correction. Further updates to follow. | What were the immediate actions taken in response to the increased vibrations in the 17B Pump? | Vibration Analysis Team to investigate the cause of the increased vibrations and recommend the appropriate adjustment or repair as required.
323 | 2017-12-12 | 30874295 | 80235871 | Abnormal vibration at turbine 5A | S4TR -4TRA5-VBX | * **************Incident Description************** * Notification 000030874295 Details * *********************************************************** * 12/12/2017 14:22:00 INCIDENT REPORT (INCIDENT REPORT) * Report submitted by: Robert Peterson ENTITY\INCIDENT: * * CONDITION DESCRIPTION/LOCATION (THE INAPPROPRIATE ACTION AND ITS NEGATIVE EFFECT/INCLUDE A DETAILED LOCATION DESCRIPTION): * During the shift transition, abnormal vibration was noticed on the 5A Turbine. The vibration levels were significantly higher than usual and exceeded set thresholds. The operation was promptly halted, and an emergency inspection was initiated. No visible external damage was detected; however, internal damages can't be ruled out. Until a detailed inspection, 5A Turbine stays offline, causing operational disruptions. * * ACTIVITIES, PROCESSES, PROCEDURES INVOLVED: * Turbine operation and emergency inspection procedures namely S4.OP-TR-CW-0001, S4.OP-TB-VD-0005. * * WHY DID CONDITION HAPPEN? * Unknown, potentially due to unaligned shaft or bearing damage. * * CONSEQUENCES: * Loss of operational efficiency because the turbine is offline and possible internal turbine damage. * * REQUIREMENTS IMPACTED: * The outage of 5A Turbine causes disruption in normal turbine operations. * * ADVERSE PHYSICAL CONDITIONS: * Abnormally high vibration levels at 5A Turbine. * * WHO WAS NOTIFIED: * Maintenance Team, Operations Supervisor * * KNOWLEDGEABLE INDIVIDUALS: * Ross Thompson, Lucas McKay, Jennifer Baker * * REPEAT OR SIMILAR CONDITION: * No, this is the first reported case. * * IMMEDIATE ACTIONS AND RECOMMENDED ACTIONS: * Request a detailed inspection and repair as necessary before reintegrating into the system. * 12/12/2017 18:57:03 ROBERT PETERSON (INCIDENT) * Maintenance team has been notified, and the in-depth examination of the turbine is scheduled for tomorrow morning. If repair is necessary, it will be planned accordingly. | What were the observed physical conditions during the abnormal incident at the turbine? | During the shift transition, abnormal vibration was noticed on the 5A Turbine. The vibration levels were significantly higher than usual and exceeded set thresholds.
324 | 2018-09-14 | 30879529 | 80235648 | Excess vibration from 13B Pump Motor | S3CW -3CWE5 | * **************Incident Description************** * Notification 000030879529 Details * *********************************************************** * 09/14/2018 14:29:00 INCIDENT REPORT (INCIDENT REPORT) * Report submitted by: Mark Thompson ENTITY\INCIDENT: * * 1) CONDITION DESCRIPTION/LOCATION (THE INAPPROPRIATE ACTION AND ITS NEGATIVE EFFECT/INCLUDE A DETAILED LOCATION DESCRIPTION): * At 1345 hours, operator reported excess vibration from the 13B Pump Motor in Unit 3. Shutdown the system from Control Room. Initial inspection did not show any noticeable damage and other system parameters were within operational range. S3.OP-AB.CW-0001 Pump Abnormality procedure was initiated due to the shutdown of 13B Pump. * * 2) ACTIVITIES, PROCESSES, PROCEDURES INVOLVED: * S3.OP.AB-CW-0001, S3.OP-SO.CW-0001 * * 3) WHY DID CONDITION HAPPEN? * Unknown. Past incidents of pump vibrations have been linked to misalignment but other causes can't be ruled out just yet. * * 4) CONSEQUENCES: * Potential damage to pump and disruption of normal operations. * * 5) REQUIREMENTS IMPACTED: * Unavailable pump, disrupted system operations. * * 6) ADVERSE PHYSICAL CONDITION: * Excess vibration from 13B Pump Motor, potential internal damage. * * 7) WHO WAS NOTIFIED: * Control Room, Maintenance Team * * 8) KNOWLEDGEABLE INDIVIDUALS: * Mark Thompson, Johnson, Smith * * 9) REPEAT OR SIMILAR CONDITION: * Yes, not frequent but has happened before. * * 10) IMMEDIATE AND RECOMMENDED ACTIONS: * Maintenance team to inspect and rectify the 13B Pump Motor problem. * 09/16/2018 17:25:15 MARK THOMPSON (INCIDENT) * The pump was inspected and it was found that misalignment and imbalance of the motor were causing the vibration. The motor was realigned | What was the immediate action recommended after the incident of excess vibration from the 13B Pump Motor? | Maintenance team to inspect and rectify the 13B Pump Motor problem.
325 | 2020-11-21 | 31078463 | 90248753 | Unusual vibration in 32C cooling unit | S3CW -3CWE8 | * **************Incident Description************** * Notification 000031078463 Details * *********************************************************** * 11/21/2020 08:41:13 INCIDENT REPORT (INCIDENT REPORT) * Report submitted by: Thomas Mitchell ENTITY\INCIDENT: * * CONDITION DESCRIPTION/LOCATION (THE INAPPROPRIATE ACTION AND ITS NEGATIVE EFFECT/INCLUDE A DETAILED LOCATION DESCRIPTION): * At 06:00 on 21/11/20, during routine inspection, an unusual vibration was observed in the 32C cooling unit. The equipment was immediately isolated and inspection initiated. The vibration subsided upon isolation. No immediate damages or leaks were observed. However, there was an undue strain on the drive belts. The operations of adjacent units are currently not affected. * * ACTIVITIES, PROCESSES, PROCEDURES INVOLVED: * Routine inspection, isolation of the suspect unit * * WHY DID CONDITION HAPPEN? * Unknown, possibly due to misalignment or wear and tear of the drive belts. * * CONSEQUENCES: * The unit was temporarily shut down, causing a reduction in cooling efficiency. Extended operation in this state could lead to significant equipment damage. * * REQUIREMENTS IMPACTED: * Normal functioning of the cooling unit * * ADVERSE PHYSICAL CONDITIONS: * Unusual vibration in the 32C cooling unit which led to the shutdown of the equipment * * WHO WAS NOTIFIED: * Supervisor, Operation and Maintenance Team * * KNOWLEDGEABLE INDIVIDUALS: * Thomas Mitchell, Supervisor, Maintenance Team * * REPEAT OR SIMILAR CONDITION: * No known similar conditions reported earlier * * IMMEDIATE ACTIONS AND RECOMMENDED ACTIONS: * Detailed inspection of the drive belts and other components of the unit has been scheduled. If required, worn-out components may need to be replaced. * 11/23/2020 14:27:45 JEFF DAVIS (MAINTENANCE) * Inspection completed and it was observed that misalignment in the drive assembly resulted in unusual vibrations. The unit has been reassembled after correction and | What immediate and recommended actions were taken after the detection of the unusual vibration in the cooling unit? | Detailed inspection of the drive belts and other components of the unit has been scheduled. If required, worn-out components may need to be replaced. Inspection completed and it was observed that misalignment in the drive assembly resulted in unusual vibrations. The unit has been reassembled after correction.
326 | 2019-02-27 | 30790456 | 80199600 | 34B Pump Motor Hesitation | S4CW -4CWE5-BLT | * **************Incident Description************** * Notification 000030790456 Details * *********************************************************** * 02/27/2019 15:20:10 INCIDENT REPORT (INCIDENT REPORT) * Report submitted by: Thomas King 987-654-3210 ENTITY\INCIDENT: * CONDITION DESCRIPTION/LOCATION (THE INAPPROPRIATE ACTION AND ITS NEGATIVE EFFECT/INCLUDE A DETAILED LOCATION DESCRIPTION): * At approximately 1410, during the operational check, 34B Pump exhibited slight hesitation and fluctuations in the reading. The water pressure was noted to be inconsistent. Additionally, there was a minor leak observed from the vicinity of the pump that could be responsible for the irregularity in the pump behavior. * * ACTIVITIES, PROCESSES, PROCEDURES INVOLVED: * Operational check carried out as part of procedure S4.OP.AB-CW-0030 * * WHY DID CONDITION HAPPEN? * Suspected damage or wear to internal pump components. Also possible seal leakage. * * CONSEQUENCES: * Reduced operational efficiency, potential for further pump damage. * * REQUIREMENTS IMPACTED: * Operational check procedures, normal pump operation. * * ADVERSE PHYSICAL CONDITIONS: * Hesitation in pump operation, minor leakage. * * WHO WAS NOTIFIED: * Duty Supervisor, Maintenance Team * * KNOWLEDGEABLE INDIVIDUALS: * Pump Operation Team, Maintenance Team * * REPEAT OR SIMILAR CONDITION: * No, first occurrence. * * IMMEDIATE ACTIONS AND RECOMMENDED ACTIONS: * Initiate isolation and inspection of the pump. If leakage from seals is confirmed, replace seals and perform maintenance check. If damage to pump components is identified, replace or repair as necessary. * 02/27/2019 18:30:56 THOMAS KING (INCIDENT) * Isolation and inspection initiated. Parts on order. Await further notification on repair actions. | What immediate actions were recommended following the incident with the 34B Pump? | Initiate isolation and inspection of the pump. If leakage from seals is confirmed, replace seals and perform maintenance check. If damage to pump components is identified, replace or repair as necessary.
327 | 2019-12-16 | 30874010 | 80223944 | 18D Pump power fluctuation | S1PW -1PWE7-PUMP | * **************Incident Description************** * Notification 000030874010 Details * ------------------------------------------------------------ * 12/16/2019 14:31:08 INCIDENT REPORT (INCIDENT REPORT) * Report submitted by: Daniel Thompson 234-532-8901 ENTITY\INCIDENT: * * CONDITION DESCRIPTION/LOCATION (THE INAPPROPRIATE ACTION AND ITS NEGATIVE EFFECT/INCLUDE A DETAILED LOCATION DESCRIPTION): * During a routine operation, it was noticed that 18D Pump was experiencing power fluctuations resulting in irregular operation. This was spotted in the power monitoring system with spikes and drops in supply electricity. It was surprising considering that other equipment on the same power grid was operating normally. * * ACTIVITIES, PROCESSES, PROCEDURES INVOLVED: * Normal operation was involved along with Power monitoring. * * WHY DID CONDITION HAPPEN? * Exact cause is unknown, potential reasons could include pump internal defect, or a problem with the power supply specifically to this pump. * * CONSEQUENCES: * Potentially significant if the pump malfunctions or stops. * * REQUIREMENTS IMPACTED: * Normal power supply and pump operation. * * ADVERSE PHYSICAL CONDITIONS: * Voltage fluctuations in the power supply to 18D Pump. * * WHO WAS NOTIFIED: * Supervisor, Electrical Maintenance Team * * KNOWLEDGEABLE INDIVIDUALS: * The electrical maintenance team members and the supervisor * * REPEAT OR SIMILAR CONDITION: * No, not previously reported in this unit. * * IMMEDIATE ACTIONS AND RECOMMENDED ACTIONS: * The electrical maintenance team is recommended to carry out a detailed inspection of both the power supply system and the internal mechanism of the 18D pump. * 12/18/2019 10:33:04 DANIEL THOMPSON (INCIDENT) * The Maintenance team inspected and rectified the issue. A faulty circuit breaker was causing the power fluctuations. It has now been replaced and the pump is back to normal operation. | What immediate actions were recommended after the power fluctuations in the 18D Pump were observed? | The electrical maintenance team is recommended to carry out a detailed inspection of both the power supply system and the internal mechanism of the 18D pump.
328 | 2016-09-25 | 30778932 | 80251836 | 33B Pump abnormal temperature rise | S1CW -1CWE3 | * **************Incident Description************** * Notification 000030778932 Details * *********************************************************** * 09/25/2016 16:30:34 INCIDENT REPORT (INCIDENT REPORT) * Report submitted by: David Johnson ENTITY\INCIDENT: * * CONDITION DESCRIPTION/LOCATION (THE INAPPROPRIATE ACTION AND ITS NEGATIVE EFFECT/INCLUDE A DETAILED LOCATION DESCRIPTION): * 33B Pump motor temperature rose 10 degrees higher than other pumps at the same load and duty. This occurred following maintenance under work order 80221456 despite tests showing normal operation and no anomalies on the bench. * * ACTIVITIES, PROCESSES, PROCEDURES INVOLVED: * S1.OP.SO.CW-0002, Routine check * * WHY DID CONDITION HAPPEN? * Initial cause unknown, could be due to hidden damage or changes in maintenance procedure * * CONSEQUENCES: * Immediate impacts are none, but potential motor failure could lead to disruption in normal operations * * REQUIREMENTS IMPACTED: * Normal plant operation * * ADVERSE PHYSICAL CONDITIONS: * Abnormally high temperature in 33B pump motor * * WHO WAS NOTIFIED: * Maintenance Supervisor, Operations Manager * * KNOWLEDGEABLE INDIVIDUALS: * Maintenance workers, supervisors, engineering staff * * REPEAT OR SIMILAR CONDITION: * Previously similar but not the same, notification 30694282 * * IMMEDIATE ACTIONS AND RECOMMENDED ACTIONS: * Investigate possible causes of abnormal temperature, check the maintenance procedure * 09/26/2016 10:00:52 DAVID JOHNSON (INCIDENT) * An investigation into the pump operation is expected. Maintenance procedures are being reviewed to see if any improvements can be made. | What were the initial actions recommended following the rise in 33B pump motor temperature? | Investigate possible causes of abnormal temperature, check the maintenance procedure.
329 | 2021-09-10 | 30978512 | 80456320 | Unexpected vibration in 34A pump | S4CW -4CWE9 | * **************Incident Description************** * Notification 000030978512 Details * *********************************************************** * 09/10/2021 07:45:17 INCIDENT REPORT (INCIDENT REPORT) * Report submitted by: Emily Smith ENTITY\INCIDENT: * * CONDITION DESCRIPTION/LOCATION (THE INAPPROPRIATE ACTION AND ITS NEGATIVE EFFECT/INCLUDE A DETAILED LOCATION DESCRIPTION): * While monitoring operations, abnormal vibrations were noted on the 34A pump. Upon visual inspection, no visible factors like leaks or visible damage were found that could cause such abnormality. Measurements taken showed an increase in vibration levels by 20% compared to normal operation. * * ACTIVITIES, PROCESSES, PROCEDURES INVOLVED: * Vibration monitoring of operating pumps, S4.OP.AB-CW-0012 * * WHY DID CONDITION HAPPEN?: * The exact cause is unknown. The pump was serviced 6 months ago under work order 80238940. It is possible the balancing of the pump wasn't done properly. * * CONSEQUENCES: * Decreased pump efficiency, possible pump damage if the issue is not addressed timely. * * REQUIREMENTS IMPACTED: * Normal pump operation, can impact overall system performance * * ADVERSE PHYSICAL CONDITIONS: * Increased vibration levels in 34A pump than usual * * WHO WAS NOTIFIED: * Maintenance Supervisor, Engineering team * * KNOWLEDGEABLE INDIVIDUALS: * Jane Doe (Maintenance Supervisor), John Doe (Engineer) * * REPEAT OR SIMILAR CONDITION: * No, this is the first incidence of abnormal vibration in 34A pump * * IMMEDIATE ACTIONS AND RECOMMENDED ACTIONS: * Engineering team to investigate the vibration issue, perform dynamic balancing if necessary. Maintenance team to carry out inspection for possible physical anomalies. * 09/12/2021 10:54:28 EMILY SMITH (INCIDENT) * The abnormal vibration seems to have been caused by imbalance. The pump was dynamically balanced and vibration levels returned to normal. The function of 34A pump has been successfully restored. | What was the incident observed during operations of the 34A pump and what were the consequent actions taken to rectify it? | While monitoring operations, abnormal vibrations were noted on the 34A pump... The pump was dynamically balanced and vibration levels returned to normal. The function of 34A pump has been successfully restored.
330 | 2016-02-18 | 30715723 | 80218910 | 8B Pump low pressure alert | S1CW -1CWE5-PLCF | * **************Incident Description************** * Notification 000030715723 Details * *********************************************************** * 02/18/2016 11:23:17 INCIDENT REPORT (INCIDENT REPORT) * Report submitted by: Robert Jackson, 123-456-7890 ENTITY\INCIDENT: * CONDITION DESCRIPTION/LOCATION (THE INAPPROPRIATE ACTION AND ITS NEGATIVE EFFECT/INCLUDE A DETAILED LOCATION DESCRIPTION): * As of 10:15 today, low pressure was detected at pump 8B. Inspection revealed that the pump’s output was less than usual, even though the inlet pressure was normal. No other abnormality was detected. * ACTIVITIES, PROCESSES, PROCEDURES INVOLVED: * General pump performance inspection, Pressure testing. * WHY DID CONDITION HAPPEN? * The exact cause is yet to be identified. Possible blockage or pump internal wear. * CONSEQUENCES: * Reduced flow rate, component strain, and potential pump failure. * REQUIREMENTS IMPACTED: * Normal pumping operation at designated pressure settings. * ADVERSE PHYSICAL CONDITIONS: * Sub-optimal pump pressure, potential pump damage. * WHO WAS NOTIFIED: * Operations Manager, Maintenance Team. * KNOWLEDGEABLE INDIVIDUALS: * Maintenance Team. * REPEAT OR SIMILAR CONDITION: * No prior instances with this pump but similar issues with other pumps. * IMMEDIATE ACTIONS AND RECOMMENDED ACTIONS: * Complete pressure tests and if necessary, disassemble the pump for a thorough inspection. Plan for possible replacements if required. * 02/18/2016 14:32:45 ROBERT JACKSON (INCIDENT) * The maintenance team is inspecting the pump. No obvious signs of blockage, but more thorough checks will be conducted. | What immediate actions were recommended after the low pressure was detected in pump 8B? | Complete pressure tests and if necessary, disassemble the pump for a thorough inspection. Plan for possible replacements if required.
331 | 2020-10-25 | 30987645 | 80231564 | Power surge in 19B Pump motor | S2CW -2MTRD-1 | * **************Incident Description************** * Notification 000030987645 Details * *********************************************************** * 09/25/2020 11:19:43 INCIDENT REPORT (INCIDENT REPORT) * Report submitted by: Derek Anderson, ENTITY\INCIDENT: * CONDITION DESCRIPTION/LOCATION (THE INAPPROPRIATE ACTION AND ITS NEGATIVE EFFECT/INCLUDE A DETAILED LOCATION DESCRIPTION): * At 1042 on 10/25/20, it was reported that 19B Pump experienced sudden power surge causing the protective systems to trip. After inspection, no visible damage was found externally, but the pump motor read high residual currents upon restarting. * * ACTIVITIES, PROCESSES, PROCEDURES INVOLVED: * Operation procedures S2.GD.MTRD-01 and safety procedure S2.GD.MTRD-02 * * WHY DID CONDITION HAPPEN? * The cause is unknown yet, although power surges have happened in facility in severe weather conditions. * * CONSEQUENCES: * Possible internal electrical damage requiring full maintenance intervention. * * REQUIREMENTS IMPACTED: * High voltage safety procedures. * * ADVERSE PHYSICAL CONDITIONS: * High residual current on pump motor, possible internal electrical damage * * WHO WAS NOTIFIED: * Control Room, Maintenance Team * * KNOWLEDGEABLE INDIVIDUALS: * O'Brian, Scott, Williams * * REPEAT OR SIMILAR CONDITION: * No * * IMMEDIATE ACTIONS AND RECOMMENDED ACTIONS: * Ensure surrounding equipment is safe and request for maintenance team to inspect 19B Pump Motor. * * 09/28/2020 08:30:51 MARK LEE (INCIDENT) * The maintenance team investigated the 19B Pump Motor thoroughly and they have concluded the insulation in the motor was slighty damaged due to the surge, causing the high residual current. The motor was tested, repaired and re-installed. It is now back to normal operation. | What immediate and recommended actions were taken after the incident with the 19B Pump? | Ensure surrounding equipment is safe and request for maintenance team to inspect 19B Pump Motor.
332 | 2019-11-12 | 30875329 | 90245218 | Leakage in Compressor 78B | S4CW -4CWE9 | * **************Incident Description************** * Notification 000030875329 Details * *********************************************************** * 11/12/2019 04:22:20 INCIDENT REPORT (INCIDENT REPORT) * Report submitted by: Emma Patterson ENTITY\INCIDENT: * * CONDITION DESCRIPTION/LOCATION (THE INAPPROPRIATE ACTION AND ITS NEGATIVE EFFECT/INCLUDE A DETAILED LOCATION DESCRIPTION): * At 0422 hours on 11/12/19, the maintenance team and on-duty operator noticed a leakage in the Compressor 78B. The machine was promptly stopped, and the leakage was controlled. Later analysis revealed that the leakage was due to a slight crack in one of the sealing surfaces. No injuries or collateral damage have been reported. * * ACTIVITIES, PROCESSES, PROCEDURES INVOLVED: * Regular on-duty patrol and observation of machinery * * WHY DID CONDITION HAPPEN? * Preliminary investigations reveal that an unnoticed manufacturing defect or significant wear and tear could be the cause of the crack. * * CONSEQUENCES: * The compressor unit is currently non-operational, which might affect the efficiency of the process until a replacement or repair is carried out. * * REQUIREMENTS IMPACTED: * Efficiency of the overall process * * ADVERSE PHYSICAL CONDITIONS: * Leakage from Compressor 78B * * WHO WAS NOTIFIED: * On-duty supervisor, Safety-team, Maintenance Manager * * KNOWLEDGEABLE INDIVIDUALS: * Safety Team, Operations Team, Maintenance Manager * * REPEAT OR SIMILAR CONDITION: * No previous record of a similar issue * * IMMEDIATE ACTIONS AND RECOMMENDED ACTIONS: * The crack has been temporarily sealed for now. A detailed inspection of the compressor components is recommended, and necessary action should be taken for repair or replacement. * 11/12/2019 06:32:01 JOHN DOE (INCIDENT) * The maintenance team will inspect the compressor thoroughly, and further actions will be taken based on their report. The supervisor will keep the management updated about the matter. | Why did the leakage in Compressor 78B happen? | Preliminary investigations reveal that an unnoticed manufacturing defect or significant wear and tear could be the cause of the crack.
333 | 2020-04-15 | 40753190 | 90129564 | 3A generator excessive vibration | S4GE -4GEN2 | * **************Incident Description************** * Notification 000040753190 Details * *********************************************************** * 04/15/2020 07:30:45 INCIDENT REPORT (INCIDENT REPORT) * Report submitted by: Dan Gomez ENTITY\INCIDENT: * * CONDITION DESCRIPTION/LOCATION (THE INAPPROPRIATE ACTION AND ITS NEGATIVE EFFECT/INCLUDE A DETAILED LOCATION DESCRIPTION): * During a routine inspection, 3A generator was found to have significant vibration. Vibration was measured to be 60% above normal. Considering the generator has recently undergone maintenance under work order 90129564, the elevated vibration is abnormal. The integrity of the generator could be compromised with continued operation under these conditions. * * ACTIVITIES, PROCESSES, PROCEDURES INVOLVED: * S4.OP.AB-GE-0001, Routine inspection * * WHY DID CONDITION HAPPEN? * Unknown currently, might be due to misalignment or unbalanced rotor after maintenance. * * CONSEQUENCES: * Might lead to generator failure, downtime, and potential repair costs. * * REQUIREMENTS IMPACTED: * Normal operation schedule * * ADVERSE PHYSICAL CONDITIONS: * Excessive generator vibration * * WHO WAS NOTIFIED: * Supervisor, Maintenance Team, Safety Officer * * KNOWLEDGEABLE INDIVIDUALS: * Maintenance Team, Safety Officer, Engineers * * REPEAT OR SIMILAR CONDITION: * No * * IMMEDIATE ACTIONS AND RECOMMENDED ACTIONS: * Emergency shutdown of the generator for immediate investigation. Engineering team to conduct a thorough analysis to determine probable causes and remedial measures. * 04/15/2020 15:33:12 DAN GOMEZ (INCIDENT) * The analysis revealed that the issue was due to a temporary misalignment post-maintenance. Generator was realigned correctly, restarted, and operation resumed with normal vibration levels. | What immediate action was recommended after the abnormal generator vibration was discovered? | Emergency shutdown of the generator for immediate investigation. Engineering team to conduct a thorough analysis to determine probable causes and remedial measures.
334 | 2018-09-29 | 30865324 | 90179856 | Excessive vibration at 30B Pump | S4CW -4CWE7 | * **************Incident Description************** * Notification 000030865324 Details * *********************************************************** * 09/29/2018 15:23:37 INCIDENT REPORT (INCIDENT REPORT) * Report submitted by: Thomas Johnson 987-654-3210 ENTITY\INCIDENT: * CONDITION DESCRIPTION/LOCATION (THE INAPPROPRIATE ACTION AND ITS NEGATIVE EFFECT/INCLUDE A DETAILED LOCATION DESCRIPTION): * During the operation, MoV indicated excessive vibration at 30B Pump. The operator readings were confirmed by the onsite maintenance team. The pump was powered down and isolated for further inspection. Therewere no indications of leakage, heat or unusual noise from the pump prior to the incident. * * ACTIVITIES, PROCESSES, PROCEDURES INVOLVED: * S4.OP.AB-CW-0002, S4.OP-SO.CW-0002 * * WHY DID CONDITION HAPPEN? * The cause is uncertain at the time, possible issues may include worn out bearing, pump misalignment, or other mechanical wear and tear. * * CONSEQUENCES: * Possible delay in operations and potential damage to pump if unchecked. * * REQUIREMENTS IMPACTED: * Normal pump operations. * * ADVERSE PHYSICAL CONDITIONS: * High vibration at pump * * WHO WAS NOTIFIED: * Control Room, Maintenance Supervisor * * KNOWLEDGEABLE INDIVIDUALS: * Maintenance Team, On-duty Engineers * * REPEAT OR SIMILAR CONDITION: * No similar conditions were reported earlier. * * IMMEDIATE ACTIONS AND RECOMMENDED ACTIONS: * The pump was immediately powered down and scheduled for inspection. Depending on the inspection results, repair or replacements may be required. * 09/30/2018 16:42:18 THOMAS JOHNSON (INCIDENT) * The initial inspection indicates an bearing failure. A detailed inspection will follow to confirm and assess the overall condition of the pump. | What immediate actions were taken following the detection of high vibration at the pump? | The pump was immediately powered down and scheduled for inspection.
335 | 2020-11-24 | 31025467 | 80258963 | Potential Leaks Detected in Pump 15Z | S4HW -4HWE5 | * **************Incident Description************** * Notification 000031025467 Details * *********************************************************** * 11/24/2020 17:15:32 INCIDENT REPORT (INCIDENT REPORT) * Report submitted by: Emily Thompson 456-789-0123 * ENTITY\INCIDENT: * CONDITION DESCRIPTION/LOCATION (THE INAPPROPRIATE ACTION AND ITS NEGATIVE EFFECT/INCLUDE A DETAILED LOCATION DESCRIPTION): * Routine inspection indicated the potential for leaks in 15Z Pump. Small pools of fluid were observed near the pump, potentially originating from the pump housing. Current pump pressure read at 20 psig, which is 5 psig higher than normal. * ACTIVITIES, PROCESSES, PROCEDURES INVOLVED: * S4.OP.AB-HW-0001, S4.OP-SO.HW-0002 * WHY DID CONDITION HAPPEN? * The cause is presently unknown; possible seals failure. * CONSEQUENCES: * Fluid loss and reduction in pump efficiency. Potential damage to pump if unchecked. * REQUIREMENTS IMPACTED: * Normal operation, maintenance schedule * ADVERSE PHYSICAL CONDITIONS: * Potential leaks from 15Z Pump, potentially causing fluid loss * WHO WAS NOTIFIED: * Supervisor, Maintenance Team * KNOWLEDGEABLE INDIVIDUALS: * Maintenance Team, Engineers * REPEAT OR SIMILAR CONDITION: * No * IMMEDIATE ACTIONS AND RECOMMENDED ACTIONS: * Inspection and maintenance required on 15Z Pump to confirm and address potential leaks. * 11/25/2020 09:30:34 JOHN HARRISON (INCIDENT) * Inspection confirmed a leak at one seal. The seal was replaced and the pump is showing no further signs of leaking. Instructions for preventative maintenance updated. | What were the immediate and recommended actions after the incident with the 15Z Pump? | Inspection and maintenance required on 15Z Pump to confirm and address potential leaks.
336 | 2018-09-10 | 30985431 | 80236890 | Cooling system malfunction NJ12 | S4CW -4CWE2 | * **************Incident Description************** * Notification 000030985431 Details * *********************************************************** * 09/10/2018 07:30:00 INCIDENT REPORT (INCIDENT REPORT) * Report submitted by: Daniel Riley ENTITY\INCIDENT: * * 1) CONDITION DESCRIPTION/LOCATION (THE INAPPROPRIATE ACTION AND ITS NEGATIVE EFFECT/INCLUDE A DETAILED LOCATION DESCRIPTION): * During standard operation, the NJ12 Cooling System began to malfunction, showing high pressure levels and reduced flow rate. Based on system parameters, the issue seems to be in the circulation pump. * * 2) ACTIVITIES, PROCESSES, PROCEDURES INVOLVED: * Performing SOP S4.OP-SO.CW-0002, during the monitoring phase, variations in the parameters were noted. * * 3) WHY DID CONDITION HAPPEN? * Initial investigation suggests pump cavitation caused by pressure fluctuations, but further investigation required. * * 4) CONSEQUENCES: * If unresolved, risks overheating and potential damage to the connected system. * * 5) REQUIREMENTS IMPACTED: * Stable operation of the cooling system. * * 6) ADVERSE PHYSICAL CONDITIONS: * High pressure and reduced flow rate in cooling system pump. * * 7) WHO WAS NOTIFIED: * Chief Engineer; Safety Team * * 8) KNOWLEDGEABLE INDIVIDUALS: * Chief Engineer, Safety Team, Shift Supervisor * * 9) REPEAT OR SIMILAR CONDITION: * No, this is an unusual issue. * * 10) IMMEDIATE ACTIONS AND RECOMMENDED ACTIONS: * Shut down the faulty system temporarily. Replace or repair the pump involved. Further investigation is needed to identify root cause. * 09/12/2018 09:17:25 JOHN DOE (INCIDENT) * The cooling pump was swapped out with a new one and the system resumed normal operation. Further tests revealed that a worn-out impeller was the cause of the pressure increase. Recommendations are put in place to replace these impellers at set intervals to avoid future incidents. | What was the initial suspected cause for the malfunction of the NJ12 Cooling System? | Initial investigation suggests pump cavitation caused by pressure fluctuations, but further investigation required.
337 | 2022-11-10 | 40962215 | 80230910 | 35B Motor abnormal vibrations | S4CW -4CWE7 | * **************Incident Description************** * Notification 000040962215 Details * *********************************************************** * 11/10/2022 15:32:18 INCIDENT REPORT (INCIDENT REPORT) * Report submitted by: Robert Martin ENTITY\INCIDENT: * * CONDITION DESCRIPTION/LOCATION (THE INAPPROPRIATE ACTION AND ITS NEGATIVE EFFECT/INCLUDE A DETAILED LOCATION DESCRIPTION): * While performing regular checks, the operator found motor 35B vibrating more than usual. The operating conditions were normal with no recent changes in the load. Based on preliminary inspections, there were no major components failing, but the abnormality can't be ignored as it may cause future downtime if not addressed. * * ACTIVITIES, PROCESSES, PROCEDURES INVOLVED: * Regular operation checks, Initial assessment * * WHY DID CONDITION HAPPEN? * Unclear, potential misalignment or imbalance issues, needs further investigation. * * CONSEQUENCES: * Performance degradation, potential failure leading to downtime * * REQUIREMENTS IMPACTED: * Motor operation, Reliability and Maintenance * * ADVERSE PHYSICAL CONDITIONS: * Abnormal vibrations at Motor 35B * * WHO WAS NOTIFIED: * Supervisor, Maintenance Team * * KNOWLEDGEABLE INDIVIDUALS: * Technician Team, Supervisor * * REPEAT OR SIMILAR CONDITION: * No, first occurrence * * IMMEDIATE ACTIONS AND RECOMMENDED ACTIONS: * Submit a work order to investigate and resolve the issue. Execute a condition-monitoring plan for anomalous behavior and future prevention. * 11/15/2022 10:24:21 JOHN DOE (INCIDENT) * The maintenance team attended the issue and found that the root cause of the vibration was a bolt that had loosened over time. The bolt was tightened and vibration levels are now back to normal. | What was the cause of the abnormal vibrations at Motor 35B and what actions were taken to address the issue? | The maintenance team attended the issue and found that the root cause of the vibration was a bolt that had loosened over time. The bolt was tightened and vibration levels are now back to normal.
338 | 2022-02-23 | 30941502 | 80256340 | Unusual vibration at 18B Pump | S4CW -4CWE2 | * **************Incident Description************** * Notification 000030941502 Details * *********************************************************** * 02/23/2022 07:51:20 INCIDENT REPORT (INCIDENT REPORT) * Report submitted by: Lucas Green ENTITY\INCIDENT: * * 1) CONDITION DESCRIPTION/LOCATION: * During the early morning shift, operator noticed unusually high vibrations at 18B Pump. The oil temperature and pressure appeared normal, but the vibration exceeded 1.2 mils, which is above the acceptable limit. The pump was immediately shut down to avoid any potential damage. * * 2) ACTIVITIES, PROCESSES, PROCEDURES INVOLVED: * S4.OP.AB-CW-0003, S4.OP-SO.CW-0002 * * 3) WHY DID CONDITION HAPPEN: * Unknown at this time, requires further investigation. Possibly due to alignment issues or inner part degradation. * * 4) CONSEQUENCES: * Potential system inefficiencies and pump failure if not addressed promptly. * * 5) REQUIREMENTS IMPACTED: * Regular operation. Monitoring and maintenance required until the problem is resolved. * * 6) ADVERSE PHYSICAL CONDITIONS: * Unusually high vibrations noticed at 18B pump. * * 7) WHO WAS NOTIFIED: * Maintenance Supervisor, Control Room Team * * 8) KNOWLEDGEABLE INDIVIDUALS: * Harrison, Stone, Gomez * * 9) REPEAT OR SIMILAR CONDITION: * No, first occurrence. * * 10) IMMEDIATE ACTIONS AND RECOMMENDED ACTIONS: * Maintenance team to inspect pump alignment and possible internal damage. Comprehensive report needed upon inspection completion. * 02/23/2022 11:18:39 LUCAS GREEN (INCIDENT) * Recommended immediate maintenance activity. Potential internal part reconditioning or overall pump replacement may be necessary based on the results of the inspection. | What immediate actions were recommended following the detection of high vibrations at the 18B pump? | Maintenance team to inspect pump alignment and possible internal damage. Comprehensive report needed upon inspection completion.
339 | 2018-09-05 | 30852345 | 80236425 | Loud Sound from Pump 15B | S4CW -4CWE9 | * **************Incident Description************** * Notification 000030852345 Details * *********************************************************** * 09/05/2018 13:57:00 INCIDENT REPORT (INCIDENT REPORT) * Report submitted by: William Thompson ENTITY\INCIDENT: * * 1) CONDITION DESCRIPTION/LOCATION (THE INAPPROPRIATE ACTION AND ITS NEGATIVE EFFECT/INCLUDE A DETAILED LOCATION DESCRIPTION): * At 1357 hours on 9/5/2018 the operator on duty noticed a loud sound emanating from pump 15B. The pump was conducting system checks when the unusual sound was identified. Immediate shut down was initiated, reducing potential damage to the pump. Operator reported no immediate signs of external damage. * * 2) ACTIVITIES, PROCESSES, PROCEDURES INVOLVED: * S4.OP-AB.CW-0011, S4.OP-SO.CW-0021 * * 3) WHY DID CONDITION HAPPEN: * Unknown at this stage. Possible causes could be internal damage or obstruction. * * 4) CONSEQUENCES: * Possible internal damage or failure in future operations. * * 5) REQUIREMENTS IMPACTED: * Unavailable pump * * 6) ADVERSE PHYSICAL CONDITION: * Loud Sound from Pump 15B, potential internal damage * * 7) WHO WAS NOTIFIED: * Control Room, Maintenance Team * * 8) KNOWLEDGEABLE INDIVIDUALS: * Harris, O'Connor, Wilson * * 9) REPEAT OR SIMILAR CONDITION: * No * * 10) IMMEDIATE AND RECOMMENDED ACTIONS: * Involve maintenance team for detailed investigation and repair if needed. * * Updated: WILLIAM THOMPSON 09.05.2018 14:20:03 * ------------------------------------------------------------ * 09/09/2018 08:27:25 JANE DOE (NUSER) * The inspection did not reveal a mechanical issue, it was a loose part that was causing the unusual sound. The component was repositioned and secured, and the pump is back | What was the issue found during inspection of Pump 15B and what action was taken to resolve it? | The inspection did not reveal a mechanical issue, it was a loose part that was causing the unusual sound. The component was repositioned and secured, and the pump is back.
340 | 2018-04-25 | 30986530 | 90231846 | 7B Pump motor misaligned post repair | S4CW -4CWE7-MTDA | * **************Incident Description************** * Notification 000030986530 Details * *********************************************************** * SUMMARY: ASSESSMENT OF PREVIOUS REQUIREMENTS REFERENCED IN * ****PS-BB-345 "VALIDATION AFTER EQUIPMENT REPAIR AND REPLACEMENT PROCESS"***** * * 1) Condition Description/Location (The inappropriate action and its negative effect/Include a detailed location description): * At 1340 on 4/25/18, it was reported that following a routine maintenance, an aberrant noise was detected from the 7B Pump motor. Upon preliminary inspection, motor misalignment was suspected. Immediate shutdown procedures were followed, involving the Unit 4 Control Room. No adverse conditions like overheating or smoke were detected, but the pump is currently offline. * * 2) ACTIVITIES, PROCESSES, PROCEDURES INVOLVED: * S4.OP.AB-CW-0007, S4.OP-SO.CW-0004 * * 3) WHY DID CONDITION HAPPEN: * Presumed motor misalignment post maintenance, although definitive cause has yet to be ascertained. * * 4) CONSEQUENCES: * Potential pump damage if operated continuously. This could potentially impact operational efficiency upon restart. * * 5) REQUIREMENTS IMPACTED: * Offline pump * * 6) ADVERSE PHYSICAL CONDITION: * Audible noise from 7B Pump motor, presumable interior damage * * 7) WHO WAS NOTIFIED: * Control Room, Maintenance Department * * 8) KNOWLEDGEABLE INDIVIDUALS: * Klein, Patterson, Wong * * 9) REPEAT OR SIMILAR CONDITION: * Not determined at this point * * 10) IMMEDIATE AND RECOMMENDED ACTIONS: * Engage engineering for detailed motor inspection post dispatching fault notification to Maintenance Team * * Updated: STEPHEN BLACK 04.25.2018 14:30:10 * ------------------------------------------------------------ * 05/10/2018 09:21:15 JASON TAYLOR (NUSER) * Post inspection | Who was notified about the issue with the 7B Pump motor? | Control Room, Maintenance Department
341 | 2019-11-25 | 30925584 | 80298765 | Excessive vibration from 28B Pump | S4CW -4CWE4 | * **************Incident Description************** * Notification 000030925584 Details * *********************************************************** * 11/25/2019 18:37:13 INCIDENT REPORT (INCIDENT REPORT) * Report submitted by: Mark Roberts ENTITY\INCIDENT: * * CONDITION DESCRIPTION/LOCATION (THE INAPPROPRIATE ACTION AND ITS NEGATIVE EFFECT/INCLUDE A DETAILED LOCATION DESCRIPTION): * During normal operation on 11/25/19, 28B Pump reported to have excessive vibration. The system was shut down immediately and the vibration ceased. Upon inspection, no visible signs of damage were noted but an unusual sound was heard coming from the motor. The Pump Abnormality procedure S4.OP-AB.CW-0002 was initiated due to the abnormal operation of 28B Pump. * * ACTIVITIES, PROCESSES, PROCEDURES INVOLVED: * S4.OP.AB-CW-0002, S4.OP-SO.CW-0002 * * WHY DID CONDITION HAPPEN: * Unknown at this stage, although similar incidents were reported with other pumps. * * CONSEQUENCES: * The pump's regular operation was disrupted, which may cause a drop in system efficiency and can potentially cause damage to the pump motor if continued to operate. * * REQUIREMENTS IMPACTED: * Functionality of 28B Pump * * ADVERSE PHYSICAL CONDITION: * Excessive vibration from 28B Pump motor, potential internal damage. * * WHO WAS NOTIFIED: * Control Room, Maintenance department * * KNOWLEDGEABLE INDIVIDUALS: * Roberts, Thompson, Williams * * REPEAT OR SIMILAR CONDITION: * Yes, pumps have shown similar behavior in the past. * * IMMEDIATE AND RECOMMENDED ACTIONS: * Pump motor to be inspected thoroughly by maintenance. Further tests will be run to determine the cause of vibration. * * Updated: MARK ROBERTS 11.26.2019 07:30:11 * ------------------------------------------------------------ * 12/06/2019 09:20:15 LINDA WALKER (NUSER) * | What immediate action was recommended following the abnormal operation of the 28B Pump? | Pump motor to be inspected thoroughly by maintenance. Further tests will be run to determine the cause of vibration.
342 | 2017-09-18 | 30780216 | 80252841 | Unexpected pressure drop in Pump 27C | S4CW -4CWE2 | * **************Incident Description************** * Notification 000030780216 Details * *********************************************************** * 09/18/2017 10:12:00 INCIDENT REPORT (INCIDENT REPORT) * Report submitted by: Quentin Johnson ENTITY\INCIDENT: * * CONDITION DESCRIPTION/LOCATION (THE INAPPROPRIATE ACTION AND ITS NEGATIVE EFFECT/INCLUDE A DETAILED LOCATION DESCRIPTION): * During our routine system check at 0930 on 9/18/17, we observed that there was a significant drop in pressure in the 27C Pump, registering at 10 psig compared to normal 15 psig. Obviously, this is not typical for the 27C Pump. The drop was sudden and unexpected, causing concern. The pump was shut down to avoid further damage or potential for a catastrophic failure. * * ACTIVITIES, PROCESSES, PROCEDURES INVOLVED: * Routine system monitoring * * WHY DID CONDITION HAPPEN? * The exact cause of the drop in pressure is yet to be established, but initial evaluations suggest a potential blockage in the pump or a mechanical failure within the pump mechanism itself. * * CONSEQUENCES: * Potential pump failure, significant decrease in operational efficiency * * REQUIREMENTS IMPACTED: * Loss of pressure affecting operational effectiveness * * ADVERSE PHYSICAL CONDITIONS: * Sudden, unexpected pressure drop in pump 27C * * WHO WAS NOTIFIED: * Supervisor, Both Technicians on Duty, and Incident Team * * KNOWLEDGEABLE INDIVIDUALS: * Incident Team, Pump Operator * * REPEAT OR SIMILAR CONDITION: * Similar conditions have been reported but not with this pump * * IMMEDIATE ACTIONS AND RECOMMENDED ACTIONS: * Pump shut down and a comprehensive evaluation planned to diagnose the issue. The issue has been escalated to the mechanical engineering team for a thorough inspection of the pump. * 09/19/2017 14:30:30 QUENTIN JOHNSON (INCIDENT) * Our mechanical team did an inspection and discovered a broken valve which likely caused the drop in pressure. Replacement parts are on order and the | What was the immediate action taken after the unexpected drop in pressure in pump 27C? | Pump shut down and a comprehensive evaluation planned to diagnose the issue. The issue has been escalated to the mechanical engineering team for a thorough inspection of the pump.
343 | 2019-11-24 | 30989101 | 90112546 | High vibration in pump 10C after lubricant change | S4CW -4CWE2 | * **************Incident Description************** * Notification 000030989101 Details * *********************************************************** * 11/24/2019 07:20:13 INCIDENT REPORT (INCIDENT REPORT) * Report submitted by: Peter Williams ENTITY\INCIDENT: * CONDITION DESCRIPTION/LOCATION (THE INAPPROPRIATE ACTION AND ITS NEGATIVE EFFECT/INCLUDE A DETAILED LOCATION DESCRIPTION): * During routine checks, significant vibration has been noted in the 10C Pump after a recent lubricant change. No visible cause was identified for the vibration. The pump was immediately taken out of the cycle. A potential alignment issue or bearing problem may have been triggered by the change of lubricant. * ACTIVITIES, PROCESSES, PROCEDURES INVOLVED: * S4.OP-AB.LUB-0002, routine check procedures, change of lubricant procedure was executed. * WHY DID CONDITION HAPPEN? * It's unclear. Possibly a complication due to the change of the lubricant or an underlying mechanical issue. * CONSEQUENCES: * Possible pump failure if vibration issue is not resolved. Reducing operating span and efficiency. * REQUIREMENTS IMPACTED: * Routine operational function * ADVERSE PHYSICAL CONDITIONS: * High vibration levels in pump 10C * WHO WAS NOTIFIED: * Supervisor, Maintenance Team, Operations Room * KNOWLEDGEABLE INDIVIDUALS: * Maintenance Team, Engineers * REPEAT OR SIMILAR CONDITION: * No, this is the first instance * IMMEDIATE ACTIONS AND RECOMMENDED ACTIONS: * Immediate inspection to be carried out by Maintenance Team to check alignment, bearings, and potential damage due to vibration. Procure additional analysis if root cause is not identified in the inspection. * 11/26/2019 15:31:42 PETER WILLIAMS (INCIDENT) * Inspection revealed that the cause of the vibration was due to misalignment post lubricant change. The problem was rectified and the pump was put back online after successful trials. Reviewed procedures for lubricant change to prevent such instances. | What was the reason for the high vibration levels in pump 10C? | Inspection revealed that the cause of the vibration was due to misalignment post lubricant change.
344 | 2022-09-25 | 30730985 | 80231578 | Unusual vibration from 16B cooler motor | S3CW -3CWE7 | * **************Incident Description************** * Notification 000030730985 Details * *********************************************************** * 09/25/2022 10:52:04 INCIDENT REPORT (INCIDENT REPORT) * Report submitted by: Peter Brown ENTITY\INCIDENT: * * CONDITION DESCRIPTION/LOCATION (THE INAPPROPRIATE ACTION AND ITS NEGATIVE EFFECT/INCLUDE A DETAILED LOCATION DESCRIPTION): * During normal operation, 16B Cooler Motor was found to be vibrating more than usual. No changes in motor output were noted. Previous incidents indicated that unseen issues lead to motor vibration. Immediate shut down was performed to avoid potential damage. Operations Team has initiated inspection following procedure S3.OP-AB.CW-0009. * * ACTIVITIES, PROCESSES, PROCEDURES INVOLVED: * Normal operation of cooler motor, S3.OP-AB.CW-0009 * * WHY DID CONDITION HAPPEN? * Unknown, need to await inspection outcome. * * CONSEQUENCES: * Potential failure or damage to 16B cooler motor * * REQUIREMENTS IMPACTED: * Normal operation of facility * * ADVERSE PHYSICAL CONDITIONS: * Unusual vibration from 16B Cooler Motor * * WHO WAS NOTIFIED: * Maintenance Manager * * KNOWLEDGEABLE INDIVIDUALS: * Operations and Maintenance Team * * REPEAT OR SIMILAR CONDITION: * Yes, however, not for 16B Cooler Motor. * * IMMEDIATE ACTIONS AND RECOMMENDED ACTIONS: * Shut down the cooler motor, Arrange for immediate inspection * 09/27/2022 08:30:05 PETER BROWN (INCIDENT) * Inspection outcome suggested misalignment, adjustment carried out and motor is back to normal operation. Suggest monitoring for a few days as a precautionary step. | What immediate action was taken when the unusual vibration from the 16B Cooler Motor was detected? | Immediate shut down was performed to avoid potential damage. Operations Team has initiated inspection following procedure S3.OP-AB.CW-0009.
345 | 2017-09-16 | 30750590 | 80231586 | Erratic operation of 8A pump | S1CW -1CWE2 | * **************Incident Description************** * Notification 000030750590 Details * *********************************************************** * 09/16/2017 07:30:00 INCIDENT REPORT (INCIDENT REPORT) * Report submitted by: Mark Johnson ENTITY\INCIDENT: * * CONDITION DESCRIPTION/LOCATION (THE INAPPROPRIATE ACTION AND ITS NEGATIVE EFFECT/INCLUDE A DETAILED LOCATION DESCRIPTION): * During inspection rounds, the operator noted that 8A Pump was cycling on and off irregularly. On further investigation, it was observed that the pump's motor was hot to touch. The standard operation does not encompass such behavior. * * ACTIVITIES, PROCESSES, PROCEDURES INVOLVED: * S1.OP.AB-CW-0001, S1.OP-SO.CW-0001 * * WHY DID CONDITION HAPPEN? * The exact cause is unknown, although similar erratic behaviors have been observed in other pump motors. * * CONSEQUENCES: * Unpredictable pump operation and possible pump motor damage. * * REQUIREMENTS IMPACTED: * Continuous and efficient pump operation. * * ADVERSE PHYSICAL CONDITIONS: * High temperature at pump motor, irregular switch operation. * * WHO WAS NOTIFIED: * Control Room, Maintenance Team * * KNOWLEDGEABLE INDIVIDUALS: * Thomas, Peterson, Robinson * * REPEAT OR SIMILAR CONDITION: * Yes, similar conditions have been reported before * * IMMEDIATE ACTIONS AND RECOMMENDED ACTIONS: * The 8A pump was taken out of service. The maintenance team was informed to examine for possible mechanical/electrical failure. * 09/20/2017 14:22:11 MARK JOHNSON (INCIDENT) * Upon inspection, it was found that a fault in the motor's electrical circuit was causing the irregular operation. The faulty components were replaced and the motor has resumed normal operation. | What immediate and recommended actions were taken upon discovering the irregular operation of the 8A pump? | The 8A pump was taken out of service. The maintenance team was informed to examine for possible mechanical/electrical failure.
346 | 2018-10-21 | 30985413 | 80325749 | High Vibration in 32B Pump Motor | S4CW - 4CWE5 | * **************Incident Description************** * Notification 000030985413 Details * *********************************************************** * 10/21/2018 14:35:56 INCIDENT REPORT (INCIDENT REPORT) * Report submitted by: Michael Green ENTITY\INCIDENT: * * CONDITION DESCRIPTION/LOCATION (THE INAPPROPRIATE ACTION AND ITS NEGATIVE EFFECT/INCLUDE A DETAILED LOCATION DESCRIPTION): * During the routine operation, High vibration was detected in 32B Pump Motor. Vibration was recorded at 5 mm/s RMS, which is above the defined operational limit. The pump was immediately shutdown from Unit 4 control room and an abnormality report was created. The vibration was checked on the adjacent pump motors and found normal. The 32B pump was last overhauled under work order 80279364 and it was operating smoothly so far. * * ACTIVITIES, PROCESSES, PROCEDURES INVOLVED: * Routine Operations and S4.OP.AB-CW-0002, S4.OP-SO.CW-0003 * * WHY DID CONDITION HAPPEN? * Unknown, it may be due to misalignment or bearing problem * * CONSEQUENCES: * Potential failure of 32B pump motor, which may affect the unit operation * * REQUIREMENTS IMPACTED: * Potential unit deration due to pump outage * * ADVERSE PHYSICAL CONDITIONS: * High Vibration in 32B Pump Motor, possible mechanical failure * * WHO WAS NOTIFIED: * Control Room, Maintenance Team * * KNOWLEDGEABLE INDIVIDUALS: * Williams, Peterson, Anderson * * REPEAT OR SIMILAR CONDITION: * No * * IMMEDIATE ACTIONS AND RECOMMENDED ACTIONS: * Maintenance to inspect 32B Pump Motor immediately * Updated: MICHAEL GREEN 10.21.2018 15:30:10 * ------------------------------------------------------------ * 10/29/2018 13:10:50 SAMUEL PETERSON (MTUSER) * Post investigation, it was found that the bearing of the motor was damaged. The bearing has been replaced and vibration is now within | What was the identified cause of the high vibration in the 32B Pump Motor? | Post investigation, it was found that the bearing of the motor was damaged.
347 | 2019-12-15 | 30958674 | 80249935 | Leak detected in 18B Pump | S4CW -4CWE2 | * **************Incident Description************** * Notification 000030958674 Details * *********************************************************** * 12/15/2019 11:35:00 INCIDENT REPORT (INCIDENT REPORT) * Report submitted by: Daniel Thompson ENTITY\INCIDENT: * * CONDITION DESCRIPTION/LOCATION (THE INAPPROPRIATE ACTION AND ITS NEGATIVE EFFECT/INCLUDE A DETAILED LOCATION DESCRIPTION): * During a routine walkthrough, a small leak was noted on the 18B pump. The pump was immediately shut down and the area was cleaned. No fluid damage detected on pump motor or adjacent equipment. * * ACTIVITIES, PROCESSES, PROCEDURES INVOLVED: * Routine inspection, S4.OP.AB.CW-0001 * * WHY DID CONDITION HAPPEN? * Investigation is ongoing, possible factors include aging of the pump and gaskets, pump vibration, excess pump pressure. * * CONSEQUENCES: * If not repaired, could cause equipment damage and efficiency loss. Provides a hazard for operators and maintenance personnel. * * REQUIREMENTS IMPACTED: * Equipment reliability, Safe operation * * ADVERSE PHYSICAL CONDITIONS: * Leak from pump * * WHO WAS NOTIFIED: * Supervisor, Maintenance Team * * KNOWLEDGEABLE INDIVIDUALS: * Daniel Thompson, Incident Team * * REPEAT OR SIMILAR CONDITION: * No, this is first time for this pump. * * IMMEDIATE ACTIONS AND RECOMMENDED ACTIONS: * Seal replacement, leak test, back in operation if test passed. * 12/17/2019 14:35:18 DANIEL THOMPSON (INCIDENT) * The seal replacement was successful and there no further leaks have been detected. The pump is now back in operation. | What immediate and recommended actions were taken after the pump leak was discovered? | Seal replacement, leak test, back in operation if test passed.
348 | 2019-09-26 | 30939653 | 80253917 | Vibration detected from pump 43A | S5CW -5CWE7 | * **************Incident Description************** * Notification 000030939653 Details * *********************************************************** * 09/26/2019 15:35:10 INCIDENT REPORT (INCIDENT REPORT) * Report submitted by: William Taylor 123-456-7890 ENTITY\INCIDENT: * CONDITION DESCRIPTION/LOCATION (THE INAPPROPRIATE ACTION AND ITS NEGATIVE EFFECT/INCLUDE A DETAILED LOCATION DESCRIPTION): * During a routine check of the pump station, abnormal vibration was detected from 43A Pump. The amplitude of the vibration was higher than the threshold and deviating from its normal range. The unit was shut down for further inspection. * * ACTIVITIES, PROCESSES, PROCEDURES INVOLVED: * Regular maintenance check * WHY DID CONDITION HAPPEN? * At this time, the exact cause is unknown, but it could be due to mechanical failure or anomaly within the system. * * CONSEQUENCES: * Potential for significant equipment damage or failure if not addressed immediately. * * REQUIREMENTS IMPACTED: * Normal operation of the pump station * * ADVERSE PHYSICAL CONDITIONS: * High levels of vibration detected in Pump 43A * * WHO WAS NOTIFIED: * Maintenance Supervisor/ INCIDENT TEAM * * KNOWLEDGEABLE INDIVIDUALS: * Incident Team, Engineering Department * * REPEAT OR SIMILAR CONDITION: * No, this is the first recorded instance. * * IMMEDIATE ACTIONS AND RECOMMENDED ACTIONS: * Required immediate inspection of Pump 43A. If the cause of vibration is not detected, a full system analysis may be required. * 09/26/2019 18:48:33 WILLIAM TAYLOR (INCIDENT) * After an initial inspection, it was found that a misalignment in the pump hardware might be causing the vibrations. Corrective measures are being taken under the guidance of the Engineering Department. | What immediate actions were suggested regarding the detected abnormal vibrations in Pump 43A? | Required immediate inspection of Pump 43A. If the cause of vibration is not detected, a full system analysis may be required.
349 | 2020-05-15 | 31204873 | 80558429 | Unexpected 30C motor vibration post overhaul | S4CW -4CWE2 | * **************Incident Description************** * Notification 000031204873 Details * *********************************************************** * 05/15/2020 10:25:12 INCIDENT REPORT (INCIDENT REPORT) * Report submitted by: Emily Adams ENTITY\INCIDENT: * CONDITION DESCRIPTION/LOCATION (THE INAPPROPRIATE ACTION AND ITS NEGATIVE EFFECT/INCLUDE A DETAILED LOCATION DESCRIPTION): * Following a planned overhaul of 30C Pump on 22 April under work order 80548962, an increase in vibration and noise was noticed on 05/15/20 during routine inspection. Despite the noise and vibration, normal operational parameters were observed. Anomalies were not present during the initial post-maintenance inspection and test. * * ACTIVITIES, PROCESSES, PROCEDURES INVOLVED: * The planned maintenance for 30C Pump under S2.OP.AB-CW-0001, S2.OP-SO.CW-0001. * * WHY DID CONDITION HAPPEN? * The source of the vibration is currently unknown. Investigation is ongoing. * * CONSEQUENCES: * Potential future failures or reduction in operating efficiency. * * REQUIREMENTS IMPACTED: * Operational performance of 30C pump. * * ADVERSE PHYSICAL CONDITIONS: * Unusual noise and vibration from 30C pump. * * WHO WAS NOTIFIED: * Maintenance Team, Operations Manager * * KNOWLEDGEABLE INDIVIDUALS: * Davis, Stevens, Hughes * * REPEAT OR SIMILAR CONDITION: * No, this is the first noted issue with 30C pump post maintenance. * * IMMEDIATE ACTIONS AND RECOMMENDED ACTIONS: * Inspection team to further investigate and address the source of vibration. * 05/17/2020 14:37:52 JOHN DOE (INSPECTION) * The inspection results showed a balance issue with the impeller. The impeller was rebalanced, reinstalled and the noise and vibration have been significantly reduced. The 30C pump is now operating within normal parameters. | What was the initial issue observed with the 30C Pump post maintenance overhaul? | Following a planned overhaul of 30C Pump on 22 April under work order 80548962, an increase in vibration and noise was noticed on 05/15/20 during routine inspection. Despite the noise and vibration, normal operational parameters were observed. Anomalies were not present during the initial post-maintenance inspection and test.
350 | 2018-12-12 | 30815970 | 90215640 | Leaks detected on pump 16B | S3CW -3CWE5 | * **************Incident Description************** * Notification 000030815970 Details * *********************************************************** * 12/12/2018 09:11:00 INCIDENT REPORT (INCIDENT REPORT) * Report submitted by: Lisa Stone ENTITY\INCIDENT: * * CONDITION DESCRIPTION/LOCATION (THE INAPPROPRIATE ACTION AND ITS NEGATIVE EFFECT/INCLUDE A DETAILED LOCATION DESCRIPTION): * During routine walk down, discovered fluid leaks from 16B pump. The leakage was on the sea side of the pump which is located in the pump house. Immediate action was taken to isolate the pump. * * ACTIVITIES, PROCESSES, PROCEDURES INVOLVED: * Regular operation, certain leaks correction process S3.OP-AB.CW-0003. * * WHY DID CONDITION HAPPEN? * Possible aging and wear of pump seals. * * CONSEQUENCES: * Potential loss of fluid, environmental harm, and mechanical failures if leak continues. * * REQUIREMENTS IMPACTED: * Pump efficiency and maintenance requirements. * * ADVERSE PHYSICAL CONDITIONS: * Leak observed on 16B pump. * * WHO WAS NOTIFIED: * Area supervisor, Maintenance Team. * * KNOWLEDGEABLE INDIVIDUALS: * Lisa Stone, Gary Harris (Maintenance Supervisor), John King (Engineer) * * REPEAT OR SIMILAR CONDITION: * Yes, similar leaks have been noticed on other pumps. * * IMMEDIATE ACTIONS AND RECOMMENDED ACTIONS: * Isolation of the pump. Request maintenance to repair 16B pump and investigate potential for similar issues in other pumps. Inspection of similar pumps is proposed. * 12/15/2018 11:32:18 GARY HARRIS (MAINTENANCE SUPERVISOR) * Maintenance actions have been completed under work order 90215641. Seals on the pump were replaced and the pump is now back in operation. Leak check performed post maintenance shows no signs of leakage. | What immediate action was taken when the fluid leak from the 16B pump was discovered? | Immediate action was taken to isolate the pump.
351 | 2016-09-18 | 30782019 | 80248960 | Overheating in Turbine 17B | S4CW -4CWE7-TURB | * **************Incident Description************** * Notification 000030782019 Details * *********************************************************** * 09/18/2016 13:11:29 INCIDENT REPORT (INCIDENT REPORT) * Report submitted by: David Foster ENTITY\INCIDENT: * * 1) CONDITION DESCRIPTION/LOCATION (THE INAPPROPRIATE ACTION AND ITS NEGATIVE EFFECT/INCLUDE A DETAILED LOCATION DESCRIPTION): * On 09/18/2016, the operator reported severe overheating occurring in Turbine 17B. The turbine was quickly disconnected from the power grid and shut down. The overheating condition was confirmed by physical inspection and infrared thermography. No immediate fire hazards were identified but there was a noticeable smell of burnt lubrication oil. Thermal scanners revealed hot spots on the rotor assembly suggesting internal damage. S4.OP-TB.DG-0005 Turbine Degradation scenario was initiated based on this overheating incident. * * 2) ACTIVITIES, PROCESSES, PROCEDURES INVOLVED: * S4.OP.TU.DG-0003, S4.OP-SO.TU-0001 * * 3) WHY DID CONDITION HAPPEN: * Preliminary investigation suggests inadequate lubrication or physical damage to rolling elements inside turbine. * * 4) CONSEQUENCES: * Shutdown of Turbine 17B resulted in reduced power production. There is a potential risk of internal damage to the turbine components. * * 5) REQUIREMENTS IMPACTED: * Turbine operation and power generation * * 6) ADVERSE PHYSICAL CONDITION: * Overheating of Turbine 17B, possible internal damage * * 7) WHO WAS NOTIFIED: * Shift Supervisor, Maintenance Department * * 8) KNOWLEDGEABLE INDIVIDUALS: * Kate Williams, David Foster * * 9) REPEAT OR SIMILAR CONDITION: * No * * 10) IMMEDIATE ACTIONS AND RECOMMENDED ACTIONS: * Engineering and maintenance teams to conduct an internal examination of Turbine 17B and determine | What was the initial cause identified for the overheating of Turbine 17B? | Preliminary investigation suggests inadequate lubrication or physical damage to rolling elements inside turbine.
352 | 2016-01-10 | 30730862 | 80244000 | Unprecedented vibration in 19B pump | S3CW -3CWE8 | * **************Incident Description************** * Notification 000030730862 Details * *********************************************************** * 01/10/2016 14:50:02 INCIDENT REPORT (INCIDENT REPORT) * Report submitted by: Daniel Thompson ENTITY\INCIDENT: * CONDITION DESCRIPTION/LOCATION (THE INAPPROPRIATE ACTION AND ITS NEGATIVE EFFECT/INCLUDE A DETAILED LOCATION DESCRIPTION): * While performing standard maintenance, a higher than normal level of vibration was noticed in the 19B pump. The vibration was so intense that it could potentially compromise the structural integrity of the unit if it continues. * ACTIVITIES, PROCESSES, PROCEDURES INVOLVED: * Standard maintenance check, S3.OP.AB-CW-0012, S3.OP-SO.CW-0008 * WHY DID CONDITION HAPPEN? * The cause is yet to be determined. Further inspection required. * CONSEQUENCES: * Prolonged vibration can lead to severe damage to the pump and a potential shutdown of the unit. * REQUIREMENTS IMPACTED: * The pump is currently out of service due to the unusual vibrations. * ADVERSE PHYSICAL CONDITIONS: * Excessive vibrations in 19B pump without an identified cause * WHO WAS NOTIFIED: * Maintenance Supervisor, Incident Team * KNOWLEDGEABLE INDIVIDUALS: * Incident Team, Engineers * REPEAT OR SIMILAR CONDITION: * No, this is the first time such vibration has been observed. * IMMEDIATE ACTIONS AND RECOMMENDED ACTIONS: * The pump was immediately shut down and will be inspected for potential faults. Further deliberation on the course of action will be carried out after inspection. * 01/11/2016 15:25:29 JASON BELLE (INCIDENT) * Upon inspection, a misalignment in the pump rotor was detected. Arrangements for realignment and further testing are being made. The pump will remain offline until the issue is fully resolved. | What immediate actions were taken after the abnormal vibration was detected in the 19B pump? | The pump was immediately shut down and will be inspected for potential faults. Further deliberation on the course of action will be carried out after inspection.
353 | 2022-03-10 | 32085050 | 90278354 | 16B Pump motor irregular power consumption | S4CW -4CWE2 | * **************Incident Description************** * Notification 000032085050 Details * *********************************************************** * 03/10/2022 16:39:22 INCIDENT REPORT (INCIDENT REPORT) * Report submitted by: Mark Thompson ENTITY\INCIDENT: * * CONDITION DESCRIPTION/LOCATION (THE INAPPROPRIATE ACTION AND ITS NEGATIVE EFFECT/INCLUDE A DETAILED LOCATION DESCRIPTION): * During routine operations on 03/10/22, the 16B Pump motor displayed an irregular power consumption detected on the power monitoring system. Even after load shedding to maintain stable operation, the power consumption remained erratic. The 16B Pump was remotely shut down by the Unit 4 Control Room post detection, investigating any potential equipment or electrical issues. * * ACTIVITIES, PROCESSES, PROCEDURES INVOLVED: * S4.OP.AB-CW-0023, S4.OP-SO.CW-0018 * * WHY DID CONDITION HAPPEN? * Unknown, former instances suggest a possible internal fault or misalignment. * * CONSEQUENCES: * Potential impact on power consumption consistency and pumping efficiency, leading to possible service disruption. * * REQUIREMENTS IMPACTED: * Maintain consistent power consumption. * * ADVERSE PHYSICAL CONDITIONS: * Irregular power consumption from 16B pump motor, potential internal fault. * * WHO WAS NOTIFIED: * Control Room, Maintenance Unit, Electrical department * * KNOWLEDGEABLE INDIVIDUALS: * Thompson, Johnson, Smith, Lee * * REPEAT OR SIMILAR CONDITION: * Yes, at different motor locations * * IMMEDIATE ACTIONS AND RECOMMENDED ACTIONS: * Electrical department to inspect the 16B Pump Motor electrical system, while Maintenance Unit investigates potential mechanical issues. * * Updated: MARK THOMPSON 03.10.2022 19:34:10 * ------------------------------------------------------------ * 03/15/2022 09:32:41 JANE DOE (INCIDENT) * An inspection revealed that it was not a core electrical issue with the motor. Misalignment between the pump and the motor was causing the power consumption irregularity. Realignment followed | What was discovered as the cause of the irregular power consumption in the 16B Pump motor? | Misalignment between the pump and the motor was causing the power consumption irregularity.
354 | 2019-03-05 | 30985034 | 80256870 | Odd vibration in 30B pump | S4CW -4CWE2 | * **************Incident Description************** * Notification 000030985034 Details * *********************************************************** * 03/05/2019 15:12:43 INCIDENT REPORT (INCIDENT REPORT) * Report submitted by: Lisa Green 345-678-9123 ENTITY\INCIDENT: * CONDITION DESCRIPTION/LOCATION (THE INAPPROPRIATE ACTION AND ITS NEGATIVE EFFECT/INCLUDE A DETAILED LOCATION DESCRIPTION): * On 3/5/19 during routine operations, noticed an unusual vibration in the 30B Pump. The subsequent inspection found no visible damage, but the vibration persisted. * ACTIVITIES, PROCESSES, PROCEDURES INVOLVED: * Standard Operating procedure - S4.OP.AB-CW-0002 * WHY DID CONDITION HAPPEN? * Cause of vibration is uncertain. It can be due to misalignment, damaged or worn out parts, or imbalance in the system. * CONSEQUENCES: * Continuous vibrations might lead to pump failure, causing unexpected downtime and potential damages to other equipment. * REQUIREMENTS IMPACTED: * Routine operation might be affected due to reduced pump efficiency. * ADVERSE PHYSICAL CONDITIONS: * Persistent vibration in the 30B Pump. * WHO WAS NOTIFIED: * Maintenance supervisor, operational team * KNOWLEDGEABLE INDIVIDUALS: * Operational team, maintenance crew * REPEAT OR SIMILAR CONDITION: * No similar case reported in the past. * IMMEDIATE ACTIONS AND RECOMMENDED ACTIONS: * Conduct thorough inspection and analysis of the pump. Implement maintenance work order if needed. * 03/08/2019 09:22:31 LISA GREEN (INCIDENT) * Maintenance intervention carried out and imbalance due to clogged pump impeller identified. The blockage was removed and the pump is running smooth without any vibration. | What was the initial unusual observation during routine operations? | On 3/5/19 during routine operations, noticed an unusual vibration in the 30B Pump. The subsequent inspection found no visible damage, but the vibration persisted.
355 | 2019-12-14 | 30913287 | 90245693 | Unexpected vibration in 18B pump after maintenance | S3CW -3CWE5 | * **************Incident Description************** * Notification 000030913287 Details * *********************************************************** * 12/14/2019 14:39:23 INCIDENT REPORT (INCIDENT REPORT) * Report submitted by: Lisa Turner ENTITY\INCIDENT: * * CONDITION DESCRIPTION/LOCATION (THE INAPPROPRIATE ACTION AND ITS NEGATIVE EFFECT/INCLUDE A DETAILED LOCATION DESCRIPTION): * Immediately after routine maintenance work on the 18B pump, the operations team noticed unexpected vibration. The pump was stopped to prevent further damage, and an inspection was initiated. Initial checks did not reveal any apparent cause for the vibration. * * ACTIVITIES, PROCESSES, PROCEDURES INVOLVED: * Maintenance of the 18B pump under work order 90245693. * * WHY DID CONDITION HAPPEN? * The cause of this condition is not yet identified. * * CONSEQUENCES: * Potential damage to the motor, impacting safe and reliable operations. * * REQUIREMENTS IMPACTED: * Safe operation of the 18B pump * * ADVERSE PHYSICAL CONDITIONS: * Unexpected vibration in pump * * WHO WAS NOTIFIED: * Operations Supervisor, Maintenance Engineer * * KNOWLEDGEABLE INDIVIDUALS: * Operations Supervisor, Maintenance Engineer * * REPEAT OR SIMILAR CONDITION: * No * * IMMEDIATE ACTIONS AND RECOMMENDED ACTIONS: * Conduct detailed inspection of the 18B pump. Update S3.OP-SO.CW-0001 and other relevant procedures if needed based on the inspection results. * 12/16/2019 10:54:22 LISA TURNER (INCIDENT) * The detailed inspection revealed that the pump was correctly assembled, but alignment was off due to a faulty baseplate. The baseplate has been replaced, and the pump is functioning without vibration. Procedures might need to include a step for checking alignment post-assembly. | What was the initial action taken when the unexpected vibration in the 18B pump was discovered? | The pump was stopped to prevent further damage, and an inspection was initiated.
356 | 2019-03-21 | 30820562 | 90245365 | Excessive Vibration in 16B Pump Motor | S3W -3CWE5 | * **************Incident Description************** * Notification 000030820562 Details * *********************************************************** * 03/21/2019 14:18:00 INCIDENT REPORT (INCIDENT REPORT) * Report submitted by: Peter Williams ENTITY\INCIDENT: * * CONDITION DESCRIPTION/LOCATION (THE INAPPROPRIATE ACTION AND ITS NEGATIVE EFFECT/INCLUDE A DETAILED LOCATION DESCRIPTION): * At 1410 on 03/21/19, excessive vibration was reported from the 16B Pump Motor in the S3W generator room. Immediate shutdown was executed from the control room followed by a joint inspection by Operation and Maintenance teams. No external damage was observed, but there were signs of metallic friction. Mortor temperature were deemed safe, yet pump vibration was at an abnormal level when compared to data on other running motors. S3.OP-AB.CW-0002 was initiated due to this event. * * ACTIVITIES, PROCESSES, PROCEDURES INVOLVED: * S3.OP.AB-CW-0002, S3.OP-SO.CW-0002 * * WHY DID CONDITION HAPPEN? * Initial inspection could not determine the exact cause. Instances of motor misalignment or foreign object damage has been encountered previously. * * CONSEQUENCES: * Could lead to motor failture, resulting in lower efficiency when back online. * * REQUIREMENTS IMPACTED: * Motor pump operation. * * ADVERSE PHYSICAL CONDITIONS: * Excessive vibration from 16B pump motor, potential internal damage. * * WHO WAS NOTIFIED: * Control Room, Maintenance Team * * KNOWLEDGEABLE INDIVIDUALS: * Peterson, Johnson, Adams * * REPEAT OR SIMILAR CONDITION: * Yes, similar event happened previously. * * IMMEDIATE ACTIONS AND RECOMMENDED ACTIONS: * Further maintenance investigation of the 16B pump motor for potential misalignment or foreign object damage. * 03/23/2019 10:35:20 PETER WILLIAMS (INCIDENT) * Vibro-analysis of the 16B pump motor revealed misalignment of motor shaft. The motor has been | What was the immediate action taken when excessive vibration was reported in the 16B Pump Motor? | Immediate shutdown was executed from the control room followed by a joint inspection by Operation and Maintenance teams.
357 | 2018-09-15 | 30845216 | 80293842 | Higher vibration from 14B pump | S4CW -4CWE5 | * **************Incident Description************** * Notification 000030845216 Details * *********************************************************** * 09/15/2018 15:45:00 INCIDENT REPORT (INCIDENT REPORT) * Report submitted by: Thomas Howard ENTITY\INCIDENT: * * CONDITION DESCRIPTION/LOCATION (THE INAPPROPRIATE ACTION AND ITS NEGATIVE EFFECT/INCLUDE A DETAILED LOCATION DESCRIPTION): * During a routine inspection, 14B Pump was found to be vibrating more than normal. Vibration monitors initially indicated a value of 30% over the normal range. The pump was not showing signs of physical damage, but was taken offline as a precautionary measure. Vibrations can cause fatigue and unexpected failure of the pump. * * ACTIVITIES, PROCESSES, PROCEDURES INVOLVED: * S4.OP.CK.CW-0002 Routine check of 14B Pump * * WHY DID CONDITION HAPPEN? * The cause of the vibration is still not clear. Could be due to wear and tear or misalignment of the pump components. * * CONSEQUENCES: * Possible premature wear and breakdown of the pump. * * REQUIREMENTS IMPACTED: * Pump reliability and performance * * ADVERSE PHYSICAL CONDITIONS: * Excessive vibration from 14B pump. * * WHO WAS NOTIFIED: * Maintenance Supervisor, Control Room * * KNOWLEDGEABLE INDIVIDUALS: * Thomas Howard, Catherine Stone, Mark Davis * * REPEAT OR SIMILAR CONDITION: * Similar incidents have been reported with other pumps. * * IMMEDIATE ACTIONS AND RECOMMENDED ACTIONS: * The pump has been taken offline and scheduled for inspection by maintenance. If necessary, components will be repaired or replaced. * 09/18/2018 10:51:22 CATHERINE STONE (INCIDENT) * The 14B Pump was inspected and found to have a misaligned impeller causing the increased vibration. The impeller has been adjusted and the pump is now running within the acceptable vibration range. | What was found to be the cause of the excessive vibration from the 14B Pump? | The 14B Pump was inspected and found to have a misaligned impeller causing the increased vibration.
358 | 2019-01-22 | 30735462 | 80245122 | Decrease in pump 32B pressure | S4CW -4CWE7 | * **************Incident Description************** * Notification 000030735462 Details * *********************************************************** * 01/22/2019 14:45:00 INCIDENT REPORT (INCIDENT REPORT) * Report submitted by: Emily Clark ENTITY\INCIDENT: * * CONDITION DESCRIPTION/LOCATION (THE INAPPROPRIATE ACTION AND ITS NEGATIVE EFFECT/INCLUDE A DETAILED LOCATION DESCRIPTION): * During an operational check, we noticed a sudden drop in pressure in pump 32B. Pump 32B pressure decreased by 15%. The pump was shut down immediately and all related systems have been inspected for possible leaks or blockages. Current opinion associates the issue either with a defective component or accumulated debris. * * ACTIVITIES, PROCESSES, PROCEDURES INVOLVED: * S4.OP.AB-CW-0002, S4.OP-SO.CW-0003 * * WHY DID CONDITION HAPPEN? * The root cause is unknown at this moment; however, components malfunction or debris accumulation could be potential causes. * * CONSEQUENCES: * The decrease in pressure can affect the efficiency of the operation and can lead to further machinery damage if not addressed. * * REQUIREMENTS IMPACTED: * Regular pump functioning. * * ADVERSE PHYSICAL CONDITIONS: * Lower pressure in Pump 32B * * WHO WAS NOTIFIED: * Operations Manager, Maintenance Team * * KNOWLEDGEABLE INDIVIDUALS: * Operations Manager, Forbes, Clark * * REPEAT OR SIMILAR CONDITION: * No previous identical cases noted. * * IMMEDIATE ACTIONS AND RECOMMENDED ACTIONS: * Commence inspection to diagnose the cause of pressure drop, perform necessary repairs, and prevent a similar incident from occurring in the near future. * 01/26/2019 09:29:52 EMILY CLARK (INCIDENT) * The inspection report indicates that the drop in pump pressure was due to a malfunctioning part. The part has been replaced and the pump is functioning at its normal pressure. Further monitoring is suggested to prevent similar incidents. | What was the identified cause for the sudden drop in pressure in pump 32B? | The inspection report indicates that the drop in pump pressure was due to a malfunctioning part.
359 | 2019-01-23 | 30781052 | 80226740 | Vibration Detected from 16D Pump | S4CW -4CWE3 | * **************Incident Description************** * Notification 000030781052 Details * *********************************************************** * 01/23/2019 10:49:00 INCIDENT REPORT (INCIDENT REPORT) * Report submitted by: Daniel Marcus ENTITY\INCIDENT: * * CONDITION DESCRIPTION/LOCATION (THE INAPPROPRIATE ACTION AND ITS NEGATIVE EFFECT/INCLUDE A DETAILED LOCATION DESCRIPTION): * At 1030 on 1/23/19, during the pump testing procedure, high vibration was detected from the 16D Pump. Considering the potential damage to the pump and the operations, it was immediately shut down. The vibration decreased and a maintenance engineer was notified. The detailed inspection found no visible signs of damage. Initial analysis suggests a possible imbalance or a mechanical fault inside the pump. * * ACTIVITIES, PROCESSES, PROCEDURES INVOLVED: * S4.OP-SO.CW-0001, S4.OP.AB-CW-0001 * * WHY DID CONDITION HAPPEN? * The exact cause of the vibration is still unknown. The imbalance could have been caused by wear and tear, or possibly a foreign object inside the pump. * * CONSEQUENCES: * Ongoing operations could have been severely affected if the vibration had led to a catastrophic failure of the pump. Immediate shutdown prevented any major consequences, however, the operations were interrupted. * * REQUIREMENTS IMPACTED: * Continuity of operation * * ADVERSE PHYSICAL CONDITIONS: * Excessive Vibration from 16D Pump * * WHO WAS NOTIFIED: * Operations Supervisor, Maintenance Engineer * * KNOWLEDGEABLE INDIVIDUALS: * Thomas Hill, Sandra Blake, Mark Kingsley * * REPEAT OR SIMILAR CONDITION: * No * * IMMEDIATE ACTIONS AND RECOMMENDED ACTIONS: * Complete thorough inspection and analysis of pump 16D. If necessary, carry out maintenance or replacement. * 01/24/2019 17:27:19 DANIEL MARCUS (INCIDENT) * Detailed inspection of the pump revealed an internal mechanical fault. The | What was the immediate action taken when high vibration was detected from the 16D Pump? | It was immediately shut down. The vibration decreased and a maintenance engineer was notified.
360 | 2016-12-01 | 30781523 | 80236904 | Overheating issue with pump 23B | S4CW -4CWE12 | * **************Incident Description************** * Notification 000030781523 Details * *********************************************************** * 12/01/2016 11:10:15 INCIDENT REPORT (INCIDENT REPORT) * Report submitted by: Samuel Ford ENTITY\INCIDENT: * * CONDITION DESCRIPTION/LOCATION (THE INAPPROPRIATE ACTION AND ITS NEGATIVE EFFECT/INCLUDE A DETAILED LOCATION DESCRIPTION): * During the morning shift, the control room reported excessive heat detected on pump 23B. The heat sensors on the pump triggered the alarm system. The pump was immediately shut down as per operational safety protocol. No fire or smoke was visible, but a noticeable smell of hot metal could be sensed near the pump. The overheat could potentially cause damage to the internal parts of the pump. * * ACTIVITIES, PROCESSES, PROCEDURES INVOLVED: * S4.OP-PH.CW-0002, S4.OP-SO.CW-0010 * * WHY DID CONDITION HAPPEN? * Unknown, electric failure suspected. * * CONSEQUENCES: * Possible pump damage, reduced operational efficiency. * * REQUIREMENTS IMPACTED: * Normal operation. * * ADVERSE PHYSICAL CONDITIONS: * Overheating of Pump 23B. * * WHO WAS NOTIFIED: * Control Room, Maintenance Team. * * KNOWLEDGEABLE INDIVIDUALS: * Johnson, Lee, Ford. * * REPEAT OR SIMILAR CONDITION: * No. * * IMMEDIATE ACTIONS AND RECOMMENDED ACTIONS: * Investigation of overheating cause is being initiated by the Maintenance Team. Extra cooling measures are being taken until the pump returns to normal operation temperature. * 12/03/2016 14:22:47 SAMUEL FORD (INCIDENT) * The overheating issue was identified. A misplaced pump component was causing friction leading to overheating. The faulty part is replaced and the pump is now in working condition. Advise regular overhaul to avoid future issues. | What was the immediate action taken when an excessive heat was detected on pump 23B? | The pump was immediately shut down as per operational safety protocol.
361 | 2022-03-15 | 30879821 | 80256789 | Unusual vibrations from 8B pump | S4CW -4CWE2 | * ***********Incident Description************ * Notification 000030879821 Details * ******************************************************************* * 03/15/2022 16:31:47 INCIDENT REPORT (INCIDENT REPORT) * Report submitted by: Elizabeth Taylor ENTITY\INCIDENT: * * CONDITION DESCRIPTION/LOCATION (THE INAPPROPRIATE ACTION AND ITS NEGATIVE EFFECT/INCLUDE A DETAILED LOCATION DESCRIPTION): * Experienced unusual vibration upon power up of the 8B pump following routine maintenance. Pump shutdown was initiated as per procedure S4.OP-AE.CW-0002. Pump was cooled down and isolated immediately to prevent any further damages. No visible external signs of wear or damage. * * ACTIVITIES, PROCESSES, PROCEDURES INVOLVED: * Post-maintenance power-up and monitoring * * WHY DID CONDITION HAPPEN? * Potential misalignment or internal damage post maintenance. Actual cause still unknown. * * CONSEQUENCES: * Potential pump failure if not identified and rectified. Possible loss of bringing the unit back online. * * REQUIREMENTS IMPACTED: * Pump operation and Unit restart * * ADVERSE PHYSICAL CONDITIONS: * High vibration levels at pump initiation * * WHO WAS NOTIFIED: * Maintenance Department, Control Room * * KNOWLEDGEABLE INDIVIDUALS: * Maintenance Supervisor, Engineers, Williams, and Miller * * REPEAT OR SIMILAR CONDITION: * No * * IMMEDIATE ACTIONS AND RECOMMENDED ACTIONS: * Carry out detailed inspection of the pump alignment post-maintenance. Monitor closely during future startups. Update procedure S4.OP-AE.CW-0002 if needed. * 03/16/2022 11:03:29 ROBERT SMITH (INCIDENT) * Post-inspection confirmed a minor misalignment issue after maintenance. The alignment issue has been corrected and the pump is now showing normal vibration levels at startup. Procedure S4.OP-AE.CW-0002 updated to include further alignment checks post-maintenance. | What was the initial problem observed with the 8B pump and what procedure was undertaken in response to the problem? | Experienced unusual vibration upon power up of the 8B pump following routine maintenance. Pump shutdown was initiated as per procedure S4.OP-AE.CW-0002. Pump was cooled down and isolated immediately to prevent any further damages.
362 | 2016-09-17 | 30758220 | 80237180 | 9B Pump excessive vibration | S5CW -5CWE2 | * **************Incident Description************** * Notification 000030758220 Details * *********************************************************** * 09/17/2016 14:13:43 INCIDENT REPORT (INCIDENT REPORT) * Report submitted by: Brian Clark ENTITY\INCIDENT: * * CONDITION DESCRIPTION/LOCATION (THE INAPPROPRIATE ACTION AND ITS NEGATIVE EFFECT/INCLUDE A DETAILED LOCATION DESCRIPTION): * At routine check, the operator noticed excessive vibration on the 9B Pump during operation. The pump was then shut down for preventive maintenance. No signs of damage were visible on the exterior, but inspection of the pumping mechanism revealed evidence of rotative imbalance. * * ACTIVITIES, PROCESSES, PROCEDURES INVOLVED: * Routine check was performed, S5.OP.AB-CW-0002, S5.OP-SO.CW-0002 * * WHY DID CONDITION HAPPEN? * It is unknown. The imbalance might be due to wear or may be a result of substandard maintenance practices. * * CONSEQUENCES: * High vibration can lead to structural damage to the pump, possibly affecting pump performance. * * REQUIREMENTS IMPACTED: * Significant vibration may influence the pump's reliability and operability. * * ADVERSE PHYSICAL CONDITIONS: * There's observable vibration, with potential risk of damage to the pump sustained from high intensity conditions. * * WHO WAS NOTIFIED: * Supervisor, Maintenance Team * * KNOWLEDGEABLE INDIVIDUALS: * Maintenance Team, Brian Clark, Engineers * * REPEAT OR SIMILAR CONDITION: * No, this is the first occurrence of such nature with this pump. * * IMMEDIATE ACTIONS AND RECOMMENDED ACTIONS: * Carry out inspection and correction of imbalances. If necessary, replace the pump. * 09/20/2016 10:17:29 BRIAN CLARK (INCIDENT) * Post inspection, the pump was rebalanced and installed back into the system. Now, it's functioning within normal vibration parameters. New preventive measures will be drafted to tackle potential future occurrences. | What was the immediate action taken after the detection of the pump issue and what was the outcome of that action? | Post inspection, the pump was rebalanced and installed back into the system. Now, it's functioning within normal vibration parameters. New preventive measures will be drafted to tackle potential future occurrences.
363 | 2017-02-23 | 30870934 | 80529301 | 17B Pump faulty vibration sensor | S4CW -4CWE5 | * **************Incident Description************** * Notification 000030870934 Details * *********************************************************** * 23/02/2017 09:35:19 INCIDENT REPORT (INCIDENT REPORT) * Report submitted by: Emily Thompson 098-765-4321 * * CONDITION DESCRIPTION/LOCATION (THE INAPPROPRIATE ACTION AND ITS NEGATIVE EFFECT/INCLUDE A DETAILED LOCATION DESCRIPTION): * During routine maintenance checks, sensor indicated extreme vibrations from the 17B Pump. However, other diagnostics and visual checks did not corroborate the sensor readings. The sensor may be faulty. * * ACTIVITIES, PROCESSES, PROCEDURES INVOLVED: * Routine maintenance and monitoring * * WHY DID CONDITION HAPPEN? * The sensor may be malfunctioning or require calibration. * * CONSEQUENCES: * False alarm and the potential to miss actual pump failure. * * REQUIREMENTS IMPACTED: * Regular sensor monitoring. * * ADVERSE PHYSICAL CONDITIONS: * Discrepancy in sensor readings * * WHO WAS NOTIFIED: * Maintenance Team * * KNOWLEDGEABLE INDIVIDUALS: * Maintenance Team, Engineer Davis * * REPEAT OR SIMILAR CONDITION: * No * * IMMEDIATE ACTIONS AND RECOMMENDED ACTIONS: * Sensor to be re-calibrated or replaced to ensure accurate readings. * 23/02/2017 12:16:13 EMILY THOMPSON (INCIDENT) * Sensor replacement has been ordered and is expected to arrive tomorrow. An emergency maintenance slot has been arranged to replace the sensor as soon as it arrives. | What could be the possible consequence of the identified sensor malfunction in the incident? | False alarm and the potential to miss actual pump failure.
364 | 2018-12-01 | 30860972 | 80245633 | Unusual vibration in 18B pump motor | S1CW -1CWE4-MTRB | * **************Incident Description************** * Notification 000030860972 Details * *********************************************************** * 12/01/2018 18:34:02 INCIDENT REPORT (INCIDENT REPORT) * Report submitted by: Emily Williams ENTITY\INCIDENT: * * CONDITION DESCRIPTION/LOCATION (THE INAPPROPRIATE ACTION AND ITS NEGATIVE EFFECT/INCLUDE A DETAILED LOCATION DESCRIPTION): * During the afternoon shift, the operations crew noticed an unusual vibration in the 18B pump motor. Safety protocols were initiated and 18B pump motor was shut down for precautionary measure. The indications were as follows: inlet pressure was normal, current was within limits but there was an unusual vibration on the motor exterior. * * ACTIVITIES, PROCESSES, PROCEDURES INVOLVED: * Daily Observation Procedure S1.OP-OB.CW-0002 * * WHY DID CONDITION HAPPEN? * The source of vibration is unknown. It might be due to internal damage or loose components within the motor. * * CONSEQUENCES: * Sustained vibration might damage the pump motor resulting in unplanned shutdown of operations. * * REQUIREMENTS IMPACTED: * Normal operation of the pump motor * * ADVERSE PHYSICAL CONDITIONS: * Unusual vibration of 18B pump motor * * WHO WAS NOTIFIED: * Supervisor, Maintenance team. * * KNOWLEDGEABLE INDIVIDUALS: * Supervisor, quality control engineer, maintenance team. * * REPEAT OR SIMILAR CONDITION: * No similar conditions were previously reported. * * IMMEDIATE ACTIONS AND RECOMMENDED ACTIONS: * Maintenance team to investigate the source of vibration in 18B pump motor. Manufacturing defects or component degradation should be considered. * 12/03/2018 10:22:25 EMILY WILLIAMS (NUSER) * Investigation found that an internal component of the motor was loose which caused the vibration. Necessary adjustments were made and the pump motor is now back to normal operation. | What was the observed issue with the 18B pump motor? | During the afternoon shift, the operations crew noticed an unusual vibration in the 18B pump motor. Safety protocols were initiated and 18B pump motor was shut down for precautionary measure. The indications were as follows: inlet pressure was normal, current was within limits but there was an unusual vibration on the motor exterior.
365 | 2022-01-30 | 40145268 | 90230749 | Vibrations from 33B Pump Motor | S4CW -4CWE8 | * **************Incident Description************** * Notification 000040145268 Details * *********************************************************** * SUMMARY: REVIEW UNDERLYING ISSUES AS PER * ****PS-DD-001 "PROBLEM IDENTIFICATION AND RESOLUTION"***** * * 1) CONDITION DESCRIPTION/LOCATION (THE INAPPROPRIATE ACTION AND ITS NEGATIVE EFFECT/INCLUDE A DETAILED LOCATION DESCRIPTION): * At 1502 on 1/30/22, operator sensed abnormal vibrations from 33B Pump Motor. The pump was safely shut down from Unit 4 Control Room and the vibration subsided. Safety inspection did not show any immediate cause but there was unusual noise upon attempt to run the motor again. This indicated possible internal problems within the pump’s mechanisms. S4.OP-DD.PT-0003 Pump Discrepancy Procedure was initiated due to the unexpected vibrations from 33B Pump. * * 2) ACTIVITIES, PROCESSES, PROCEDURES INVOLVED: * S4.OP.DD-PT-0003, S4.OP-SO.PT-0091 * * 3) WHY DID CONDITION HAPPEN: * Unknown, although similar incidents have occurred in the past * * 4) CONSEQUENCES: * Potential severe damage to the pump, affecting regular operations when the pump is needed * * 5) REQUIREMENTS IMPACTED: * Absence of 33B pump for normal operations * * 6) ADVERSE PHYSICAL CONDITION: * Vibrations from 33B Pump motor, probable internal component fault * * 7) WHO WAS NOTIFIED: * Control Room, Safety Team * * 8) KNOWLEDGEABLE INDIVIDUALS: * McAdams, Roberts, Wang * * 9) REPEAT OR SIMILAR CONDITION: * Yes * * 10) IMMEDIATE AND RECOMMENDED ACTIONS: * Engineering team to conduct a thorough inspection on the 33B Pump Motor * * Updated: JAMES BLACK 01.30.2022 16:15:27 * ------------------------------------------------------------ * 02/10/2022 | What was the immediate action taken regarding the abnormal vibrations sensed in the 33B Pump Motor? | The pump was safely shut down from Unit 4 Control Room and the vibration subsided.
366 | 2016-09-23 | 30768412 | 80229293 | Unusual Vibration from Pump 17C | S1CW -1CWE8 | * **************Incident Description************** * Notification 000030768412 Details * *********************************************************** * 09/23/2016 21:32:50 INCIDENT REPORT (INCIDENT REPORT) * Report submitted by: Taylor Johnson ENTITY\INCIDENT: * * CONDITION DESCRIPTION/LOCATION (THE INAPPROPRIATE ACTION AND ITS NEGATIVE EFFECT/INCLUDE A DETAILED LOCATION DESCRIPTION): * During night patrol, Operator Taylor Johnson noticed an unusual vibration from Pump 17C. Johnson called Maintenance, which determined that the pump needed immediate shut down due to bearing failure risk. Pump 17C was promptly shut down from Control Room. * * ACTIVITIES, PROCESSES, PROCEDURES INVOLVED: * S1.OP.AB-CW-0005, S1.OP-SO.CW-0003 * * WHY DID CONDITION HAPPEN? * Ball bearing failure is suspected. Further investigation is needed to confirm. * * CONSEQUENCES: * Increased risk of equipment failure, potential impact on operations if not addressed swiftly. * * REQUIREMENTS IMPACTED: * Potential loss of normal operation due to pump shutdown. * * ADVERSE PHYSICAL CONDITIONS: * Unusual vibration observed from Pump 17C. * * WHO WAS NOTIFIED: * Maintenance Team, Control Room * * KNOWLEDGEABLE INDIVIDUALS: * Johnson, Rodriguez, Lee * * REPEAT OR SIMILAR CONDITION: * Yes, reported vibration in pumps before. * * IMMEDIATE ACTIONS AND RECOMMENDED ACTIONS: * Maintenance team plans to replace the potentially faulty ball bearings in the pump. Maintenance will monitor the pump closely after repair and start up. * 09/24/2016 10:20:21 TAYLOR JOHNSON (INCIDENT) * Work order 80229321 was issued to replace ball bearings. Post maintenance run was successful with no unusual vibration observed. Pump 17C returned to normal operation. | Who noticed the unusual vibration from the pump and what was the immediate action taken? | Operator Taylor Johnson noticed an unusual vibration from Pump 17C. Johnson called Maintenance, which determined that the pump needed immediate shut down due to bearing failure risk. Pump 17C was promptly shut down from Control Room.
367 | 2022-01-12 | 30894372 | 80322118 | Unusual vibration from motor 7B | S4CW -4CWE1 | * **************Incident Description************** * Notification 000030894372 Details * *********************************************************** * 01/12/2022 15:27:36 INCIDENT REPORT (INCIDENT REPORT) * Report submitted by: Kim Martinez ENTITY\INCIDENT: * * CONDITION DESCRIPTION/LOCATION (THE INAPPROPRIATE ACTION AND ITS NEGATIVE EFFECT/INCLUDE A DETAILED LOCATION DESCRIPTION): * During the scheduled maintenance of motor 7B noticeable vibration was detected from the drive shaft. The vibration was not seen before and there were no other physical symptoms present. The motor was promptly shut down for safety reasons and to avoid potential damage to other components. The Unit 4 Control Room was engaged and the situation was reported. * * ACTIVITIES, PROCESSES, PROCEDURES INVOLVED: * S4.OP.AB-CW-0001, S4.OP-SO.CW-0001 * * WHY DID CONDITION HAPPEN? * The cause is not immediately known. Other similar motors have had some vibration in the past, but this case seems more pronounced. * * CONSEQUENCES: * Unknown motor condition may lead to wider system interruption if not addressed quickly. * * REQUIREMENTS IMPACTED: * Motor reliability and system continuity. * * ADVERSE PHYSICAL CONDITIONS: * High vibration level of the drive shaft in motor 7B * * WHO WAS NOTIFIED: * Control Room, Maintenance Team * * KNOWLEDGEABLE INDIVIDUALS: * Kim Martinez, Sam Lewis, Riley Peterson * * REPEAT OR SIMILAR CONDITION: * No same incidents before, but similar problems in other system components. * * IMMEDIATE ACTIONS AND RECOMMENDED ACTIONS: * Immediate shutdown of the motor was initiated, maintenance unit to investigate the cause of the vibration and report on the recommended actions to remedy the situation. * 01/15/2022 13:13:02 MARK TAYLOR (ENGINEER) * Identified as a balance issue of the drive shaft, re-balancing the drive shaft has removed the vibration. Motor 7B has been tested and returned to Service under | What was the discovered issue with motor 7B and what action was taken to address it? | Identified as a balance issue of the drive shaft, re-balancing the drive shaft has removed the vibration. Motor 7B has been tested and returned to Service.
368 | 2019-05-30 | 30937515 | 90213875 | SWING CHECK VALVE JAMMING | S4PV -4PVE8 | * **************Incident Description************** * Notification 000030937515 Details * *********************************************************** * 05/30/2019 14:44:26 INCIDENT REPORT (INCIDENT REPORT) * Report submitted by: Richard Williams ENTITY\INCIDENT: * * CONDITION DESCRIPTION/LOCATION (THE INAPPROPRIATE ACTION AND ITS NEGATIVE EFFECT/INCLUDE A DETAILED LOCATION DESCRIPTION): * During routine monitoring, the operator reported that swing check valve in the pipeline has been experiencing unnecessary resistance/jamming. As SWING CHECK VALVE is crucial for flow non-return, continuous pattern of such disturbances could lead to serious implications on flow and the associated equipment. * * ACTIVITIES, PROCESSES, PROCEDURES INVOLVED: * Regular checkup, S4.OP.SO.PV-0002 * WHY DID CONDITION HAPPEN? * Unknown, Possible corrosion/sediment buildup. * * CONSEQUENCES: * Potential valve failure, interrupted flow. * * REQUIREMENTS IMPACTED: * Functioning valve * * ADVERSE PHYSICAL CONDITIONS: * Valve jamming/resistance * * WHO WAS NOTIFIED: * Control Room, Maintenance * * KNOWLEDGEABLE INDIVIDUALS: * Control Room Supervisor, Operator, Maintenance Technician * * REPEAT OR SIMILAR CONDITION: * Yes, random incidents were observed in the past. * * IMMEDIATE ACTIONS AND RECOMMENDED ACTIONS: * Valve cleanup, replace if required. If jamming continues, whole system flush might be necessary. * 05/31/2019 08:22:38 BRITTANY CARTER (OWNER) * Maintenance response reported the issue was due to sediment buildup causing the valve to jam. After a cleanup, the valve is functioning smoothly. Another cleanup has been scheduled as a safety measure. A system flush will be conducted timely. | What immediate action was recommended to fix the issue with the swing check valve? | Valve cleanup, replace if required. If jamming continues, whole system flush might be necessary.
369 | 2019-12-12 | 40031572 | 90267584 | Elevator 3A bearing vibrations | S5EV -3EVA1 | * **************Incident Description************** * Notification 000040031572 Details * *********************************************************** * 12/12/2019 14:08:00 INCIDENT REPORT (INCIDENT REPORT) * Report submitted by: Daniel Fox ENTITY\INCIDENT: * * CONDITION DESCRIPTION/LOCATION (THE INAPPROPRIATE ACTION AND ITS NEGATIVE EFFECT/INCLUDE A DETAILED LOCATION DESCRIPTION): * Elevator 3A bearing experienced unusual vibrations during operation. An emergency shutdown was initiated, resulting in the temporary cessation of elevator services. No physical harm was reported from the incident, but concerns of internal damage were raised. * * ACTIVITIES, PROCESSES, PROCEDURES INVOLVED: * Emergency shutdown procedure, routine operation check * * WHY DID CONDITION HAPPEN? * Unknown. Despite regular maintenance, the issue occurred, suggesting possible component fatigue or unaddressed structural issues. * * CONSEQUENCES: * Safety risks, operational delays, possible expensive repairs if there's severe internal damage. * * REQUIREMENTS IMPACTED: * Normal operations, safety regulations * * ADVERSE PHYSICAL CONDITIONS: * Unusual vibrations of bearing in Elevator 3A * * WHO WAS NOTIFIED: * Incident Response Team, Building Management * * KNOWLEDGEABLE INDIVIDUALS: * Maintenance Team, Incident Response Team * * REPEAT OR SIMILAR CONDITION: * No. This is a first-time occurrence. * * IMMEDIATE ACTIONS AND RECOMMENDED ACTIONS: * Elevator to be inspected thoroughly by maintenance team for identifying the issue source and potential damage. If necessary, repairs or replacement of components must be conducted promptly. * 12/16/2019 10:52:17 DANIEL FOX (INCIDENT) * Inspection revealed a misalignment in the bearing assembly. Necessary adjustments were made and the elevator is back in service with no reported issues. | What was the cause of the unusual vibration in Elevator 3A and what immediate action was taken? | Inspection revealed a misalignment in the bearing assembly. Necessary adjustments were made and the elevator is back in service with no reported issues.
370 | 2022-01-15 | 31020514 | 90212347 | 16B Pump Vibration Alarm | S4JB -4JBE7 | * **************Incident Description************** * Notification 000031020514 Details * *********************************************************** * 01/15/2022 09:12:00 INCIDENT REPORT (INCIDENT REPORT) * Report submitted by: Sam Waters ENTITY\INCIDENT: * * CONDITION DESCRIPTION/LOCATION (THE INAPPROPRIATE ACTION AND ITS NEGATIVE EFFECT/INCLUDE A DETAILED LOCATION DESCRIPTION): At 08:35 on 15/01/22, the operator noted a high vibration indicated by an alarm from the 16B pump control panel. Visual inspection showed noticeable vibration in the lines feeding the pump. Event was noted, and 16B Pump was shutdown from Main Control Room. Pump restart attempt was unsuccessful. * * ACTIVITIES, PROCESSES, PROCEDURES INVOLVED: * S4.PP.JB-0001, S4.MT.SO.JB-0003 * * WHY DID CONDITION HAPPEN: * The high vibration levels are unexplained. Previous maintenance was completed in December 2021 on this pump. * * CONSEQUENCES: * Continued operation could lead to pump failure and loss of pumping capacity. * * REQUIREMENTS IMPACTED: * Continued safe operation of Plant. * * ADVERSE PHYSICAL CONDITIONS: * Increased Vibration in 16B Pump. * * WHO WAS NOTIFIED: * Control Room, Maintenance Team * * KNOWLEDGEABLE INDIVIDUALS: * Johnson, Ryan, Kelly * * REPEAT OR SIMILAR CONDITION: * No known instances of similar conditions in this pump's history. * * IMMEDIATE ACTIONS AND RECOMMENDED ACTIONS: Maintenance to overhaul 16B Pump to investigate and correct source of vibration. * 01/15/2022 13:32:00 SAM WATERS (INCIDENT) * A maintenance inspection has discovered that the pump's bearings were worn significantly. The pump is scheduled for immediate repair and replacement of the bearings. The bearing material will be analyzed to determine the root cause of the abnormal wear. | What immediate actions and recommended actions were taken for the high vibration in the 16B Pump? | Maintenance to overhaul 16B Pump to investigate and correct source of vibration. A maintenance inspection has discovered that the pump's bearings were worn significantly. The pump is scheduled for immediate repair and replacement of the bearings. The bearing material will be analyzed to determine the root cause of the abnormal wear.
371 | 2020-03-25 | 30957319 | 80245639 | 9D Engine Misfire | S4EC -4ECE1 | * **************Incident Description************** * Notification 000030957319 Details * *********************************************************** * 03/25/2020 14:30:49 INCIDENT REPORT (INCIDENT REPORT) * Report submitted by: Emily Johnson ENTITY\INCIDENT: * * CONDITION DESCRIPTION/LOCATION (THE INAPPROPRIATE ACTION AND ITS NEGATIVE EFFECT/INCLUDE A DETAILED LOCATION DESCRIPTION): * Following regular maintenance procedures, the 9D engine was reported showing signs of misfire. The symptoms were identified during a regular test run at 1347 hrs on 03/25/20. Misfires were intermittent but consistent throughout the test. The 9D engine was immediately shut down to avoid potential damage. No external signs of damage were visible and the exact cause has yet to be determined. * * ACTIVITIES, PROCESSES, PROCEDURES INVOLVED: * S4.EN.OP-AB.EC-0001, S4.EN.SO.EC-0001 * * WHY DID CONDITION HAPPEN? * Currently unknown, subject to an ongoing investigation. Possibilities include spark plug malfunction, poor fuel quality, or internal engine components degradation. * * CONSEQUENCES: * A misfiring engine can result in loss of performance, increased emissions and potential internal damage if not addressed in due course. * * REQUIREMENTS IMPACTED: * Regular engine services and operations. * * ADVERSE PHYSICAL CONDITIONS: * Intermittent misfire from 9D engine, possible internal damage * * WHO WAS NOTIFIED: * Control Room, Maintenance Department * * KNOWLEDGEABLE INDIVIDUALS: * Thompson, Baker, Hughes * * REPEAT OR SIMILAR CONDITION: * No, this is an isolated incident. * * IMMEDIATE ACTIONS AND RECOMMENDED ACTIONS: * Mechanics and engineers to investigate further the 9D engine conditions * * Updated: EMILY JOHNSON 03.25.2020 14:58:23 * ---------------------------------------------------------- * 03/27/2020 09:10:00 JOHN SMITH (INCIDENT) * The investigation concluded that | What were the consequences of the engine misfire? | A misfiring engine can result in loss of performance, increased emissions and potential internal damage if not addressed in due course.
372 | 2021-06-08 | 30985231 | 80378139 | Overload warning on Pump 3X | S1CW -1CWE5 | * **************Incident Description************** * Notification 000030985231 Details * *********************************************************** * 06/08/2021 13:32:08 INCIDENT REPORT (INCIDENT REPORT) * Report submitted by: Parker Green ENTITY\INCIDENT: * CONDITION DESCRIPTION/LOCATION (THE INAPPROPRIATE ACTION AND ITS NEGATIVE EFFECT/INCLUDE A DETAILED LOCATION DESCRIPTION): * During normal operations, Overload warning on Pump 3X was detected. Temperature and pressure readings were observed to be within normal range. This issue has never been encountered with this pump before. Additional monitoring initiated and motor continues to run. * * ACTIVITIES, PROCESSES, PROCEDURES INVOLVED: * S1.OP-AB.CW-0002, S1.OP-SO.CW-0003 * * WHY DID CONDITION HAPPEN? * Unknown cause, possibly an electrical issue or mechanical stress * * CONSEQUENCES: * Sudden shutdown of 3X Pump may happen affecting the normal operations * * REQUIREMENTS IMPACTED: * Pump 3X normal operation * * ADVERSE PHYSICAL CONDITIONS: * Overload warning on Pump 3X * * WHO WAS NOTIFIED: * Control Room, Maintenance Head, Engineer's Desk * * KNOWLEDGEABLE INDIVIDUALS: * Parker, Lopez, Morris * * REPEAT OR SIMILAR CONDITION: * No, this is a first-time event for Pump 3X * * IMMEDIATE ACTIONS AND RECOMMENDED ACTIONS: * Engineering and maintenance teams to jointly investigate Pump 3X, Monitor for any additional symptoms closely. * 06/08/2021 15:12:47 PARKER GREEN (INCIDENT) * Investigation underway. Preliminary inspection does not reveal visual abnormalities. Detailed inspection and tests aligned. | What was the initial observation when the overload warning on Pump 3X was detected? | During normal operations, Overload warning on Pump 3X was detected. Temperature and pressure readings were observed to be within normal range. This issue has never been encountered with this pump before. Additional monitoring initiated and motor continues to run.
373 | 2020-09-15 | 30912548 | 90223619 | Overheating observed in 9BP pump | S3CW -3CWE7 | * **************Incident Description************** * Notification 000031092548 Details * *********************************************************** * 09/15/2020 07:32:10 INCIDENT REPORT (INCIDENT REPORT) * Report submitted by: Thomas Green ENTITY\INCIDENT: * * CONDITION DESCRIPTION/LOCATION (THE INAPPROPRIATE ACTION AND ITS NEGATIVE EFFECT/INCLUDE A DETAILED LOCATION DESCRIPTION): * During a routine inspection on September 15, 2020, at 0730, the 9BP Pump was found to be excessively hot. The pump is located in Unit 3, and upon inspection, was found to be operating at higher temperatures compared to other pumps in the same unit. Temperatures were recorded to be critical and the pump was shut down immediately. Witnessed a slight smoke emission, potentially indicating an insulation burnout. * * ACTIVITIES, PROCESSES, PROCEDURES INVOLVED: * S3.OP.AB-PW-0002, S3.OP-SO.PW-0001 * * WHY DID CONDITION HAPPEN? * Unknown, previous instances of overheating have been recorded. * * CONSEQUENCES: * Possible pump motor damage and reduced efficiency * * REQUIREMENTS IMPACTED: * Affects the operational readiness of the pump * * ADVERSE PHYSICAL CONDITIONS: * Overheating of the pump, potential internal damages * * WHO WAS NOTIFIED: * Supervisors, Incident Team, Control Room * * KNOWLEDGEABLE INDIVIDUALS: * Taylor, Cooper, Miller * * REPEAT OR SIMILAR CONDITION: * Yes, Previous occurrences noted * * IMMEDIATE ACTIONS AND RECOMMENDED ACTIONS: * Maintenance team to investigate and repair 9BP Pump * 09/17/2020 11:51:32 THOMAS GREEN (INCIDENT) * Post investigation, it was identified as an overheating issue due to an internal blockage. Technicians cleared the blockage and the pump has resumed normal operations. Future similar issues are to be prevented with regular cleaning schedules. | What was the immediate action taken after finding the pump in a critical condition? | Maintenance team to investigate and repair 9BP Pump
374 | 2022-01-18 | 40798522 | 90172832 | 17A Energy Fluctuation | S4PW -4PWE7 | * **************Incident Description************** * Notification 000040798522 Details * *********************************************************** * 01/18/2022 14:01:57 INCIDENT REPORT (INCIDENT REPORT) * Report submitted by: Sam Lewis ENTITY\INCIDENT: * * CONDITION DESCRIPTION/LOCATION (THE INAPPROPRIATE ACTION AND ITS NEGATIVE EFFECT/INCLUDE A DETAILED LOCATION DESCRIPTION): * During routine maintenance checks, it was observed that Energy Distribution Center 17A displayed sudden energy fluctuations. The energy output varied uncontrollably between 50-90%. There had been no recent modifications or accidents which would justify such drastic fluctuations in energy output. * * ACTIVITIES, PROCESSES, PROCEDURES INVOLVED: * Routine maintenance supervision, S4.OP.17A-ED-0002 * * WHY DID CONDITION HAPPEN? * Unknown, potential issues with redistributor or interference. * * CONSEQUENCES: * Potential threat to stability of overall energy grid, reduced efficiency. * * REQUIREMENTS IMPACTED: * Energy output predictability, stability of feed to consumption sectors. * * ADVERSE PHYSICAL CONDITIONS: * None detected beyond system reading discrepancies. * * WHO WAS NOTIFIED: * Control Centre, Supervisor * * KNOWLEDGEABLE INDIVIDUALS: * Distribution Supervisor, Control Centre Manager, Senior Engineer * * REPEAT OR SIMILAR CONDITION: * No, first time occurrence * * IMMEDIATE ACTIONS AND RECOMMENDED ACTIONS: * Energy fluctuation should be investigated with a priority on the distributor component as that is often the cause of such glitches. Consulting with the manufacturer may also be beneficial. * 01/20/2022 11:15:57 SAM LEWIS (INCIDENT) * Post inspections reveal that redistributor was functioning well and manufacturer's consult yielded no mechanical default. Potential cause might be interference or system glitch. Running additional diagnostics. | What were the immediate and recommended actions following the energy distribution center incident? | Energy fluctuation should be investigated with a priority on the distributor component as that is often the cause of such glitches. Consulting with the manufacturer may also be beneficial.
375 | 2018-04-11 | 30825497 | 80223641 | High Pressure in Disk Pump 13B | S1CW -1CWE5 | * **************Incident Description************** * Notification 000030825497 Details * *********************************************************** * 04/11/2018 08:32:45 INCIDENT REPORT (INCIDENT REPORT) * Report submitted by: Jennifer Thompson ENTITY\INCIDENT: * * CONDITION DESCRIPTION/LOCATION (THE INAPPROPRIATE ACTION AND ITS NEGATIVE EFFECT/INCLUDE A DETAILED LOCATION DESCRIPTION): * During a scheduled system check, the 13B Disk Pump displayed unusually high pressure. Further checks showed the operating pressure to be around 35 psi, a significant increase from the usual 20 psi. The pump was immediately brought offline to avoid equipment damage and a detailed system review was initiated. * * ACTIVITIES, PROCESSES, PROCEDURES INVOLVED: * Scheduled System Check * WHY DID CONDITION HAPPEN? * Unknown, possible causes could be blockages or pump malfunctions. * * CONSEQUENCES: * Potential system downtime, unanticipated pump replacement costs. * * REQUIREMENTS IMPACTED: * Regular system operation * * ADVERSE PHYSICAL CONDITIONS: * High pump pressure * * WHO WAS NOTIFIED: * Incident Control Team, Maintenance Supervisor * * KNOWLEDGEABLE INDIVIDUALS: * Jason, Laura, Michaels * * REPEAT OR SIMILAR CONDITION: * No * * IMMEDIATE ACTIONS AND RECOMMENDED ACTIONS: * Immediate actions include offline check, system review. If the issue remains after check, maintenance should be scheduled. * 04/11/2018 12:07:59 JENNIFER THOMPSON (INCIDENT) * Initial checks did not reveal any system blockages. Maintenance has been scheduled for further investigation. January DOE (Incident) has been tasked with coordinating. | What immediate actions were taken when the 13B Disk Pump displayed unusually high pressure? | Immediate actions include offline check, system review. If the issue remains after check, maintenance should be scheduled.
376 | 2022-01-25 | 40019872 | 90236547 | 10B condenser pump unusual vibration | S4CW -4CWE2 | * **************Incident Description************** * Notification 000040019872 Details * *********************************************************** * 01/25/2022 14:01:15 INCIDENT REPORT (INCIDENT REPORT) * Report submitted by: Olivia Thompson ENTITY\INCIDENT: * * CONDITION DESCRIPTION/LOCATION (THE INAPPROPRIATE ACTION AND ITS NEGATIVE EFFECT/INCLUDE A DETAILED LOCATION DESCRIPTION): * Following a recent service, the 10B Condenser pump began to emit unusual vibrations, despite all previous post-maintenance checks reporting normal functionality. As the abnormality resided within the designated operating guidelines, the pump was not shut down, but an emergency inspection was initiated for a comprehensive understanding of the situation. * * ACTIVITIES, PROCESSES, PROCEDURES INVOLVED: * S4.OP-PA.CW-0002, the pump service, was recently implemented. * * WHY DID CONDITION HAPPEN? * Unclear at this time. Suggest further review into the success of S4.OP-PA.CW-0002. * * CONSEQUENCES: * Potential pump damage and disruption of cooling operations. * * REQUIREMENTS IMPACTED: * Routine operation and equipment integrity. * * ADVERSE PHYSICAL CONDITIONS: * Unusual vibration in 10B condenser pump post-maintenance. * * WHO WAS NOTIFIED: * Maintenance Manager, Operations Supervisor. * * KNOWLEDGEABLE INDIVIDUALS: * Thompson, Harris, Gonzalez * * REPEAT OR SIMILAR CONDITION: * No similar instances found at this time. * * IMMEDIATE ACTIONS AND RECOMMENDED ACTIONS: * To undertake a thorough review of the S4.OP-PA.CW-0002 procedure and conduct further testing of 10B pump. * 01/29/2022 16:32:20 OLIVIA THOMPSON (INCIDENT) * Upon further testing, it was discovered that the vibrations were due to an imbalance in the pump impeller. The pump has been taken out of service and the impeller replaced. The testing did not reveal any faults in the implemented procedure. | What was the unusual condition observed in the 10B Condenser pump, and what was the action taken in response to it? | Following a recent service, the 10B Condenser pump began to emit unusual vibrations, despite all previous post-maintenance checks reporting normal functionality. As the abnormality resided within the designated operating guidelines, the pump was not shut down, but an emergency inspection was initiated for a comprehensive understanding of the situation. Upon further testing, it was discovered that the vibrations were due to an imbalance in the pump impeller. The pump has been taken out of service and the impeller replaced. The testing did not reveal any faults in the implemented procedure.
377 | 2017-02-18 | 30918726 | 80231251 | 7B pump low output pressure | S3CW -3CWX1 | * **************Incident Description************** * Notification 000030918726 Details * *********************************************************** * 02/18/2017 08:28:40 INCIDENT REPORT (INCIDENT REPORT) * Report submitted by: Frank Mitchell ENTITY\INCIDENT: * * CONDITION DESCRIPTION/LOCATION (THE INAPPROPRIATE ACTION AND ITS NEGATIVE EFFECT/INCLUDE A DETAILED LOCATION DESCRIPTION): * Inspection on 02/18/2017 7B Pump indicated a lower output pressure than expected. The 7B Pump operates normally for all other parameters, but observed pressure should be 85 psig, it only delivers 78 psig. This event was not seen in previous operation and all other pumps are operating within specified limits. * * ACTIVITIES, PROCESSES, PROCEDURES INVOLVED: * Regular integrity and pressure-checking measures, S3.OP-AB.CW-0007 * * WHY DID CONDITION HAPPEN? * Unknown at present, possible blockage or wear on pump components. * * CONSEQUENCES: * Reduced efficiency of pump operation, potential for failure if not addressed. * * REQUIREMENTS IMPACTED: * Pump efficiency and function impacted, potential process delays. * * ADVERSE PHYSICAL CONDITIONS: * Lower output pressure from 7B pump * * WHO WAS NOTIFIED: * Maintenance Team, Supervisor * * KNOWLEDGEABLE INDIVIDUALS: * Maintenance Team, Supervisor, System Engineers * * REPEAT OR SIMILAR CONDITION: * No, first occurrence noted * * IMMEDIATE ACTIONS AND RECOMMENDED ACTIONS: * Request complementary team for inspection. If blockage is noted, remove blockage and restore pump. In case of component wear, a replacement maybe required. * 02/20/2017 10:16:30 BARBARA DOE (INCIDENT) * Investigation found slight wear on pump components. The components have been replaced and the pump is returned to service. Output pressure now at expected 85 psig. No further anomalous conditions observed. | What was the initial problem with the 7B Pump? | Inspection on 02/18/2017 7B Pump indicated a lower output pressure than expected. The 7B Pump operates normally for all other parameters, but observed pressure should be 85 psig, it only delivers 78 psig. This event was not seen in previous operation and all other pumps are operating within specified limits.
378 | 2017-12-09 | 30974645 | 80549732 | Leakage detected in pump 19C | S4CW -4CWE7 | * **************Incident Description************** * Notification 000030974645 Details * *********************************************************** * 12/09/2017 17:33:40 INCIDENT REPORT (INCIDENT REPORT) * Report submitted by: Robert Green ENTITY\INCIDENT: * * CONDITION DESCRIPTION/LOCATION (THE INAPPROPRIATE ACTION AND ITS NEGATIVE EFFECT/INCLUDE A DETAILED LOCATION DESCRIPTION): * Notification 30974645 was created after the operator reported water leakage in the 19C Pump during overall system monitoring. The unit was manually shut down and isolated from the rest of the pumping system. The leakage area was cooled down and the spare unit put into operation. * * ACTIVITIES, PROCESSES, PROCEDURES INVOLVED: * System monitoring, Manual shutdown, S4.OP.AB-CW-0002, S4.OP-SO.CW-0002 * * WHY DID CONDITION HAPPEN? * Leak could have been due to wear and tear, impact damage or inefficient seals. Actual cause is yet to be determined after inspection. * * CONSEQUENCES: * Immediate reduction in pumping capacity, but compensated with the functioning of spare unit. Long-term effect would be the cost of repair and potential scheduling delays. * * REQUIREMENTS IMPACTED: * Pumping capacity and system integrity * * ADVERSE PHYSICAL CONDITIONS: * Water leakage from 19C Pump could lead to potential structural damage * * WHO WAS NOTIFIED: * Operations Supervisor, Maintenance Team * * KNOWLEDGEABLE INDIVIDUALS: * Davis, Thompson, Stewart * * REPEAT OR SIMILAR CONDITION: * No, this is an isolated incident * * IMMEDIATE ACTIONS AND RECOMMENDED ACTIONS: * The maintenance team has been dispatched to identify the problem and take corrective action. Depending on the nature and extent of the problem, the pump may need to be replaced or refurbished. * 12/09/2017 19:54:15 ROBERT GREEN (INCIDENT) * A preliminary inspection seems to suggest a failure in the pump's seal. The detailed investigation will provide further insights. | What immediate and long-term consequences the water leakage from the 19C Pump might have led to? | Immediate reduction in pumping capacity, but compensated with the functioning of spare unit. Long-term effect would be the cost of repair and potential scheduling delays.
379 | 2020-11-25 | 30971524 | 80252470 | Leaking at Pump 18B | S4CW -4CWE7 | * **************Incident Description************** * Notification 000030971524 Details * *********************************************************** * 11/25/2020 06:08:43 INCIDENT REPORT (INCIDENT REPORT) * Report submitted by: Kim Davis ENTITY\INCIDENT: * * CONDITION DESCRIPTION/LOCATION (THE INAPPROPRIATE ACTION AND ITS NEGATIVE EFFECT/INCLUDE A DETAILED LOCATION DESCRIPTION): * At 0608 hours on 25/11/20, the operator noted a small oil leak from Pump 18B. The pump was not in operation at the time. The leak seemed to be emanating from the casing bolt flanges. A temporary oil catchment was put in place to capture the leak and prevent further contamination. * * ACTIVITIES, PROCESSES, PROCEDURES INVOLVED: * Inspection, Restricted operation * * WHY DID CONDITION HAPPEN? * Unknown, possible wear on washers or loosened bolts. * * CONSEQUENCES: * Potential oil spill, restricted pump operation, environmental concerns * * REQUIREMENTS IMPACTED: * Pump 18B operation * * ADVERSE PHYSICAL CONDITIONS: * Small oil leak at pump * * WHO WAS NOTIFIED: * Supervisor, Environment Safety Officer * * KNOWLEDGEABLE INDIVIDUALS: * Supervisor, Operations Staff, Environment Safety Officer * * REPEAT OR SIMILAR CONDITION: * No * * IMMEDIATE ACTIONS AND RECOMMENDED ACTIONS: * Cordon off, put up signs, coordinated cleanup and further inspection. * 11/26/2020 11:00:15 JOHN DOE (INCIDENT) * After inspection, it was revealed that some bolts had become loose over time since the last maintenance. The bolts were tightened and the leak has stopped. A full service is recommended at the next scheduled downtime to verify the integrity of the other bolts and washers. | What immediate actions were recommended after the oil leak from Pump 18B was discovered? | Cordon off, put up signs, coordinated cleanup and further inspection.
380 | 2020-05-15 | 30912477 | 81547257 | Overheating on Pump Motor 32C | S3CW -3CWE5 | * **************Incident Description************** * Notification 000030912477 Details * *********************************************************** * 05/15/2020 13:21:12 INCIDENT REPORT (INCIDENT REPORT) * Report submitted by: Mark Greene ENTITY\INCIDENT: * * CONDITION DESCRIPTION/LOCATION (THE INAPPROPRIATE ACTION AND ITS NEGATIVE EFFECT/INCLUDE A DETAILED LOCATION DESCRIPTION): * At 1300 on 5/15/20, we discovered that Pump Motor 32C was overheating during normal operation. Emergency procedures were initiated, and the pump was shut off immediately to prevent any potential damage or fire hazard. Upon inspection, no signs of external damage or abnormal wear were observed. * ACTIVITIES, PROCESSES, PROCEDURES INVOLVED: * S3.OP.AB-CW-0001, S3.OP-SO.CW-0001 * WHY DID CONDITION HAPPEN? * It is not certain, but a possible explanation could be an internal blockage or a malfunctioning coolant system. * CONSEQUENCES: * Unavailable motor, potential motor damage, risk of fire * REQUIREMENTS IMPACTED: * Normal operation and potential risk control * ADVERSE PHYSICAL CONDITIONS: * High heat from Pump Motor 32C * WHO WAS NOTIFIED: * Control Room, Fire Department, Operations Team * KNOWLEDGEABLE INDIVIDUALS: * Mark Greene, John Smith, Emily Davis * REPEAT OR SIMILAR CONDITION: * No, this is the first incident of this nature with Pump Motor 32C * IMMEDIATE ACTIONS AND RECOMMENDED ACTIONS: * Initiated emergency shutdown of the 32C Pump. Maintenance is recommended to thoroughly inspect and rectify the overheating problem of 32C Pump. * Updated: MARK GREENE 05.15.2020 14:31:27 * ------------------------------------------------------------- * 05/20/2020 10:30:33 ALEX BROWN (INCIDENT) * The overheating was due to a failed cooling system within the | What immediate action was taken after the overheating of Pump Motor 32C was discovered? | Emergency procedures were initiated, and the pump was shut off immediately to prevent any potential damage or fire hazard.
381 | 2019-10-11 | 30986632 | 80478491 | Emergency shutdown of 30C Pump motor | S4CW -4CWE2 | * **************Incident Description************** * Notification 000030986632 Details * *********************************************************** * 10/11/2019 14:23:44 INCIDENT REPORT (INCIDENT REPORT) * Report submitted by: William Sanders ENTITY\INCIDENT: * * CONDITION DESCRIPTION/LOCATION (THE INAPPROPRIATE ACTION AND ITS NEGATIVE EFFECT/INCLUDE A DETAILED LOCATION DESCRIPTION): * At 1356 on 10/11/19, the control room detected an isolation signal on the 30C pump motor. The motor was urgently deactivated from Control room. Upon inspection, no fire or damage was observed, but a slight burning smell was detected. External conditions appeared similar to other pumps in operation. Abnormalities in pump 30C led to its emergency shutdown according to S4.OP-AB.CW-0004. * * ACTIVITIES, PROCESSES, PROCEDURES INVOLVED: * S4.OP.AB-CW-0004, S4.OP-SO.CW-0003 * * WHY DID CONDITION HAPPEN? * At this stage, the reason remains unidentified, despite previous instances of pump motors overheating. * * CONSEQUENCES: * No immediate outcome, but potential unseen damage might cause a decrease in efficiency once the unit resumes its operation. * * REQUIREMENTS IMPACTED: * The pump is currently out of order. * * ADVERSE PHYSICAL CONDITIONS: * Possible internal damage and heat from the 30C pump motor. * * WHO WAS NOTIFIED: * Operations team, Fire Department. * * KNOWLEDGEABLE INDIVIDUALS: * Johnson, Parker, Davis. * * REPEAT OR SIMILAR CONDITION: * Unconfirmed. * * IMMEDIATE ACTIONS AND RECOMMENDED ACTIONS: * A thorough inspection of the 30C Pump Motor by the maintenance team is recommended. * * Updated: WILLIAM SANDERS 10.11.2019 15:32:10 * ------------------------------------------------------- * 10/20/2019 10:43:40 SAMANTHA DOE (INCIDENT) * Further Investigation uncovered that the event was not due to an electrical malfunction of the | Who was notified about the incident involving the 30C pump motor? | Operations team, Fire Department.
382 | 2020-09-15 | 400930343 | 91010232 | Overheating in 25B generator | S4CG -4CWE8-GEN | * **************Incident Description************** * Notification 0000400930343 Details * *********************************************************** * SUMMARY: CHECKING STANDARD OPERATING PROCEDURES IN LINE WITH * ****PS-NV-735 "GENERATOR MANAGEMENT AND MAINTENANCE PROCESS"***** * * 1) Condition Description/Location (The inappropriate action and its negative effect/Include a detailed location description): * At 1310 on 9/15/20, the maintenance officer reported intense heat from the 25B generator. The generator was promptly shut down from Control Station 4 and the heat released. Initial inspection uncovered no fire but there was an evident smell of charred wires. Generator temperature readings were in line with those currently operational and no external signs of damage were detected. S4.OP-AB.CW-0005 Generator Overheating Procedure was implemented due to the immediate shutdown of 25B Generator. * * 2) ACTIVITIES, PROCESSES, PROCEDURES INVOLVED: * S4.OP.AB-CG-0005, S4.OP-SO.CW-0003 * * 3) WHY DID CONDITION HAPPEN: * Uncertain, although generator overheating has occurred before * * 4) CONSEQUENCES: * No immediate consequences, but possible generator damage may cause efficiency loss when brought back online. * * 5) REQUIREMENTS IMPACTED: * Hindered generator functionality * * 6) ADVERSE PHYSICAL CONDITION: * Overheating of 25B Generator, potential internal damage * * 7) WHO WAS NOTIFIED: * Control Station, Maintenance Team * * 8) KNOWLEDGEABLE INDIVIDUALS: * Rodriguez, Kim, Patel * * 9) REPEAT OR SIMILAR CONDITION: * Uncertain * * 10) IMMEDIATE AND RECOMMENDED ACTIONS: * Maintenance should inspect 25B Generator * * Updated: GEORGE ROE 09.15.2020 14:30:23 * ------------------------------------------------------------ * 09/23/2020 10:32: | What immediate procedure was undertaken due to the overheating of the 25B Generator? | S4.OP-AB.CW-0005 Generator Overheating Procedure was implemented due to the immediate shutdown of 25B Generator.
383 | 2017-03-12 | 30850763 | 80432346 | 8B Pump motor vibration post maintenance | S4CW -4CWE8 | * **************Incident Description************** * Notification 000030850763 Details * *********************************************************** * 03/12/2017 15:17:42 INCIDENT REPORT (INCIDENT REPORT) * Report submitted by: Laura Johnson ENTITY\INCIDENT: * * CONDITION DESCRIPTION/LOCATION (THE INAPPROPRIATE ACTION AND ITS NEGATIVE EFFECT/INCLUDE A DETAILED LOCATION DESCRIPTION): * After returning from regular maintenance, 8B Pump started exhibiting unusual vibrations. The vibrations are not with consistent frequency. Maintenance records don't show any immediate cause for this condition. This pump was serviced under work order 80432346. * * ACTIVITIES, PROCESSES, PROCEDURES INVOLVED: * Regular maintenance check on 8B Pump was performed. * WHY DID CONDITION HAPPEN? * Unidentified, requires further investigation, possibly some alignment or balance issue post maintenance. * * CONSEQUENCES: * The abnormal vibration of the pump motor can potentially cause wear and tear, reducing the overall service life of the motor. * * REQUIREMENTS IMPACTED: * Normal operation of 8B Pump. Noise and vibration limits. * * ADVERSE PHYSICAL CONDITIONS: * High vibration levels in 8B Pump motor. * * WHO WAS NOTIFIED: * Supervisor/ Maintenance Team * * KNOWLEDGEABLE INDIVIDUALS: * Maintenance Team * * REPEAT OR SIMILAR CONDITION: * No, this is a new incident. * * IMMEDIATE ACTIONS AND RECOMMENDED ACTIONS: * Need to perform a thorough mechanical assessment of 8B Pump Motor. If necessary, component replacements should be done to reduce the vibrations. * 03/15/2017 10:53:43 LAURA JOHNSON (INCIDENT) * The inspection team has identified the problem to be aligned with shaft balance. A rebalance of the shaft in the 8B Pump motor has been recommended. | What was the initial issue found with the 8B Pump after regular maintenance? | After returning from regular maintenance, 8B Pump started exhibiting unusual vibrations. The vibrations are not with consistent frequency.
384 | 2019-04-15 | 30809455 | 80233850 | F3B Pump Failed to Start During Routine Check | S5CW -5CWF3-MTRD | * **************Incident Description************** * Notification 000030809455 Details * *********************************************************** * 04/15/2019 14:13:19 INCIDENT REPORT (INCIDENT REPORT) * Report submitted by: Richard Young ENTITY\INCIDENT: * * CONDITION DESCRIPTION/LOCATION (THE INAPPROPRIATE ACTION AND ITS NEGATIVE EFFECT/INCLUDE A DETAILED LOCATION DESCRIPTION): * During the routine daily check conducted at 1413 hours, F3B pump did not start per operation procedures. All Control system indicators were showing normal status but the pump motor did not start. * * ACTIVITIES, PROCESSES, PROCEDURES INVOLVED: * S5.OP.AB.WP-0004, Daily routine check * WHY DID CONDITION HAPPEN? * Unknown at this point. A failure in the motor start system or mechanical defects could possibly be the reason. * * CONSEQUENCES: * Inefficiency in operations and potential disruption in the workflow. * * REQUIREMENTS IMPACTED: * Normal running of the pump. * * ADVERSE PHYSICAL CONDITIONS: * No apparent physical condition was detected. * * WHO WAS NOTIFIED: * Maintenance Supervisor, Control Room Operator * * KNOWLEDGEABLE INDIVIDUALS: * Richard Young, John Simons * * REPEAT OR SIMILAR CONDITION: * No, this is the first time such an event has occurred. * * IMMEDIATE ACTIONS AND RECOMMENDED ACTIONS: * Required immediate Maintenance intervention. Recommended Actions include detailed check of the pump motor and control circuitry after secure isolation. * 04/15/2019 17:30:12 RICHARD YOUNG (INCIDENT) * Maintenance completed. The issue was due to a faulty relay in the motor start circuit. The relay was replaced and the pump function was tested. Everything is back to normal. | What was the cause of the F3B pump failing to start according to the incident report? | The issue was due to a faulty relay in the motor start circuit.
385 | 2021-04-05 | 30798054 | 80213527 | Overheating of Compressor M34 | S1CV -1CVE4 | * ******************Incident Description******************** * Notification 000030798054 Details * *********************************************************** * 04/05/2021 17:30:24 INCIDENT REPORT (INCIDENT REPORT) * Report submitted by: Derek Sanchez ENTITY\INCIDENT: * * 1) CONDITION DESCRIPTION/LOCATION (THE INAPPROPRIATE ACTION AND ITS NEGATIVE EFFECT/INCLUDE A DETAILED LOCATION DESCRIPTION): * On 04/05/21 during routine inspection, Compressor M34 was discovered to be overheating. Immediate shut down and cooling procedures were implemented. The temperature of M34 Compressor was found to be significantly higher compared to other similar units. A loud grinding noise was also detected. * * 2) ACTIVITIES, PROCESSES, PROCEDURES INVOLVED: * S1.OP.AB-CV- 0002, S1.OP-SO.CV-0003 * * 3) WHY DID CONDITION HAPPEN? * Preliminary findings suggest lubrication failure, although more investigation is required. * * 4) CONSEQUENCES: * Possible compressor damage, decreased productivity, possible safety hazards. * * 5) REQUIREMENTS IMPACTED: * Work stoppage due to unsafe conditions, potential quality control issues. * * 6) ADVERSE PHYSICAL CONDITIONS: * Overheated compressor, possible internal damage * * 7) WHO WAS NOTIFIED: * Supervisor, Maintenance Team * * 8) KNOWLEDGEABLE INDIVIDUALS: * Thompson, Roberts, Sanchez * * 9) REPEAT OR SIMILAR CONDITION: * No previous similar conditions recorded. * * 10) IMMEDIATE AND RECOMMENDED ACTIONS: * Complete shutdown of M34 Compressor, detailed investigation required. Recommend planned review of other compressors on site. * * Updated: DEREK SANCHEZ 04.05.2021 17:45:19 * ------------------------------------------------------------ * 04/10/2021 12:46:55 JANE DOE (NUSER) * Maintenance review determined that a lube oil pump failure led to the overheating of | What was the cause of the overheating in Compressor M34? | Maintenance review determined that a lube oil pump failure led to the overheating.
386 | 2019-03-15 | 30745123 | 80218745 | Overload on 18C Motor | S3CW -3CWE5 | * **************Incident Description************** * Notification 000030745123 Details * *********************************************************** * 03/15/2019 11:32:00 INCIDENT REPORT (INCIDENT REPORT) * Report submitted by: Kylie Baker ENTITY\INCIDENT: * * CONDITION DESCRIPTION/LOCATION (THE INAPPROPRIATE ACTION AND ITS NEGATIVE EFFECT/INCLUDE A DETAILED LOCATION DESCRIPTION): * Routine inspection data indicated that the 18C Motor has been operating under overload conditions for past 24 hours. The operating current was 30% over the nominal rating, placing the motor and connected equipments at risk. The motor 18C is located at unit 3 cooling water pump station. * * ACTIVITIES, PROCESSES, PROCEDURES INVOLVED: * S3.OP.AB-PV-0004, routine inspection and monitoring of operating metrics. * * WHY DID CONDITION HAPPEN? * Preliminary observation suggests possible failure of protection relay settings adjustment, actual cause to be identified. * * CONSEQUENCES: * Severe wear of the Motor, overheating, potential risk of malfunction or equipment failure which could disrupt normal service. * * REQUIREMENTS IMPACTED: * Continuous Operation * * ADVERSE PHYSICAL CONDITIONS: * Overloaded Motor, high-temperature operating conditions * * WHO WAS NOTIFIED: * Maintenance Supervisor, Plant Manager * * KNOWLEDGEABLE INDIVIDUALS: * Maintenance Team, Electrical Engineers * * REPEAT OR SIMILAR CONDITION: * No, first occurrence noted * * IMMEDIATE ACTIONS AND RECOMMENDED ACTIONS: * Immediate shut down of 18C Motor, conduct an inspection on the protection relay settings and electrical testing to verify any internal damage. * 03/17/2019 10:30:11 JOHN DOE (INCIDENT) * The investigation showed that the protection relay was found to be inappropriately calibrated leading to overload situation. The relay is now correctly set, checked the Motor which seems to be functioning normally. Further monitoring for a day would be carried out to observe after-effects, if any. | What immediate actions were taken after identifying the overload conditions of the 18C Motor? | Immediate shut down of 18C Motor, conduct an inspection on the protection relay settings and electrical testing to verify any internal damage.
387 | 2018-12-27 | 30765239 | 80245833 | Unexpected power drop in Turbine 13Z | S4TR -4TUE3 | * **************Incident Description************** * Notification 000030765239 Details * *********************************************************** * 12/27/2018 18:01:00 INCIDENT REPORT (INCIDENT REPORT) * Report submitted by: Richard Stone ENTITY\INCIDENT: * * CONDITION DESCRIPTION/LOCATION (THE INAPPROPRIATE ACTION AND ITS NEGATIVE EFFECT/INCLUDE A DETAILED LOCATION DESCRIPTION): * At 1720 hours, an unexpected drop in power output from Turbine 13Z was observed. The power output had decreased to 80% from its usual level. The turbine was operating under normal parameters before this event. Log reports and system diagnostics suggest a possible issue with the steam input valve. * * ACTIVITIES, PROCESSES, PROCEDURES INVOLVED: * Normal operation of Turbine 13Z under operation model S4.OP-SO.TR-0003. * * WHY DID CONDITION HAPPEN? * Possible mechanical issue with the steam input valve. Further inspection required. * * CONSEQUENCES: * Dependability of Turbine 13Z compromised, resulting in decreased power output. * * REQUIREMENTS IMPACTED: * Power generation, efficiency, normal operation of Turbine 13Z. * * ADVERSE PHYSICAL CONDITIONS: * Lower power output from Turbine 13Z. * * WHO WAS NOTIFIED: * Supervision, Engineers, Technical team. * * KNOWLEDGEABLE INDIVIDUALS: * Technical team, Richard Stone. * * REPEAT OR SIMILAR CONDITION: * No, this is a unique incident. * * IMMEDIATE ACTIONS AND RECOMMENDED ACTIONS: * Turbine shut off for emergency inspection and correction of the steam input valve issue. If necessary, replacement process underway. * 12/30/2018 09:17:13 WILLIAM SMITH (INCIDENT) * Turbine 13Z has been inspected and the steam input valve was found to be faulty. The valve has been replaced and Turbine 13Z is now functioning at its full capacity. | What was the immediate action taken when the drop in power output from Turbine 13Z was observed? | Turbine shut off for emergency inspection and correction of the steam input valve issue. If necessary, replacement process underway.
388 | 2022-01-01 | 30892050 | 80208304 | Abnormal vibration in 10C Pump Motor | S4CW -4CWE8 | * **************Incident Description************** * Notification 000030892050 Details * *********************************************************** *01/01/2022 07:23:12 INCIDENT REPORT (INCIDENT REPORT) * Report submitted by: Mark Wilson PHONE: 234-567-8901 ENTITY\INCIDENT: * * CONDITION DESCRIPTION/LOCATION (THE INAPPROPRIATE ACTION AND ITS NEGATIVE EFFECT/INCLUDE A DETAILED LOCATION DESCRIPTION): * During a scheduled round, operator reported abnormal vibration in the 10C Pump Motor. This issue has not been reported before. Further close examination noticed misalignment and possibly a worn-out bearing. * * ACTIVITIES, PROCESSES, PROCEDURES INVOLVED: * Routine inspection, S4.OP.MT.CW-0003. * * WHY DID CONDITION HAPPEN? * Suspected to be from wearing out of components after long period of use. * * CONSEQUENCES: * Possible failure of the motor, if not addressed promptly. This could affect efficiency and overall operational performance. * * REQUIREMENTS IMPACTED: * Normal operation and reliability. * * ADVERSE PHYSICAL CONDITIONS: * Excessive vibrations observed in the motor. * * WHO WAS NOTIFIED: * Maintenance Supervisor, Safety Team * * KNOWLEDGEABLE INDIVIDUALS: * Maintenance Supervisor, Senior Operator * * REPEAT OR SIMILAR CONDITION: * No, this is the first time such an issue has been reported with this unit. * * IMMEDIATE ACTIONS AND RECOMMENDED ACTIONS: * A thorough investigation by the maintenance team is recommended along with immediate shutdown of the unit until the cause of vibration is identified and mitigated. * 01/02/2022 15:45:48 MARK WILSON (INCIDENT) * Further investigation revealed excessive wear on the bearing. The part has been replaced and realignment has been performed. The unit is scheduled for a test run before resuming normal operation. | What were the immediate and recommended actions following the detection of abnormal vibration in the pump motor? | A thorough investigation by the maintenance team is recommended along with immediate shutdown of the unit until the cause of vibration is identified and mitigated.
389 | 2019-09-25 | 30871936 | 80262840 | Unexpected leak in 17B Pump | S3CW -3CWE5 | * **************Incident Description************** * Notification 000030871936 Details * *********************************************************** * 09/25/2019 10:24:12 INCIDENT REPORT (INCIDENT REPORT) * Report submitted by: Daniel Thompson ENTITY\INCIDENT: * * CONDITION DESCRIPTION/LOCATION (THE INAPPROPRIATE ACTION AND ITS NEGATIVE EFFECT/INCLUDE A DETAILED LOCATION DESCRIPTION): * During a routine site inspection, it was noticed that there was an unexpected leak in the 17B Pump. The leakage was significant enough to activate the alarm system. Immediate shut-down of the pump was initiated as a safety measure to avoid any potential disaster. * * ACTIVITIES, PROCESSES, PROCEDURES INVOLVED: * S3.OP.AB-CW-0018, S3.OP.BO.CW-0002 * * WHY DID CONDITION HAPPEN: * Preliminary investigation suggests corrosion or mechanical wear might be the cause. A detailed inspection is required to confirm. * * CONSEQUENCES: * If left unattended, this can lead to serious damage to the pump, potential flooding in the area and disruption of regular activities. * * REQUIREMENTS IMPACTED: * The pump is currently unavailable which can impact regular operation. * * ADVERSE PHYSICAL CONDITIONS: * Significant leakage in 17B pump * * WHO WAS NOTIFIED: * Supervisor, Safety Team * * KNOWLEDGEABLE INDIVIDUALS: * Daniel Thompson, Tina White, Mark Sanders * * REPEAT OR SIMILAR CONDITION: * No, not for this pump. * * IMMEDIATE ACTIONS AND RECOMMENDED ACTIONS: * A detail inspection is underway to identify the source of leakage and recommend actions for repair. Meanwhile, backup pump is operational to ensure service continuity. * 09/27/2019 14:15:14 DANIEL THOMPSON (INCIDENT) * A detailed analysis revealed that the leakage was because of a faulty gasket. Replaced the gasket and the pump is now in normal operating condition. | What was the initial action taken when the leakage in the 17B Pump was detected? | Immediate shut-down of the pump was initiated as a safety measure to avoid any potential disaster.
390 | 2020-09-10 | 30879202 | 80245893 | 25B pump vibrational issues | S4CW -4CWE7 | * **************Incident Description************** * Notification 000030879202 Details * *********************************************************** * 09/10/2020 10:15:17 INCIDENT REPORT (INCIDENT REPORT) * Report submitted by: Daniel Clark ENTITY\INCIDENT: * * CONDITION DESCRIPTION/LOCATION (THE INAPPROPRIATE ACTION AND ITS NEGATIVE EFFECT/INCLUDE A DETAILED LOCATION DESCRIPTION): * In routine maintenance inspection, 25B Pump was noticed to be exhibiting unusual vibrations. Vibrations were measured and found to be 1.6 times the normal amplitude. This abnormal behavior can potentially lead to long-term damage to the pump and hence, was immediately reported to the control room. * * ACTIVITIES, PROCESSES, PROCEDURES INVOLVED: * S4.OP-VB.PM-0002, Vibration Monitoring and Analysis. * * WHY DID CONDITION HAPPEN? * Unknown, could be due to excessive wear and tear or improper alignment. * * CONSEQUENCES: * If left unchecked, the irregular vibrational pattern can cause significant damage to the pump structure and internals, and further lead to operational inefficiency. * * REQUIREMENTS IMPACTED: * Equipment stability and operational efficiency. * * ADVERSE PHYSICAL CONDITIONS: * Unusual pump vibrations included indication of potential structural damage. * * WHO WAS NOTIFIED: * Control Room, Maintenance Manager. * * KNOWLEDGEABLE INDIVIDUALS: * Peterson, Andrew, Evans. * * REPEAT OR SIMILAR CONDITION: * No, first incident of this nature. * * IMMEDIATE ACTIONS AND RECOMMENDED ACTIONS: * Immediate pump isolation and detailed inspection is required, including checking alignment and wear of internal components. * 09/16/2020 11:47:08 DANIEL CLARK (INCIDENT) * The inspection revealed misalignment of the internal rotor. The component has been realigned and vibration levels are back to normal. The pump is safely returned to operation. | What immediate actions were recommended after noticing the unusual vibrations in the pump? | Immediate pump isolation and detailed inspection is required, including checking alignment and wear of internal components.
391 | 2019-09-01 | 30902524 | 90135792 | Overheating of 18B Pump Motor | S4CW- 4CWE4-PMP18B | * **************Incident Description************** * Notification 000030902524 Details * *********************************************************** * SUMMARY: CHECK THE CURRENT CONDITIONS AGAINST * ****PS-AA-180 "OPERATIONAL ID ANALYSIS AND PROCESSING***** * * 1) CONDITION DESCRIPTION/LOCATION (THE INAPPROPRIATE ACTION AND ITS NEGATIVE EFFECT/INCLUDE A DETAILED LOCATION DESCRIPTION): * At 1405 on 9/1/19, the technician reported overheating of the 18B Pump motor. Due to a rising temperature alert, the 18B Pump was immediately shut down from Unit 4 Control Room, the temperature receded shortly. Fire and Safety unit inspection revealed no signs of fire hazard but a strong smell of overheated metal was present. Pump motor temperature significantly deviated from other active pumps, no apparent external damage was observed. S4.OP-AB.CW-0002 process was triggered in light of the emergency shutdown of the 18B Pump. * * 2) ACTIVITIES, PROCESSES, PROCEDURES INVOLVED: * S4.OP-AB.CW-0002, S4.OP-SO.CW-0018 * * 3) WHY DID CONDITION HAPPEN: * Uncertain, previously similar events has been observed with pump motors. * * 4) CONSEQUENCES: * No immediate fallout, though the possibility of internal motor damage could affect efficiency once the unit is reactivated. * * 5) REQUIREMENTS IMPACTED: * Offline pump * * 6) ADVERSE PHYSICAL CONDITIONS: * Overheating of 18B Pump motor, potential internal damage * * 7) WHO WAS NOTIFIED: * Control Room, Fire and Safety Unit * * 8) KNOWLEDGEABLE INDIVIDUALS: * Thompson, Gomez, Patel * * 9) REPEAT OR SIMILAR CONDITION: * Uncertain * * 10) IMMEDIATE AND RECOMMENDED ACTIONS: * Maintenance to thoroughly inspect the 18B Pump Motor * * Updated: JOHN SMITH | What immediate action was recommended following the overheating of the 18B Pump motor? | Maintenance to thoroughly inspect the 18B Pump Motor
392 | 2022-01-28 | 40010530 | 90312104 | Unusual Vibration in Pump 30C | S4CW -4CWE8 | * **************Incident Description************** * Notification 000040010530 Details * *********************************************************** * 01/28/2022 15:26:32 INCIDENT REPORT (INCIDENT REPORT) * Report submitted by: William Day ENTITY\INCIDENT: * * CONDITION DESCRIPTION/LOCATION: * On 01/25/22, during a routine check, an unusual vibration was detected on Pump 30C. A thorough vibration analysis was carried out, which showed increased amplitude and an abnormal pattern. Given the sensitivity of the pump, it was decided to shut it down temporarily for a more detailed examination. * * ACTIVITIES, PROCESSES, PROCEDURES INVOLVED: * Vibration analysis, visual inspection, S4.OP-SO.CW-0002. * * WHY DID CONDITION HAPPEN? * Unknown. Preliminary inspection suggests possible misalignment or looseness of the pump shaft. * * CONSEQUENCES: * Prolonged operation under these conditions may lead to severe damage of the pump and resulting downstream effects. * * REQUIREMENTS IMPACTED: * Planned routine operation, possible impact on efficiency. * * ADVERSE PHYSICAL CONDITIONS: * Unusual vibration on Pump 30C. * * WHO WAS NOTIFIED: * Control Room, Maintenance Department * * KNOWLEDGEABLE INDIVIDUALS: * Jane Doe, William Day, Oliver Smith * * REPEAT OR SIMILAR CONDITION: * No, this is the first instance of this condition for Pump 30C. * * IMMEDIATE ACTIONS AND RECOMMENDED ACTIONS: * Pump was shut down for a detailed inspection. Will coordinate with the maintenance team for corrective measures. If necessary, replacement parts will be procured. * 01/29/2022 06:45:00 William Day (INCIDENT) * Inspection revealed misalignment in the pump shaft. We are working with the maintenance team to correct the issue. | Why was Pump 30C shut down temporarily? | An unusual vibration was detected on Pump 30C. A thorough vibration analysis was carried out, which showed increased amplitude and an abnormal pattern. Given the sensitivity of the pump, it was decided to shut it down temporarily for a more detailed examination.
393 | 2019-12-03 | 30989215 | 80235849 | Power failure at Circuit Station C4 | SE4C -4EWC1 | * **************Incident Description************** * Notification 000030989215 Details * *********************************************************** * 12/03/2019 16:15:38 INCIDENT REPORT (INCIDENT REPORT) * Report submitted by: Sam Winter ENTITY\INCIDENT: * * CONDITION DESCRIPTION/LOCATION (THE INAPPROPRIATE ACTION AND ITS NEGATIVE EFFECT/INCLUDE A DETAILED LOCATION DESCRIPTION): * At 1615, Circuit Station C4 experienced a sudden loss of power. The automated system indicated a surge in the power, followed by a total failure. The control room team triggered the emergency power backup system, which prevented further operations disruption. An inspection revealed a burnt fuse in the feeder circuit. Without the instant actions taken by the control room, a total blackout could have taken place, severely compromising all operations. * * ACTIVITIES, PROCESSES, PROCEDURES INVOLVED: * SE4.OP.AB-CW-0001, SE4.OP-SO.CW-0001 * * WHY DID CONDITION HAPPEN? * Preliminary investigation suggests a power surge was the cause. An in-depth investigation is necessary to identify definitive reasons. * * CONSEQUENCES: * Interruption to normal operations, compromised safety measures, impending repair costs and potential equipment damage. * * REQUIREMENTS IMPACTED: * All electrical dependent operations in the plant. * * ADVERSE PHYSICAL CONDITIONS: * Circuit Station C4 burned fuse. * * WHO WAS NOTIFIED: * All affected departments, including Control Room, Operations, Maintenance, and Safety. * * KNOWLEDGEABLE INDIVIDUALS: * Electronics Engineers, Smith & Lee. Control Room officials. * * REPEAT OR SIMILAR CONDITION: * No. First such incident at Circuit Station C4. * * IMMEDIATE ACTIONS AND RECOMMENDED ACTIONS: * Fuse replacement, Inspection of all circuit stations for similar conditions. Update maintenance protocol for more frequent checks on all circuit stations. * * Updated: SAM WINTER 12.03.2019 18:20:15 * ------------------------------------------------------------ * 12/10/2019 15:40:55 JANE SMITH ( | What caused the power failure at Circuit Station C4? | Preliminary investigation suggests a power surge was the cause.
394 | 2020-10-14 | 30954213 | 90128390 | Unusual vibrations in 30B Pump motor | S4CW -4CWE2 | * **************Incident Description************** * Notification 000030954213 Details * *********************************************************** * 10/14/2020 14:17:13 INCIDENT REPORT (INCIDENT REPORT) * Report submitted by: William Thompson ENTITY\INCIDENT: * * CONDITION DESCRIPTION/LOCATION (THE INAPPROPRIATE ACTION AND ITS NEGATIVE EFFECT/INCLUDE A DETAILED LOCATION DESCRIPTION): * At 1315 on 10/14/20, the operator reported unusual vibrations detected on the 30B Pump motor. Pump operation was ceased promptly, and a subsequent assessment by the maintenance team identified the presence of unusually worn-out motor bearings. This could be a probable reason for the vibrations. S4.OP.AB.CW-0003 Bearing Replacement was initiated. * * ACTIVITIES, PROCESSES, PROCEDURES INVOLVED: * S4.OP.AB.CW-0003, S4.OP-SO.CW-0003 * * WHY DID CONDITION HAPPEN? * The most probable reason is the extensive wear of pump motor bearings. * * CONSEQUENCES: * Operational downtime, potential failure of the pump unit. * * REQUIREMENTS IMPACTED: * Pump availability * * ADVERSE PHYSICAL CONDITIONS: * Unusual vibrations indicating probable internal damage. * * WHO WAS NOTIFIED: * Maintenance team, Control Room * * KNOWLEDGEABLE INDIVIDUALS: * Plummer, Davis, Johnson * * REPEAT OR SIMILAR CONDITION: * Not prior to this incident * * IMMEDIATE ACTIONS AND RECOMMENDED ACTIONS: * Bearings need to be replaced immediately before resuming pump operation. * * Updated: WILLIAM THOMPSON 10.14.2020 17:30:29 * ------------------------------------------------------------ * 10/16/2020 12:45:22 JANE DOE (NUSER) * The bearings have been replaced and the motor is currently under testing. The testing feedback will decide the course of next actions for the pump. | What was the initial issue with the 30B Pump motor and what action was taken? | At 1315 on 10/14/20, the operator reported unusual vibrations detected on the 30B Pump motor. Pump operation was ceased promptly, and a subsequent assessment by the maintenance team identified the presence of unusually worn-out motor bearings. S4.OP.AB.CW-0003 Bearing Replacement was initiated.
395 | 2017-11-15 | 30982923 | 80453224 | Pump K3 malfunctioning | G5BG -5BGE7-PMPK | * **************Incident Description************** * Notification 000030982923 Details * *********************************************************** * 11/15/2017 11:33:01 INCIDENT REPORT (INCIDENT REPORT) * Report submitted by: David Blackburn ENTITY\INCIDENT: * * 1) CONDITION DESCRIPTION/LOCATION (THE INAPPROPRIATE ACTION AND ITS NEGATIVE EFFECT/INCLUDE A DETAILED LOCATION DESCRIPTION): * During a routine system check, it was observed that Pump K3 was malfunctioning. The pump showed a voltage drop and was not maintaining the required pressure level, which led to reduced efficiency in the system. * * 2) ACTIVITIES, PROCESSES, PROCEDURES INVOLVED: * Routine system check, Operational Procedure Ref: G5.OP-AB.PM-0023. * * 3) WHY DID CONDITION HAPPEN: * The reason for malfunction is at present unknown and needs to be diagnosed. It might be due to a component failure or electrical issue. * * 4) CONSEQUENCES: * The malfunctioning of Pump K3 will impact the efficiency and operation of the overall system, leading to potential downtime. * * 5) REQUIREMENTS IMPACTED: * Normal operation and system efficiency * * 6) ADVERSE PHYSICAL CONDITIONS: * Drop in pump voltage and pressure * * 7) WHO WAS NOTIFIED: * Maintenance Supervisor, Operations Team * * 8) KNOWLEDGEABLE INDIVIDUALS: * Maintenance Team, Electrical Engineers * * 9) REPEAT OR SIMILAR CONDITION: * No previous instances reported * * 10) IMMEDIATE ACTIONS AND RECOMMENDED ACTIONS: * The Maintenance team should immediately investigate the cause of malfunctioning and rectify the problem. If required, the pump needs to be replaced or serviced. * 11/15/2017 14:52:52 DAVID BLACKBURN (INCIDENT) * Specified that the pump should be taken out of service for testing and possible replacement. To minimize downtime, a reserve unit should be prepared for immediate installation. | What immediate steps were recommended after the malfunctioning of Pump K3? | The Maintenance team should immediately investigate the cause of malfunctioning and rectify the problem. If required, the pump needs to be replaced or serviced.
396 | 2019-04-12 | 30831645 | 80215543 | Vibration in 33C Pump | S1CW -1CWE5 | * **************Incident Description************** * Notification 000030831645 Details * *********************************************************** * 04/12/2019 14:20:51 INCIDENT REPORT (INCIDENT REPORT) * Report submitted by: Mark Green ENTITY\INCIDENT: * * CONDITION DESCRIPTION/LOCATION (THE INAPPROPRIATE ACTION AND ITS NEGATIVE EFFECT/INCLUDE A DETAILED LOCATION DESCRIPTION): * During the afternoon shift, the operator reported abnormal vibration on 33C Pump. The pump was shut down immediately to prevent damage to the equipment. Vibration Analysis Team was called in and identified an alignment issue with the pump rotor. Prior to shutdown, the pump was operating with inlet pressure - 18 psig, and current - 275. * * ACTIVITIES, PROCESSES, PROCEDURES INVOLVED: * Shutdown Procedure S1.OP-AB.CW-0002 and Vibration Analysis S1.VA.CW.0001. * * WHY DID CONDITION HAPPEN? * Preliminary assessment suggests improper alignment during last maintenance activity. * * CONSEQUENCES: * Forced shutdown of 33C pump, potential for motor and rotor damage if unnoticed. * * REQUIREMENTS IMPACTED: * Operational availability of 33C pump. * * ADVERSE PHYSICAL CONDITIONS: * High vibration levels at pump. * * WHO WAS NOTIFIED: * Operations Supervisor, Maintenance Team * * KNOWLEDGEABLE INDIVIDUALS: * Mark Green, Allison Taylor, Bob Johnson * * REPEAT OR SIMILAR CONDITION: * No, first occurrence on the 33C pump. * * IMMEDIATE ACTIONS AND RECOMMENDED ACTIONS: * Technical team to check alignment and fix. Review maintenance procedures for alignment checks. * 04/13/2019 10:23:11 ALISON TAYLOR (INCIDENT) * Alignment on the 33C pump was corrected. The pump was restarted and is operating normally. S1.VA.OP-0001 maintenance procedure will be updated to include more stringent checks for alignment. | What was the immediate action taken after noticing the abnormality in the 33C pump? | The pump was shut down immediately to prevent damage to the equipment. Vibration Analysis Team was called in and identified an alignment issue with the pump rotor.
397 | 2016-12-30 | 30892305 | 80236721 | LV07 Generator Shaft Vibration Detected | S4GN -4GNE7-GEN | * **************Incident Description************** * Notification 000030892305 Details * *********************************************************** * 12/30/2016 14:58:42 INCIDENT REPORT (INCIDENT REPORT) * Report submitted by: Eric Williams ENTITY\INCIDENT: * CONDITION DESCRIPTION/LOCATION (THE INAPPROPRIATE ACTION AND ITS NEGATIVE EFFECT/INCLUDE A DETAILED LOCATION DESCRIPTION): * Vibration alarm for the LV07 generator was activated during a routine inspection. The alarmed vibration value was 2.3 Richter, which is 8.6% above the threshold. LV07 Generator was shut down to avoid potential damage. * * ACTIVITIES, PROCESSES, PROCEDURES INVOLVED: * Routine generator check * * WHY DID CONDITION HAPPEN? * Unknown, potential issues could involve shaft alignment, worn out bearings or generator phase imbalance. * * CONSEQUENCES: * Unscheduled generator shutdown, potential generator damage * * REQUIREMENTS IMPACTED: * Availability of LV07 generator * * ADVERSE PHYSICAL CONDITIONS: * Increased vibration on LV07 generator shaft * * WHO WAS NOTIFIED: * Incident Response Team, Maintenance Supervisor * * KNOWLEDGEABLE INDIVIDUALS: * Incident Response Team, Maintenance Team * * REPEAT OR SIMILAR CONDITION: * Not at this time * * IMMEDIATE ACTIONS AND RECOMMENDED ACTIONS: * Maintenance team to investigate the cause of the vibration, repairs or replacements may be necessary depending on the results. * * 31/12/2016 09:00:29 ERIC WILLIAMS (INCIDENT) * An investigation found a misaligned shaft was causing the vibration. The generator shaft has been realigned and vibration levels have returned to normal parameters. LV07 generator has been put back into service. | What immediate actions were taken after the LV07 generator vibration alarm was activated? | Maintenance team to investigate the cause of the vibration, repairs or replacements may be necessary depending on the results.
398 | 2020-07-15 | 30789545 | 90256793 | S4 Oil Spill Boiler Room | S4RM -4RMB4-OLPP | * **************Incident Description************** * Notification 000030789545 Details * *********************************************************** * 07/15/2020 13:42:36 INCIDENT REPORT (INCIDENT REPORT) * Report submitted by: Emma White ENTITY\INCIDENT: * * CONDITION DESCRIPTION/LOCATION (THE INAPPROPRIATE ACTION AND ITS NEGATIVE EFFECT/INCLUDE A DETAILED LOCATION DESCRIPTION): * Spotted an oil leak in the boiler room during maintenance round. The oil spill from the sump drain line caused slip hazards, potential work delay. Immediate shutdown initiated for clean-up and spill prevention. * * ACTIVITIES, PROCESSES, PROCEDURES INVOLVED: * S4.OP-AB.RM-0002, S4.OP-SO.RM-0003 * * WHY DID CONDITION HAPPEN? * Unknown, but might be due to pipe erosion or loosened joints * * CONSEQUENCES: * Increased safety hazards, potential equipment damages, possible environmental issue * * REQUIREMENTS IMPACTED: * Normal operations, safety regulations * * ADVERSE PHYSICAL CONDITIONS: * Oil Spill in plant area * * WHO WAS NOTIFIED: * Control Room, Safety Department, Environmental Agency * * KNOWLEDGEABLE INDIVIDUALS: * Emma White, John Doe, Maintenance Team * * REPEAT OR SIMILAR CONDITION: * No * * IMMEDIATE ACTIONS AND RECOMMENDED ACTIONS: * Immediately halted the operation for cleaning and mitigation. A thorough equipment inspection and leak detection should be performed ASAP. * 07/15/2020 19:18:57 JANE DOE (INCIDENT) * Clean-up was initiated, and leak was found on a line joining clamp which was tightened. Mitigation for future such spills includes frequent inspection, and using higher-grade materials for pipe and clamp. Maintenance process will be revised. | What immediate and recommended actions were taken following the detection of the oil leak in the boiler room? | Immediately halted the operation for cleaning and mitigation. A thorough equipment inspection and leak detection should be performed ASAP. Clean-up was initiated, and leak was found on a line joining clamp which was tightened. Mitigation for future such spills includes frequent inspection, and using higher-grade materials for pipe and clamp. Maintenance process will be revised.
399 | 2016-02-16 | 30831741 | 80361280 | Detecting leak in 5A Pump | S3CW -3CWE5 | * **************Incident Description************** * Notification 000030831741 Details * *********************************************************** * 02/16/2016 09:35:30 INCIDENT REPORT (INCIDENT REPORT) * Report submitted by: David Green ENTITY\INCIDENT: * * CONDITION DESCRIPTION/LOCATION (THE INAPPROPRIATE ACTION AND ITS NEGATIVE EFFECT/INCLUDE A DETAILED LOCATION DESCRIPTION): * During the daily operating procedure, the 5A Pump exhibited a small leak. The leak was noticed due to puddle forming near the pump. The leak condition was discovered during a routine inspection, no prior warning signs were evident. Proper procedures were followed to immediately halt the pumping activity and safety measures were put in place. * * ACTIVITIES, PROCESSES, PROCEDURES INVOLVED: * Regular Pumping * * WHY DID CONDITION HAPPEN? * Initial inspection suggests wear and tear, more detailed analysis to follow * * CONSEQUENCES: * Possible interruption in service, Potential for more extensive damage if not resolved * * REQUIREMENTS IMPACTED: * Service continuity, Equipment function * * ADVERSE PHYSICAL CONDITIONS: * Leak in 5A Pump * * WHO WAS NOTIFIED: * Supervisor, Technical Team * * KNOWLEDGEABLE INDIVIDUALS: * Technical Team, Supervisor * * REPEAT OR SIMILAR CONDITION: * Not to the best of my knowledge. * * IMMEDIATE ACTIONS AND RECOMMENDED ACTIONS: * Halted pump operations, Initiated safety measures, Scheduled technical team review * * 02/18/2016 12:05:34 DAVID GREEN (INCIDENT) * Post detailed inspection by the technical team, it was revealed that the leak was due to worn gaskets. Replacement of gaskets is being scheduled and operations will be resumed post successful testing. | What was the cause of the leak in the 5A Pump? | The leak was due to worn gaskets.
400 | 2017-08-27 | 40734591 | 90212576 | 32B Pump vibration abnormalities | S4CW -4CWE4-PTSD | * **************Incident Description************** * Notification 000040734591 Details * *********************************************************** * 08/27/2017 11:45:09 INCIDENT REPORT (INCIDENT REPORT) * Report submitted by: Thomas Williams ENTITY\INCIDENT: * * CONDITION DESCRIPTION/LOCATION (THE INAPPROPRIATE ACTION AND ITS NEGATIVE EFFECT/INCLUDE A DETAILED LOCATION DESCRIPTION): * During routine inspection, detected abnormal vibration of pump 32B. Though no immediate operational issues were detected, this has raised concerns about pump reliability. Its behavior was divergent from other pumps in operation. * * ACTIVITIES, PROCESSES, PROCEDURES INVOLVED: * Daily Pump inspection and operational records check * * WHY DID CONDITION HAPPEN? * Unknown, there could be potential issues with bearings or cavitation. * * CONSEQUENCES: * A potential pump failure which could disrupt normal operation. * * REQUIREMENTS IMPACTED: * Plant operation and safety measures * * ADVERSE PHYSICAL CONDITIONS: * High vibration at pump 32B without identifiable cause * * WHO WAS NOTIFIED: * Plant Supervisor, Maintenance Engineer, Shift Team * * KNOWLEDGEABLE INDIVIDUALS: * Maintenance Team, Plant Supervisor * * REPEAT OR SIMILAR CONDITION: * No, this is the first incident with 32B Pump. * * IMMEDIATE ACTIONS AND RECOMMENDED ACTIONS: * A thorough mechanical check, focusing on bearings and cavitation. Additional monitoring encouraged till the cause of vibration is identified. * 08/30/2017 14:45:23 THOMAS WILLIAMS (INCIDENT) * The Mechanical check detected few worn out bearings that were promptly replaced. The vibration has ceased post intervention. If vibration recurs, further analysis will be conducted. | What was the issue detected during the routine inspection of pump 32B and what actions were recommended? | During routine inspection, detected abnormal vibration of pump 32B. Though no immediate operational issues were detected, this has raised concerns about pump reliability. Its behavior was divergent from other pumps in operation. A thorough mechanical check, focusing on bearings and cavitation. Additional monitoring encouraged till the cause of vibration is identified.
401 | 2017-12-12 | 30900001 | 80236789 | Abnormal vibration detected in Pump 7A | S4CW -4CWE5 | * **************Incident Description************** * Notification 000030900001 Details * *********************************************************** * 12/12/2017 14:14:32 INCIDENT REPORT (INCIDENT REPORT) * Report submitted by: Richard Clark ENTITY\INCIDENT: * * 1) CONDITION DESCRIPTION/LOCATION (THE INAPPROPRIATE ACTION AND ITS NEGATIVE EFFECT/INCLUDE A DETAILED LOCATION DESCRIPTION): * During a routine shift, an abnormal vibration was detected from Pump 7A. The alert was forwarded to the Control Room, and personnel confirmed the abnormal vibration. The pump was instantly shut down to avoid further damage. A visual inspection did not reveal any external damage. * * 2) ACTIVITIES, PROCESSES, PROCEDURES INVOLVED: * Routine operational checks involved the detection of the abnormality. * * 3) WHY DID CONDITION HAPPEN? * The cause for the abnormal vibration is still unknown. It could possibly be due to a mechanical failure or debris in the pump cavities. * * 4) CONSEQUENCES: * If the pump isn't repaired, damage could possibly escalate further, possibly result in pump inefficiency or failure. * * 5) REQUIREMENTS IMPACTED: * Operations might be affected due to pump unavailability. * * 6) ADVERSE PHYSICAL CONDITIONS: * Abnormal operation of 7A Pump, Potential mechanical damage * * 7) WHO WAS NOTIFIED: * Supervisor, Control Room, Maintenance Team, Safety Department * * 8) KNOWLEDGEABLE INDIVIDUALS: * Clark, Barnes, Arnold, Hudson * * 9) REPEAT OR SIMILAR CONDITION: * This kind of issue has been noted on different pumps in the past, but this is the first instance involving Pump 7A. * * 10) IMMEDIATE ACTIONS AND RECOMMENDED ACTIONS: * Maintenance Team should perform an immediate detailed inspection of the 7A Pump and determine the reason for the abnormal vibrations. Concurrently, put the corresponding stand-by pump in service. * * 12/12/2017 22:48:33 RICHARD CLARK | What immediate actions were recommended after the detection of abnormal vibration in Pump 7A? | Maintenance Team should perform an immediate detailed inspection of the 7A Pump and determine the reason for the abnormal vibrations. Concurrently, put the corresponding stand-by pump in service.
402 | 2014-05-07 | 30630710 | 80122410 | Overheating of Pump 16B | S1CW-1CWE3-EQ | * **************Incident Description************** * Notification 000030630710 Details * *********************************************************** * 05/07/2014 08:21:16 INCIDENT REPORT (INCIDENT REPORT) * Report submitted by: Paul Williams 234-567-8901 * ENTITY\INCIDENT: * CONDITION DESCRIPTION/LOCATION (THE INAPPROPRIATE ACTION AND ITS NEGATIVE EFFECT/INCLUDE A DETAILED LOCATION DESCRIPTION): * At 0745 on 5/7/14 during routine inspection, the operator detected intense heat from pump 16B. Immediate shut down of the pump was commanded from Unit 1 Control Room leading to reduction of heat. There was no observed fire, however an unusual smell of burnt rubber was present. After an inspection, the pump motor temperatures fell within the tolerable limits of functioning pumps with no visible external damage. The safety operational procedure S1.OP-AB.CW-0002 for abnormal pump conditions was initiated due to immediate shut down of 16B Pump. * * ACTIVITIES, PROCESSES, PROCEDURES INVOLVED: * S1.OP-AB.CW-0002 and S1.OP-SO.CW-0002 * * WHY DID CONDITION HAPPEN? * Unknown, overheating of pump could be a possible explanation * * CONSEQUENCES: * Possible interruption in the efficiency of the unit when it resumes operation * * REQUIREMENTS IMPACTED: * Unavailability of 16B pump * * ADVERSE PHYSICAL CONDITIONS: * Overheating of 16B pump, potential internal degradation * * WHO WAS NOTIFIED: * Control Room, Maintenance Team * * KNOWLEDGEABLE INDIVIDUALS: * Johnson, Hanson, Smith * * REPEAT OR SIMILAR CONDITION: * Unknown * * IMMEDIATE ACTIONS AND RECOMMENDED ACTIONS: * The maintenance team to inspect 16B pump * * Updated: PAUL WILLIAMS 05.07.2014 09:14:20 * ------------------------------------------------------------ * 05/19/2014 08:43:51 LUCY KLARK (N | What actions were taken when there was an unusual heat detection from pump 16B? | Immediate shut down of the pump was commanded from Unit 1 Control Room leading to reduction of heat.
403 | 2018-09-26 | 30985237 | 80231541 | Overheat in Generator Motor 2C | S4CW -4CWE7-PMTD | * **************Incident Description************** * Notification 000030985237 Details * *********************************************************** * 09/26/2018 14:20:34 INCIDENT REPORT (INCIDENT REPORT) * Report submitted by: Sarah Bell 555-666-7777 * * CONDITION DESCRIPTION/LOCATION (THE INAPPROPRIATE ACTION AND ITS NEGATIVE EFFECT/INCLUDE A DETAILED LOCATION DESCRIPTION): * During a routine check at 1415 on 9/26/18, an abnormal overheat was detected in the Generator Motor 2C. The overheating prompted an emergency shutdown from Control Room 4, and the unit showed no signs of external damage. A distinct smell of burnt wires persisted post-shutdown, suggesting possible internal damage. * * ACTIVITIES, PROCESSES, PROCEDURES INVOLVED: * S4.OP-AB.CW-0002, S4.OP-SO.CW-0002 * * WHY DID CONDITION HAPPEN: * Unknown. Investigations are in progress. Previous incidents of overheating have occurred. * * CONSEQUENCES: * Possible internal damage could result in a decrease in operational efficiency or complete breakdown. * * REQUIREMENTS IMPACTED: * Generator Motor 2C currently offline * * ADVERSE PHYSICAL CONDITION: * Overheating of Generator Motor 2C * * WHO WAS NOTIFIED: * Control Room Supervisor, Maintenance Team * * KNOWLEDGEABLE INDIVIDUALS: * Miller, Davis, Bell * * REPEAT OR SIMILAR CONDITION: * Yes, though frequency and exact similar conditions are under investigation * * IMMEDIATE AND RECOMMENDED ACTIONS: * Maintenance and Engineering team to investigate Generator Motor 2C * * 09/26/2018 18:45:56 SARAH BELL (INCIDENT) * Initial inspection suggests no high-end damage. Further inspection needed to rule out any internal damage. Awaiting Engineering Team's insights. | What actions were recommended after the detection of the overheating in Generator Motor 2C? | Maintenance and Engineering team to investigate Generator Motor 2C
404 | 2018-12-09 | 31058556 | 90115993 | 10B Compressor showing low pressure | S4CW -4CWE5 | * **************Incident Description************** * Notification 000031058556 Details * *********************************************************** * 12/09/2018 08:47:35 INCIDENT REPORT (INCIDENT REPORT) * Report submitted by: Emily Taylor 987-654-3210 ENTITY\INCIDENT: * CONDITION DESCRIPTION/LOCATION (THE INAPPROPRIATE ACTION AND ITS NEGATIVE EFFECT/INCLUDE A DETAILED LOCATION DESCRIPTION): * At approximately 0830 on 12/9/18, the operator noted that 10B Compressor's pressure readings were significantly lower than normal. Initial checks of leakages yielded negative results. Abnormality procedure initiated under S4.OP-AB.CW-0002 due to the low pressure in 10B Compressor. * * ACTIVITIES, PROCESSES, PROCEDURES INVOLVED: * S4.OP.AB-CW-0002, S4.OP-SO.CW-0003 * * WHY DID CONDITION HAPPEN? * Unknown, this is the first time this compressor has shown low pressure. * * CONSEQUENCES: * Underperforming compressor can lead to system inefficiencies and potential safety hazards. * * REQUIREMENTS IMPACTED: * Normal compressor operation and resulting system performance * * ADVERSE PHYSICAL CONDITIONS: * Lower-than-normal pressure readings from 10B Compressor. * * WHO WAS NOTIFIED: * Supervisor, Maintenance Department * * KNOWLEDGEABLE INDIVIDUALS: * Hill, Peterson, Davis * * REPEAT OR SIMILAR CONDITION: * No * * IMMEDIATE ACTIONS AND RECOMMENDED ACTIONS: * Request Maintenance to investigate the cause of the low pressure in 10B Compressor. * 12/09/2018 12:52:10 EMILY TAYLOR (INCIDENT) * After initial checks, it appears the low pressure might be result of a faulty sensor. Maintenance team is scheduled to replace the pressure sensor on 10B Compressor. | What immediate action was recommended following the incident with the 10B Compressor? | Request Maintenance to investigate the cause of the low pressure in 10B Compressor.
405 | 2016-07-08 | 30785612 | 80205234 | 14D motor RPM fluctuation | S4CW -4CWE7-MTRD | * **************Incident Description************** * Notification 000030785612 Details * *********************************************************** * SUMMARY: TO ADDRESS RPM FLUCTUATIONS FOUND IN * ****S4.ME-CW-120 "MOTOR OPERATION AND DIAGNOSIS PROCESS"***** * * 1) Condition Description/Location (The inappropriate action and its negative effect/Include a detailed location description): * At 15:32 on 7/08/16, aberrant RPM fluctuation was noticed in the 14D Motor. A routine maintenance check had revealed the unexpected fluctuation in RPMs, potentially indicating internal issues. A visual inspection revealed no external signs of overheat or wear and tear. S4.ME-CW-120 Motor Operation Assessment was initiated due to these abnormal findings in 14D Motor. * * 2) ACTIVITIES, PROCESSES, PROCEDURES INVOLVED: * S4.ME-CW-120, S4.OP-ME.CW-0008 * * 3) WHY DID CONDITION HAPPEN: * Unknown, preliminary inspection showed no clear causes * * 4) CONSEQUENCES: * Potential internal motor damage which may cause breakdown or reduced efficiency * * 5) REQUIREMENTS IMPACTED: * Regular Motor operation * * 6) ADVERSE PHYSICAL CONDITION: * 14D Motor RPM fluctuation * * 7) WHO WAS NOTIFIED: * Operations Supervisor, Maintenance Team * * 8) KNOWLEDGEABLE INDIVIDUALS: * Williams, Miller, Taylor * * 9) REPEAT OR SIMILAR CONDITION: * No * * 10) IMMEDIATE AND RECOMMENDED ACTIONS: * Engineering assessment on 14D Motor along with performance tests * * Updated: JAMES DOE 07.08.2016 18:00:29 * ------------------------------------------------------------ * 07/15/2016 09:15:40 LISA STEVENSON (OPERATOR) * Engineering assessment identified a minor internal misalignment to be the source of the RPM fluctuation. The motor was realigned and | What was the observed irregularity in the 14D Motor operation? | At 15:32 on 7/08/16, aberrant RPM fluctuation was noticed in the 14D Motor. A routine maintenance check had revealed the unexpected fluctuation in RPMs, potentially indicating internal issues. A visual inspection revealed no external signs of overheat or wear and tear.
406 | 2020-09-23 | 308924850 | 85922341 | 13B Pump unusual vibration | S3CW -3CWE7 | * **************Incident Description************** * Notification 0000308924850 Details * *********************************************************** * 09/23/2020 14:47:22 INCIDENT REPORT (INCIDENT REPORT) * Report submitted by: Rachel Sanchez ENTITY\INCIDENT: * * CONDITION DESCRIPTION/LOCATION (THE INAPPROPRIATE ACTION AND ITS NEGATIVE EFFECT/INCLUDE A DETAILED LOCATION DESCRIPTION): * During a routine inspection, the operator noticed an unusual vibration from 13B Pump. The vibration was felt on touch and was higher than normal. There were no other abnormal indications. No heat or unusual noise. The pump was immediately shut down for further inspection. * * ACTIVITIES, PROCESSES, PROCEDURES INVOLVED: * S3.OP.AB-CW-0002, S3.OP-SO.CW-0002 * * WHY DID CONDITION HAPPEN? * The exact cause of the vibration is unknown. The pump was properly maintained and operating under normal conditions. Further inspection needed. * * CONSEQUENCES: * Unanticipated downtime, potential damage to pump mechanisms if continued to operate. * * REQUIREMENTS IMPACTED: * Availability of 13B pump for operation * * ADVERSE PHYSICAL CONDITIONS: * Unusual vibration from 13B pump motor * * WHO WAS NOTIFIED: * Supervisor, Maintenance team * * KNOWLEDGEABLE INDIVIDUALS: * Sanchez, Thompson, Patel * * REPEAT OR SIMILAR CONDITION: * No, this is the first incident for this pump * * IMMEDIATE ACTIONS AND RECOMMENDED ACTIONS: * The pump has been scheduled for maintenance. Further investigation of the pump will be carried out to determine the cause of the vibration. * 09/23/2020 16:57:05 RACHEL SANCHEZ (INCIDENT) * Upon further inspection, no significant wear or damage has been found on the pump. Will be continuing to monitor closely for any recurrence of the vibration. | What were the immediate actions taken after noticing the unusual vibration on the 13B Pump? | The pump was immediately shut down for further inspection. The pump has been scheduled for maintenance. Further investigation of the pump will be carried out to determine the cause of the vibration.
407 | 2021-02-25 | 31238456 | 81234567 | Overheating issue in 18B Pump motor | S2CW -3CWE7-MTRD | * **************Incident Description************** * Notification 000031238456 Details * *********************************************************** * SUMMARY: OBSERVE CURRENT PARAMETERS ACCORDING TO * ****PS-AA-345 "ISSUE IDENTIFICATION AND PUMP OPERATION PROCESS"***** * * 1) Condition Description/Location (The undesirable scenario and its negative impact/Include a detailed location description): * At 1243 on 2/25/21, Pump operator reported overheating issue in the 18B Pump motor. Immediate shutdown from Unit 3 Control Room was initiated and the overheating was controlled. Site inspection did not reveal any fire but a strong burnt odor was prevalent. Motor temperatures were unusually high compared to other pumps in operation and there were no external damage signs. S3.OP-AB.CW-0006 Pump overheating was initiated due to the immediate shutdown of the 18B Pump. * * 2) ACTIVITIES, PROCESSES, PROCEDURES INVOLVED: * S2.OP.AB-CW-0006, S2.OP-SO.CW-0004 * * 3) WHY DID CONDITION HAPPEN: * Undetermined, even though pump motor overheating issues have been recorded in the past. * * 4) CONSEQUENCES: * Immediate consequences are absent, but prospective motor damage could lead to efficiency loss when the unit resumes operation. * * 5) REQUIREMENTS IMPACTED: * Decommissioned pump * * 6) ADVERSE PHYSICAL CONDITION: * Overheating of 18B Pump motor, probable internal damage * * 7) WHO WAS NOTIFIED: * Control Room, Site Safety Team * * 8) KNOWLEDGEABLE INDIVIDUALS: * Williams, Chandler, Garcia * * 9) REPEAT OR SIMILAR CONDITION: * Undetermined * * 10) IMMEDIATE AND RECOMMENDED ACTIONS: * Maintenance to inspect 18B Pump Motor * * Updated: JAMES ROSS 02.25.2021 15:23:45 * ------------------------------------------------------------ * 03 | What action was taken when the overheating issue was reported in the 18B Pump motor? | Immediate shutdown from Unit 3 Control Room was initiated and the overheating was controlled.
408 | 2022-02-15 | 30975862 | 80235678 | Overloaded circuit at 13B control panel | S4CW -4CWE2 | * **************Incident Description************** * Notification 000030975862 Details * *********************************************************** * 02/15/2022 13:25:00 INCIDENT REPORT (INCIDENT REPORT) * Report submitted by: Patricia Green ENTITY\INCIDENT: * * CONDITION DESCRIPTION/LOCATION (THE INAPPROPRIATE ACTION AND ITS NEGATIVE EFFECT/INCLUDE A DETAILED LOCATION DESCRIPTION): * During routine monitoring, system overload was identified at 13B control panel. * The main circuit brakers had tripped cutting off power to vital systems. * Immediate reset did not work. Initial findings indicated an electro-thermal * event at the circuit board. * * ACTIVITIES, PROCESSES, PROCEDURES INVOLVED: * Routine system monitoring and troubleshooting procedure S4.OP-SO.CW-0001 * * WHY DID CONDITION HAPPEN? * Initial inspection suggests a possible short circuit or component failure. Could also be due to manufacturing defect or wear and tear. * * CONSEQUENCES: * Power outage to critical systems, could lead to complete shutdown if not attended to promptly. * * REQUIREMENTS IMPACTED: * Equipment reliability and overall system performance. * * ADVERSE PHYSICAL CONDITIONS: * Overheating of the circuit board and electrical components. * * WHO WAS NOTIFIED: * Control Room, Maintenance Department, Safety Officer * * KNOWLEDGEABLE INDIVIDUALS: * Gregory, Roberts, Sandra from Maintenance department * * REPEAT OR SIMILAR CONDITION: * No, this is the first occurrence of such an incident. * * IMMEDIATE ACTIONS AND RECOMMENDED ACTIONS: * Isolate the problem and mitigate risks. Maintenance to inspect and repair circuit board. * Review safety procedures and update if needed. * 02/20/2022 16:42:20 SAMANTHA GRAY (INCIDENT) * The detailed inspection of the 13B control panel has been concluded under work order 80235678. * Aged components were the cause of the circuit overload. These have been replaced * and future preventive measure will include regular thermal imaging to detect component degradation earlier. * The control panel is back | What was the initial cause of the system overload at the 13B control panel? | Initial inspection suggests a possible short circuit or component failure. Could also be due to manufacturing defect or wear and tear.
409 | 2020-10-10 | 30740211 | 80681332 | Unexpected Shutdown of 30B pump motor | S4CW -4CWE2 | * **************Incident Description************** * Notification 000030740211 Details * *********************************************************** * 10/10/2020 15:49:32 INCIDENT REPORT (INCIDENT REPORT) * Report submitted by: William Wilson 789-123-4560 ENTITY\INCIDENT: * CONDITION DESCRIPTION/LOCATION (THE INAPPROPRIATE ACTION AND ITS NEGATIVE EFFECT/INCLUDE A DETAILED LOCATION DESCRIPTION): * On 10/10/2020, during an operations monitoring shift, an unexpected auto-shutdown was triggered on 30B pump. The pump ceased operation abruptly without any initial sign of malfunction. No significant heat emission or irregular noise was noted. * * ACTIVITIES, PROCESSES, PROCEDURES INVOLVED: * Daily operations monitoring * * WHY DID CONDITION HAPPEN? * Initial investigation points towards a possible internal malfunction. Further technical investigation is needed. * * CONSEQUENCES: * Interruption of normal operations, possible internal damage to the pump. * * REQUIREMENTS IMPACTED: * Continuous operation of the pump. * * ADVERSE PHYSICAL CONDITIONS: * Unexpected shutdown of the 30B pump. * * WHO WAS NOTIFIED: * Supervisor, Operations Team * * KNOWLEDGEABLE INDIVIDUALS: * Maintenance Team * * REPEAT OR SIMILAR CONDITION: * No, this is the first instance. * * IMMEDIATE ACTIONS AND RECOMMENDED ACTIONS: * Triggers system reset, further functionality analysis and in-depth inspection is required. * 10/10/2020 17:32:45 WILLIAM WILSON (INCIDENT) * Further investigation revealed a software glitch triggered the auto-shutdown. The software is currently being analyzed for possible bugs. The pump was manually restarted post system reset and is functioning as expected. | What immediate actions were taken following the unexpected shutdown of the pump? | Triggers system reset, further functionality analysis and in-depth inspection is required.
410 | 2022-01-04 | 30980290 | 90234765 | Vibration Detected in 6B Pump Motor | S5CW -5CWE2 | * **************Incident Description************** * Notification 000030980290 Details * *********************************************************** * 01/04/2022 10:34:25 INCIDENT REPORT (INCIDENT REPORT) * Report submitted by: Robert Johnson, ENTITY\INCIDENT: * * CONDITION DESCRIPTION/LOCATION (THE INAPPROPRIATE ACTION AND ITS NEGATIVE EFFECT/INCLUDE A DETAILED LOCATION DESCRIPTION): * During a routine inspection at 0930 on 1/4/22, the operator noticed an unusual vibration from the 6B Pump Motor. The motor was immediately shut down for further inspection. Vibration monitoring revealed readings that are higher than normal. There was no significant smell of burnt insulation or other signs of overheating. The entire system is currently under investigation for potential internal damage. * * ACTIVITIES, PROCESSES, PROCEDURES INVOLVED: * S5.OP-AB.VB-0005, S5.OP-SO.VB-0005 * * WHY DID CONDITION HAPPEN: * The cause of the unusual vibration is still unknown at this time. * * CONSEQUENCES: * The immediate shutdown might affect the overall plant operations. If not addressed promptly, it could result in severe pump motor damage and costly replacements. * * REQUIREMENTS IMPACTED: * Pump operations * * ADVERSE PHYSICAL CONDITION: * Unusual vibration on the 6B Pump motor, potential internal damage. * * WHO WAS NOTIFIED: * Maintenance Supervisor, Incident Response Team * * KNOWLEDGEABLE INDIVIDUALS: * Thompson, Blake, Miller * * REPEAT OR SIMILAR CONDITION: * This situation seems to be a first of its kind. * * IMMEDIATE ACTIONS AND RECOMMENDED ACTIONS: * Immediate inspection and maintenance of the 6B Pump Motor should be undertaken. If vibration persists, a comprehensive * investigation to determine the cause, followed by corrective measures is recommended. * 01/07/2022 08:22:14 JONATHAN DOE (INCIDENT) * The motor has been dismantled, examined, and found a misalignment in the internal | What was the initial abnormal sign observed from the 6B Pump Motor? | During a routine inspection at 0930 on 1/4/22, the operator noticed an unusual vibration from the 6B Pump Motor.
411 | 2022-05-30 | 30845236 | 80236592 | High Vibration in Pump 17C | S4CW -4CWE7 | * **************Incident Description************** * Notification 000030845236 Details * *********************************************************** * 05/30/2022 18:41:00 INCIDENT REPORT (INCIDENT REPORT) * Report submitted by: Emily Davis 123-789-4560 ENTITY\INCIDENT: * * CONDITION DESCRIPTION/LOCATION (THE INAPPROPRIATE ACTION AND ITS NEGATIVE EFFECT/INCLUDE A DETAILED LOCATION DESCRIPTION): * During the daily routine maintenance, unsual high vibration was noticed on Pump 17C. The reading of vibration was around 1.8 in/s RMS. This is above the acceptable limit. No visible external damages were observed on the pump. According to SOP vibrations should not exceed 0.8 in/s RMS. * * ACTIVITIES, PROCESSES, PROCEDURES INVOLVED: * Daily routine maintenance and SOP-S4.OP-AB.CW-0001 * * WHY DID CONDITION HAPPEN? * The exact cause is unknown. Possible reasons could be imbalance, loose connections, bearing failure, or pump malfunction. * * CONSEQUENCES: * If vibration levels continue to exceed limits, it can lead to equipment failure. This could potentially halt the operations, leading to loss of efficiency and productivity. * * REQUIREMENTS IMPACTED: * Availability of pump for operation * * ADVERSE PHYSICAL CONDITIONS: * Abnormal vibrations in Pump 17C * * WHO WAS NOTIFIED: * Supervisory Team, Maintenance and operations teams. * * KNOWLEDGEABLE INDIVIDUALS: * Maintenance team, Pump Incharge * * REPEAT OR SIMILAR CONDITION: * No known repeat or similar condition. * * IMMEDIATE ACTIONS AND RECOMMENDED ACTIONS: * Inspection, and potentially maintenance for Pump 17C. * 05/31/2022 10:11:26 EMILY DAVIS (INCIDENT) * After thorough inspection, the imbalance was detected in the pump. Corrective action has been taken and the pump is restored to normal operation. Guidelines for early detection of such conditions has been suggested to avoid recurrence. | What immediate actions were recommended following the unusual high vibration on Pump 17C? | Inspection, and potentially maintenance for Pump 17C.
412 | 2019-03-16 | 30723105 | 80266687 | Overheating at 19B Pump during startup | S4CW -4CWE7 | * **************Incident Description************** * Notification 000030723105 Details * *********************************************************** * 03/16/2019 15:24:20 INCIDENT REPORT (INCIDENT REPORT) * Report submitted by: Samantha Jacobs ENTITY\INCIDENT: * * CONDITION DESCRIPTION/LOCATION (THE INAPPROPRIATE ACTION AND ITS NEGATIVE EFFECT/INCLUDE A DETAILED LOCATION DESCRIPTION): * 19B Pump motor observed to be overheating at start-up. This was not typically a behavior for this pump. The pump was shut down immediately with no serious consequences but could lead to significant equipment damage if repeated. * * ACTIVITIES, PROCESSES, PROCEDURES INVOLVED: * Regular startup procedures. * * WHY DID CONDITION HAPPEN? * Preliminary assessment suggests potential issues with the pump's cooling system. * * CONSEQUENCES: * Potential equipment damage and reduced operational efficiency. * * REQUIREMENTS IMPACTED: * Startup procedures, equipment health * * ADVERSE PHYSICAL CONDITIONS: * Overheat of the 19B pump motor * * WHO WAS NOTIFIED: * Control Room, Maintenance Supervisor * * KNOWLEDGEABLE INDIVIDUALS: * Operations Manager, Chief Maintenance Officer, Sr. Engineer * * REPEAT OR SIMILAR CONDITION: * No, this is a first time issue with this pump. * * IMMEDIATE ACTIONS AND RECOMMENDED ACTIONS: * The pump has been isolated and is no longer in use until an in-depth inspection can be performed. The recommendation for now is to inspect the cooling system and check for any abnormalities. * * Updated: SAMANTHA JACOBS 03.16.2019 19:40:32 * ------------------------------------------------------------ * 03/19/2019 15:30:33 TOM BROWN (MAINTENANCE) * The cooling system was inspected and a blocked cooling line was discovered. The blockage was removed and pump was tested successfully. The pump is now ready for operation. | What was the immediate action taken after the overheating of the 19B pump motor was observed? | The pump has been isolated and is no longer in use until an in-depth inspection can be performed.
413 | 2019-12-30 | 30825173 | 80236517 | Inconsistent pressure in valve 4B | S6PW -6PWE12 | * **************Incident Description************** * Notification 000030825173 Details * *********************************************************** * 12/30/2019 15:32:45 INCIDENT REPORT (INCIDENT REPORT) * Report submitted by: Kevin White 987-654-3210 ENTITY\INCIDENT: * CONDITION DESCRIPTION/LOCATION (THE INAPPROPRIATE ACTION AND ITS NEGATIVE EFFECT/INCLUDE A DETAILED LOCATION DESCRIPTION): * During the system audit check at 1330 hours, valve 4B showed inconsistent pressure. Preliminary tests were conducted and fluctuating readings between 20-30 psi were recorded. On a normal workday, the valve PSI readings are consistent across all measurement intervals. * * ACTIVITIES, PROCESSES, PROCEDURES INVOLVED: * Systematic System Audit Check * WHY DID CONDITION HAPPEN? * Suspected wear and tear, but detailed inspection required to ascertain the cause. * * CONSEQUENCES: * Potential system failure, valve replacement may be required. * * REQUIREMENTS IMPACTED: * System fluidity and continuity * * ADVERSE PHYSICAL CONDITIONS: * Fluctuating pressure in valve 4B * * WHO WAS NOTIFIED: * Supervisor/ Fault Rectification Team / Notification Team * * KNOWLEDGEABLE INDIVIDUALS: * Notification Team, Technician Greg, Supervisor * * REPEAT OR SIMILAR CONDITION: * No, this is the first incident * * IMMEDIATE ACTIONS AND RECOMMENDED ACTIONS: * Service Team should inspect the valve and rectify the problem. If rectification doesn't work, valve replacement may be required. * 12/30/2019 18:45:38 KEVIN WHITE (INCIDENT) * Immediate action has been taken. The service team will inspect the valve tomorrow for any possible damages. | What was the identified issue with valve 4B during the system audit check? | During the system audit check at 1330 hours, valve 4B showed inconsistent pressure. Preliminary tests were conducted and fluctuating readings between 20-30 psi were recorded.
414 | 2018-03-22 | 30730415 | 80234512 | 33B Discharge Pump Fluid Leakage | S1YW -1YWE5-PMPY | * **************Incident Description************** * Notification 000030730415 Details * *********************************************************** * 03/22/2018 14:45:00 INCIDENT REPORT (INCIDENT REPORT) * Report submitted by: David Thompson ENTITY\INCIDENT: * * CONDITION DESCRIPTION/LOCATION (THE INAPPROPRIATE ACTION AND ITS NEGATIVE EFFECT/INCLUDE A DETAILED LOCATION DESCRIPTION): * At approximately 1350 on 3/22/18, a leak was discovered on the 33B Discharge Pump during routine inspection. The leakage appeared to be oil, potentially indicating seal failure. The pump was taken offline immediately and the affected area was cleaned up. Secondary containment measures were not fully effective, leaving oil residue on the floor. * * ACTIVITIES, PROCESSES, PROCEDURES INVOLVED: * S1.OP.AB-PY-0003, Regular Inspection * * WHY DID CONDITION HAPPEN: * Preliminary investigation suggests failure of the pump seal. Further inspection required. * * CONSEQUENCES: * Risk of environmental impact and occupational hazard. Impacted operational efficiency with the need to switch to backup pump. * * REQUIREMENTS IMPACTED: * Regular operation, Environmental standards * * ADVERSE PHYSICAL CONDITION: * Fluid leakage from Pump 33B, potential internal damage * * WHO WAS NOTIFIED: * Control Room, Maintenance Supervisor, EHS Officer * * KNOWLEDGEABLE INDIVIDUALS: * Johnson, Evans, Peterson * * REPEAT OR SIMILAR CONDITION: * No Known Previous Instance * * IMMEDIATE AND RECOMMENDED ACTIONS: * Seal Replacement Necessary. EHS team to evaluate environmental impact. Implementation of more effective containment measures recommended. * Updated: DAVID THOMPSON 03.22.2018 15:25:00 * ------------------------------------------------------------ * 03/23/2018 14:55:00 JANE DOE (NUSER) * The broken seal was successfully replaced, and the pump is back in normal operation. EHS Team carried out an environmental impact evaluation and confirmed minimal impact. Regular checking of pump seals | What immediate and recommended actions were proposed after the discovery of the leak in the pump? | Seal Replacement Necessary. EHS team to evaluate environmental impact. Implementation of more effective containment measures recommended.
415 | 2020-05-15 | 31072460 | 80212910 | 23B Cooler lower flow rate | S4CW -4CWE2 | * **************Incident Description************** * Notification 000031072460 Details * *********************************************************** * 05/15/2020 14:33:00 INCIDENT REPORT (INCIDENT REPORT) * Report submitted by: Robert Green ENTITY\INCIDENT: * * CONDITION DESCRIPTION/LOCATION (THE INAPPROPRIATE ACTION AND ITS NEGATIVE EFFECT/INCLUDE A DETAILED LOCATION DESCRIPTION): * At 1420 hours on 15/05/20, it was reported that 23B Cooler was showing a reduced flow rate. Immediate checks indicated no external leakage or blockage. This abnormal behavior has resulted in reduced cooling efficiency for associated processes. Further investigation needed. * * ACTIVITIES, PROCESSES, PROCEDURES INVOLVED: * S4.OP.AB-CW-0002, S4.OP-SO.CW-0002 were activated. * * WHY DID CONDITION HAPPEN? * It's uncertain at this stage, but initial insight suggests system imbalance or internal blockage. * * CONSEQUENCES: * Affecting the cooling efficiency, potential equipment damage if not rectified promptly. * * REQUIREMENTS IMPACTED: * Cooling processes * * ADVERSE PHYSICAL CONDITIONS: * Decreased flow rate for 23B Cooler * * WHO WAS NOTIFIED: * Control Room, Maintenance Department * * KNOWLEDGEABLE INDIVIDUALS: * Thompson, Lewis, Jackson * * REPEAT OR SIMILAR CONDITION: * No * * IMMEDIATE ACTIONS AND RECOMMENDED ACTIONS: * Maintenance and engineering teams to conduct a thorough inspection of the 23B Cooler. * * Updated: ROBERT GREEN 05.15.2020 14:45:32 * ------------------------------------------------------------ * 05/20/2020 10:34:11 JANE DOE (NUSER) * Investigation revealed a blockage in an internal pipe of the cooler. The pipe was cleaned and the flow rate returned to normal. Maintenance will be conducting regular checks to prevent reoccurrence. The cooler is now back to normal operation. | What was the identified issue with the 23B Cooler and how was it rectified? | Investigation revealed a blockage in an internal pipe of the cooler. The pipe was cleaned and the flow rate returned to normal. Maintenance will be conducting regular checks to prevent reoccurrence. The cooler is now back to normal operation.
416 | 2019-04-01 | 30920315 | 80541570 | Abnormal Vibration on 28B Pump | S4CW -4CWE5 | * **************Incident Description************** * Notification 000030920315 Details * *********************************************************** * 04/01/2019 10:15:30 INCIDENT REPORT (INCIDENT REPORT) * Report submitted by: Patricia White ENTITY\INCIDENT: * * CONDITION DESCRIPTION/LOCATION (THE INAPPROPRIATE ACTION AND ITS NEGATIVE EFFECT/INCLUDE A DETAILED LOCATION DESCRIPTION): * During routine inspection, 28B Pump was found exhibiting abnormal vibration. Historically, this pump has operated without such heavy vibration. This abnormality was identified early in the morning, causing unplanned inspection and vibration analysis. Current, temperature, nozzle pressure, and flow rate were found to be within normal values. * ACTIVITIES, PROCESSES, PROCEDURES INVOLVED: * Vibration Analysis and inspection as part of routine monitoring. * WHY DID CONDITION HAPPEN? * Unknown at this time. A complete analysis and inspection will be conducted. * CONSEQUENCES: * Continued operation under these conditions might result in pump damage or failure, reducing the reliability and efficiency of the system. * REQUIREMENTS IMPACTED: * Potential impact on normal operation. * ADVERSE PHYSICAL CONDITIONS: * Abnormal pump vibration. * WHO WAS NOTIFIED: * Supervisor, Maintenance Team, Vibration Analyst * KNOWLEDGEABLE INDIVIDUALS: * Vibration Analyst, Maintenance Supervisor. * REPEAT OR SIMILAR CONDITION: * No, this is a first-time occurrence with this pump. * IMMEDIATE ACTIONS AND RECOMMENDED ACTIONS: * The pump was temporarily taken out of service. A detailed inspection and vibration analysis will be performed to ascertain the cause of the situation. * 04/01/2019 17:39:56 PATRICIA WHITE (INCIDENT) * After thorough analysis and inspection, it was found out that there were misaligned couplings. Maintenance team is asked to fix the misaligned couplings. Further monitoring is suggested. | What was the identified cause of the abnormal vibration in 28B Pump? | After thorough analysis and inspection, it was found out that there were misaligned couplings.
417 | 2017-01-21 | 30781293 | 80242932 | Unusual noise from 7A Pump | S4CW -4CWE2 | * **************Incident Description************** * Notification 000030781293 Details * *********************************************************** * 01/21/2017 15:32:22 INCIDENT REPORT (INCIDENT REPORT) * Report submitted by: Robert White ENTITY\INCIDENT: * * CONDITION DESCRIPTION/LOCATION (THE INAPPROPRIATE ACTION AND ITS NEGATIVE EFFECT/INCLUDE A DETAILED LOCATION DESCRIPTION): * During morning rounds, discovered that the 7A Pump was making an odd noise, not typically heard from this unit. Recorder readings indicated current as 320. * * ACTIVITIES, PROCESSES, PROCEDURES INVOLVED: * S4.OP-SO.CW-0002 routine operation, S4.OP-AB.CW-0005 pump abnormaility * * WHY DID CONDITION HAPPEN? * Unknown cause, could be due to wear & tear or any lodged particles. * * CONSEQUENCES: * Potential failure of pump, disruption of operations. * * REQUIREMENTS IMPACTED: * Normal operation of the 7A pump. * * ADVERSE PHYSICAL CONDITIONS: * Abnormal noise from 7A pump. * * WHO WAS NOTIFIED: * Plant Manager/MAINTENANCE TEAM * KNOWLEDGEABLE INDIVIDUALS: * Robert White, Christina Perry, Liam Powell * * REPEAT OR SIMILAR CONDITION: * No * * IMMEDIATE ACTIONS AND RECOMMENDED ACTIONS: * Initiate S4.OP-AB.CW-0005 for abnormal pump noise and schedule inspection. If needed, replace or repair the affected components. * 01/21/2017 19:30:41 ROBERT WHITE (INCIDENT) * The initial inspection does not reveal any visual damage. Recommended thorough internal inspection to determine the cause of the noise. | What immediate actions were recommended upon discovering the abnormal noise of the 7A pump? | Initiate S4.OP-AB.CW-0005 for abnormal pump noise and schedule inspection. If needed, replace or repair the affected components.
418 | 2018-04-26 | 30980416 | 80650133 | 14B FM noise register post-operational testing | S4CW -4CWE5 | * **************Incident Description************** * Notification 000030980416 Details * *********************************************************** * 04/26/2018 15:33:24 INCIDENT REPORT (INCIDENT REPORT) * Report submitted by: Emma Watson ENTITY\INCIDENT: * * CONDITION DESCRIPTION/LOCATION (THE INAPPROPRIATE ACTION AND ITS NEGATIVE EFFECT/INCLUDE A DETAILED LOCATION DESCRIPTION): * After post-operational testing, 14B Flow Meter (FM) registered unusual noise. The vibration, normally stable at around 3.0 mm/s, had suddenly increased to 7.5 mm/s after the testing. Vibration of adjacent flow meters remained at acceptable levels around 3.0 -3.5 mm/s. * * ACTIVITIES, PROCESSES, PROCEDURES INVOLVED: * Regular post-operational testing * * WHY DID CONDITION HAPPEN? * Unsure, possibly due to bearings or rotor imbalance. * * CONSEQUENCES: * Potential malfunction of flow meter and influence on overall facility function. * * REQUIREMENTS IMPACTED: * Flow Meter operation * * ADVERSE PHYSICAL CONDITIONS: * Increased vibration, noise from FM * * WHO WAS NOTIFIED: * Maintenance Supervisor/ INCIDENT TEAM * * KNOWLEDGEABLE INDIVIDUALS: * Engineer, Flow meter Technician * * REPEAT OR SIMILAR CONDITION: * No * * IMMEDIATE ACTIONS AND RECOMMENDED ACTIONS: * Immediate inspection of FM 14B, verify calibration, and check the rotor condition. If necessary, replace the bearings. * 04/26/2018 18:15:21 EMMA WATSON (INCIDENT) * The inspection returned positive for worn out bearings, causing the increase in vibration. Bearings are to be replaced under OrderNum 80650134. Post repair, the FM requires calibration and monitoring. | What immediate actions were recommended regarding the incident with the 14B Flow Meter? | Immediate inspection of FM 14B, verify calibration, and check the rotor condition. If necessary, replace the bearings.
419 | 2017-09-30 | 30750345 | 80231647 | 18B Pump motor failure | S2CW -2CWE9 | * **************Incident Description************** * Notification 000030750345 Details * *********************************************************** * 09/30/2017 15:54:09 INCIDENT REPORT (INCIDENT REPORT) * Report submitted by: Samuel Connolly 321-654-0987 ENTITY\INCIDENT: * CONDITION DESCRIPTION/LOCATION (THE INAPPROPRIATE ACTION AND ITS NEGATIVE EFFECT/INCLUDE A DETAILED LOCATION DESCRIPTION): * During a routine inspection, the 18B Pump, post maintenance, was found to be non-operational. The circuit-breaker repeatedly tripping indicated a probable motor failure. The pump was last serviced on 01/2017 under work order 80217745. * * ACTIVITIES, PROCESSES, PROCEDURES INVOLVED: * Routine inspection, immediate troubleshoot * * WHY DID CONDITION HAPPEN? * Likely a motor failure but further investigation required for definitive cause. * * CONSEQUENCES: * Disruption to normal operation, potential extended downtime * * REQUIREMENTS IMPACTED: * Unavailable pump, impact on daily operations. * * ADVERSE PHYSICAL CONDITIONS: * Non-operational pump, potential motor damage * * WHO WAS NOTIFIED: * Operations team, Maintenance team * * KNOWLEDGEABLE INDIVIDUALS: * Maintenance team, Operations manager * * REPEAT OR SIMILAR CONDITION: * No, this is the first time * * IMMEDIATE ACTIONS AND RECOMMENDED ACTIONS: * Temporarily switch to the alternate unit, initiate an immediate technical investigation of 18B Pump Motor. * 10/02/2017 11:58:34 SAMUEL CONNOLLY (INCIDENT) * Confirmed failure of the motor due to winding insulation failure. Ordering for replacements and updating maintenance procedures to include regular insulation resistance testing. | What was the immediate action recommended in response to the pump failure? | Temporarily switch to the alternate unit, initiate an immediate technical investigation of 18B Pump Motor.
420 | 2019-01-30 | 40620450 | 90127946 | 30B Motor vibration detected | S4CW -4CWE2 | * **************Incident Description************** * Notification 000040620450 Details * *********************************************************** * 01/30/2019 10:35:29 INCIDENT REPORT (INCIDENT REPORT) * Report submitted by: Martin Lawrence ENTITY\INCIDENT: * * CONDITION DESCRIPTION/LOCATION (THE INAPPROPRIATE ACTION AND ITS NEGATIVE EFFECT/INCLUDE A DETAILED LOCATION DESCRIPTION): * On 01/30/2019 during a routine operation, 30B Motor, observed with unusual vibration. While checking the operations of the motor, the voltage inspected to be in normal range. However, the vibration persisted. The motor had been serviced under work order 90127946 and returned to service on 01/28/2019. * * ACTIVITIES, PROCESSES, PROCEDURES INVOLVED: * Regular operational check and vibration monitoring of 30B Motor * * WHY DID CONDITION HAPPEN? * Uncertain, however it's possible that the misalignment after recent maintenance could have caused the unusual vibration. * * CONSEQUENCES: * Unusual vibration can lead to motor failure, creating potential operational interruptions. * * REQUIREMENTS IMPACTED: * Equipment vibrational parameters have been exceeded. * * ADVERSE PHYSICAL CONDITIONS: * High vibration on 30B Motor * * WHO WAS NOTIFIED: * Supervisor, Engineering, Maintenance Teams * * KNOWLEDGEABLE INDIVIDUALS: * Engineering, Maintenance Teams * * REPEAT OR SIMILAR CONDITION: * No, this is the first instance post maintenance. * * IMMEDIATE ACTIONS AND RECOMMENDED ACTIONS: * Recommend Maintenance to inspect 30B Motor for misalignment and correct as needed. * 01/30/2019 13:12:53 MARTIN LAWRENCE (INCIDENT) * Maintenance Team has been informed and will be inspecting the 30B Motor for possible misalignment as part of further investigation and addressing the issue. | What immediate action was recommended after observing the high vibration on the 30B Motor? | Recommend Maintenance to inspect 30B Motor for misalignment and correct as needed.
421 | 2018-11-15 | 30957211 | 80293811 | Coolant leak detected at unit 2D | S4CW -4CWE5 | * **************Incident Description************** * Notification 000030957211 Details * *********************************************************** * 11/15/2018 14:37:19 INCIDENT REPORT (INCIDENT REPORT) * Report submitted by: David White ENTITY\INCIDENT: * * CONDITION DESCRIPTION/LOCATION (THE INAPPROPRIATE ACTION AND ITS NEGATIVE EFFECT/INCLUDE A DETAILED LOCATION DESCRIPTION): * During a routine inspection, there was a coolant leak detected at unit 2D pump. The coolant is leaking at an alarming rate and measures have been taken to contain the leak. The pump has been shut down temporarily until further inspection and rectification. The coolant leak may be due to fault in the pump or an external issue, further investigation is required. * * ACTIVITIES, PROCESSES, PROCEDURES INVOLVED: * Routine inspection and S4.OP-AB.CW-0002 Leakage detection procedure * * WHY DID CONDITION HAPPEN? * Culprit could be wear and tear or pump damage, conclusion will be based on further inspection * * CONSEQUENCES: * Possible damage to the pump, hazardous environment due to coolant leak, reduced efficiency * * REQUIREMENTS IMPACTED: * Operations are held due to pump failure, affecting the daily process * * ADVERSE PHYSICAL CONDITIONS: * Coolant leak from the pump, potential internal damage to the pump * * WHO WAS NOTIFIED: * Supervisor, Inspection Team, Incident head * * KNOWLEDGEABLE INDIVIDUALS: * Incident Team, Maintenance Head * * REPEAT OR SIMILAR CONDITION: * No, first occurrence. * * IMMEDIATE ACTIONS AND RECOMMENDED ACTIONS: * Stop the usage of pump, containment of coolant leak, further inspection of the pump to find out the cause of leak. * 11/22/2018 16:56:28 DAVID WHITE (INCIDENT) * Post inspection, it was found that the leakage was due to the failure of a coolant pipe. This has been resolved and the leakage contained. The pump is now operational and no further leakage has been observed. | What was concluded as the cause of the coolant leak in pump unit 2D after further inspection? | Post inspection, it was found that the leakage was due to the failure of a coolant pipe.
422 | 2019-10-07 | 30789566 | 80223451 | Excessive vibration from 12C pump | S4CW -4CWE7 | * **************Incident Description************** * Notification 000030789566 Details * *********************************************************** * 10/07/2019 08:20:32 INCIDENT REPORT (INCIDENT REPORT) * Report submitted by: David Ford ENTITY\INCIDENT: * * CONDITION DESCRIPTION/LOCATION (THE INAPPROPRIATE ACTION AND ITS NEGATIVE EFFECT/INCLUDE A DETAILED LOCATION DESCRIPTION): * During a routine check of the facilities, excessive vibration from the 12C Pump was noticed. This pump has been in operation since its last maintenance under Work Order 80212247 six months ago. There were no such issues reported then. The pump has been temporary shutdown for further inspection. * * ACTIVITIES, PROCESSES, PROCEDURES INVOLVED: * S4.OP.AB-CW-0012, Regular maintenance check. * * WHY DID CONDITION HAPPEN? * The cause for this is unclear at this moment but could be due to failure of internal components. * * CONSEQUENCES: * Unexpected failure could lead to production disturbances and potential breakdown. * * REQUIREMENTS IMPACTED: * Reliability and operation of the 12C pump. * * ADVERSE PHYSICAL CONDITIONS: * Excessive vibration from pump 12C. * * WHO WAS NOTIFIED: * Site Supervisor, Maintenance team * * KNOWLEDGEABLE INDIVIDUALS: * Maintenance team, Site Supervisor * * REPEAT OR SIMILAR CONDITION: * No, this is first time for 12C pump. However, similar cases happened in other pumps. * * IMMEDIATE ACTIONS AND RECOMMENDED ACTIONS: * Shutdown the pump, carry out a detailed investigation to identify the cause of the vibration and remedy it. Incorporate findings into preventive maintenance plan. * 10/07/2019 15:33:43 DAVID FORD (INCIDENT) * Maintenance team found some damaged bearings which likely caused the excessive vibration. The pump has now been repaired and is running smoothly. Recommendations for enhanced regular maintenance checks on all pumps have now been relayed to the supervisor. | What was the initial observation that led to the inspection of the 12C pump? | During a routine check of the facilities, excessive vibration from the 12C Pump was noticed.
423 | 2018-10-13 | 30763594 | 80245673 | Sudden drop in 18B pump pressure | S2CW -3CWE2- PUMPA | * **************Incident Description**************** * Notification 000030763594 Details * *********************************************************** * 10/13/2018 15:20:34 INCIDENT RESPONSE (INCIDENT RESPONSE) * Report submitted by: Danny Morris ENTITY\INCIDENT: * * CONDITION DESCRIPTION/LOCATION (THE INAPPROPRIATE ACTION AND ITS NEGATIVE EFFECT/INCLUDE A DETAILED LOCATION DESCRIPTION): * During routine system monitoring on the evening of 10/13/2018, an unexpected pressure drop was reported on the 18B pump. Subsequent visual inspection revealed unusual noise and vibration. While there was no immediate adverse impact on system operations, the unexplained condition raised concerns about potential pump damage and reliability. * * ACTIVITIES, PROCESSES, PROCEDURES INVOLVED: * Routine system monitoring and live system parameters evaluation. * * WHY DID CONDITION HAPPEN? * It is uncertain at this stage. Initial thoughts suggest possible malfunctioning pressure sensors, but this remains to be confirmed by in-depth diagnostics. * * CONSEQUENCES: * An unexpected pressure drop may indicate a potential failure which may cause the pump to operate inefficiently or even lead to a system outage. * * REQUIREMENTS IMPACTED: * Normal pump operation, reliability, and system stability. * * ADVERSE PHYSICAL CONDITIONS: * Sudden drop in pressure in the 18B pump, noticeable unusual noise and vibration. * * WHO WAS NOTIFIED: * System Control Manager, On-Call technician, and the Incident Response Team. * * KNOWLEDGEABLE INDIVIDUALS: * Danny Morris, Senior Operation Technician. Incident Response Team. * * REPEAT OR SIMILAR CONDITION: * No, this is the first occurrence of such an issue with the 18B pump. * * IMMEDIATE ACTIONS AND RECOMMENDED ACTIONS: * A prompt technical review of the situation is recommended. Scheduled an immediate maintenance inspection of the 18B pump and the associated pressure sensing and control systems. * 10/14/2018 08:28:16 DANNY MORRIS (INCIDENT) | What immediate actions were taken after the unexpected pressure drop in the pump? | A prompt technical review of the situation is recommended. Scheduled an immediate maintenance inspection of the 18B pump and the associated pressure sensing and control systems.
424 | 2019-04-11 | 30823947 | 80345278 | 28B Cooler malfunction causing temperature rise | S4CW -4CWE9 | * **************Incident Description************** * Notification 000030823947 Details * *********************************************************** * 04/11/2019 13:24:48 INCIDENT REPORT (INCIDENT REPORT) * Report submitted by: Richard Gray ENTITY\INCIDENT: * * CONDITION DESCRIPTION/LOCATION (THE INAPPROPRIATE ACTION AND ITS NEGATIVE EFFECT/INCLUDE A DETAILED LOCATION DESCRIPTION): * During the afternoon shift, the monitoring system reported unusually high temperatures on the 28B Cooler. The cooler was inspected, revealing high leakage through the cooling system, with clear signs of dried salt deposits. Noise level was within normal. * * ACTIVITIES, PROCESSES, PROCEDURES INVOLVED: * S4.OP.ML.CW-0003, S4.OP-SR.CO-0002 * * WHY DID CONDITION HAPPEN? * Possible seal or gasket failure causing leak. Further investigation is needed. * * CONSEQUENCES: * Impact on cooling efficiency, possible environmental impact. * * REQUIREMENTS IMPACTED: * Operational continuity and environmental compliance. * * ADVERSE PHYSICAL CONDITIONS: * Elevated cooler temperatures, noticeable coolant leakage. * * WHO WAS NOTIFIED: * Shift Supervisor, Environmental Officer, Maintenance Team. * * KNOWLEDGEABLE INDIVIDUALS: * Peterson, O’Connor, Thompson. * * REPEAT OR SIMILAR CONDITION: * No, this is the first instance. * * IMMEDIATE ACTIONS AND RECOMMENDED ACTIONS: * Stop the 28B cooler operation and initiate repair process. Ensure coolant leakage is contained and cleaned up. * 04/12/2019 08:37:22 RICHARD GRAY (INCIDENT) * A seal defect was confirmed as the cause of the leakage. The cooler was shut down, repaired overnight, and is now operating within normal parameters. Other coolers are being inspected as a precaution for similar faults. | What immediate and recommended actions were taken after the unusual temperature and leakage were detected in the 28B Cooler? | Stop the 28B cooler operation and initiate repair process. Ensure coolant leakage is contained and cleaned up. A seal defect was confirmed as the cause of the leakage. The cooler was shut down, repaired overnight, and is now operating within normal parameters. Other coolers are being inspected as a precaution for similar faults.
425 | 2022-03-10 | 40123920 | 90213405 | Cooling tower fan 18C unusual vibration | S1CW -1CWE3 | * **************Incident Description************** * Notification 000040123920 Details * ************************************************************* * 03/10/2022 14:10:45 INCIDENT REPORT (INCIDENT REPORT) * Report submitted by: Chris Burton ENTITY\INCIDENT: * * CONDITION DESCRIPTION/LOCATION (THE INAPPROPRIATE ACTION AND ITS NEGATIVE EFFECT/INCLUDE A DETAILED LOCATION DESCRIPTION): * During a routine inspection at 14:10 on 03/10/2022, the operator noticed unusual vibration in the cooling tower 18C fan. The fan was immediately shut down. The preliminary inspection revealed excessive lateral movement on the fan's drive shaft assembly. Despite recent maintenance on cooling tower fans, this abnormality was unexpected and indicates potential internal issues. * * ACTIVITIES, PROCESSES, PROCEDURES INVOLVED: * S1.OP-SO.CW-0001, S1.OP-AB.CW-0001 * * WHY DID CONDITION HAPPEN: * Probable internal issues, specific cause is yet to be identified. Previous similar incident resulted from misalignment of the drive shaft assembly. * * CONSEQUENCES: * Immediate operational disruption and potential major system failure if not rectified. * * REQUIREMENTS IMPACTED: * Normal operation of the cooling tower, possible delay in operations. * * ADVERSE PHYSICAL CONDITIONS: * Abnormal vibrations in cooling tower fan. * * WHO WAS NOTIFIED: * Maintenance Team, Control Room * * KNOWLEDGEABLE INDIVIDUALS: * Supervisor, Mechanical Engineer, Smith, Johnson * * REPEAT OR SIMILAR CONDITION: * Yes, there has been a similar incident previously. * * IMMEDIATE ACTIONS AND RECOMMENDED ACTIONS: * Urgent investigation required on cooling tower fan 18C via maintenance request, shutdown cooling tower 18C for risk assessment and repair if required. * 03/15/2022 10:22:35 JAMES REED (INCIDENT) * Following the inspection of Cooling Tower Fan 18C, it was discovered that the issue was with the drive shaft's alignment. Immediate rectifications have been carried out and the system is | What was the identified issue causing unusual vibration in the cooling tower fan, and what measures were taken after its discovery? | Following the inspection of Cooling Tower Fan 18C, it was discovered that the issue was with the drive shaft's alignment. Immediate rectifications have been carried out and the system.
426 | 2018-10-13 | 30835890 | 80235648 | Leakage from F5B Pump | S3CW -3FWE2 | * **************Incident Description************** * Notification 000030835890 Details * *********************************************************** * 10/13/2018 09:16:21 INCIDENT REPORT (INCIDENT REPORT) * Report submitted by: Robert Walker 120-456-7894 ENTITY\INCIDENT: * CONDITION DESCRIPTION/LOCATION (THE INAPPROPRIATE ACTION AND ITS NEGATIVE EFFECT/INCLUDE A DETAILED LOCATION DESCRIPTION): * Maintenance crew reported that during a routine inspection, leakage was observed from the F5B pump. The leak was significant enough to observe but not enough to cause a shutdown. The leakage level will need to be continuously monitored and the pump may need to be replaced. * * ACTIVITIES, PROCESSES, PROCEDURES INVOLVED: * Routine inspection * WHY DID CONDITION HAPPEN? * Unknown, possibly due to wear and tear or a seal failure * * CONSEQUENCES: * Risk of pump failure, increased maintenance requirements * * REQUIREMENTS IMPACTED: * Daily operation schedule, planned maintenance * * ADVERSE PHYSICAL CONDITIONS: * Leak from F5B pump * * WHO WAS NOTIFIED: * Supervisor, Head of Maintenance Department * * KNOWLEDGEABLE INDIVIDUALS: * Robert Walker, Maintenance Team * * REPEAT OR SIMILAR CONDITION: * No, this is the first occurrence * * IMMEDIATE ACTIONS AND RECOMMENDED ACTIONS: * The pump will continue to be monitored closely. If leakage persists or increases, pump will be tested for efficiency and might need replacement. * 10/14/2018 15:43:11 Robert Walker (INCIDENT) * Additional inspection completed, minor wear found on seals potentially causing leakage. Seal replacement scheduled. | What was the issue observed during the routine inspection of the F5B pump? | Maintenance crew reported that during a routine inspection, leakage was observed from the F5B pump. The leak was significant enough to observe but not enough to cause a shutdown.
427 | 2016-12-24 | 30782465 | 90263784 | 9B Pump Clog | S1PW -1PWE2 | * **************Incident Description************** * Notification 000030782465 Details * *********************************************************** * 12/24/2016 13:15:34 INCIDENT REPORT (INCIDENT REPORT) * Report submitted by: Ryan Anderson ENTITY\INCIDENT: * * CONDITION DESCRIPTION/LOCATION (The inappropriate action and its negative effect/Include a detailed location description): * During normal operation, at 1330 hrs, the operator noted a sudden pressure drop at the 9B Pump. Upon inspection, it was found that the pump has clogged due to excess debris. The pump was immediately turned off for further inspection. * * ACTIVITIES, PROCESSES, PROCEDURES INVOLVED: * Routine inspection and operation of 9B pump. * * WHY DID CONDITION HAPPEN? * The cause might be the absence of a proper filtration mechanism leading to debris clogging the pump. * * CONSEQUENCES: * The operation of the unit gets affected due to unavailable pump. * * REQUIREMENTS IMPACTED: * Normal operation of the pump * * ADVERSE PHYSICAL CONDITIONS: * Clogged 9B Pump, and probable internal damage * * WHO WAS NOTIFIED: * Supervisor / Incident Team * * KNOWLEDGEABLE INDIVIDUALS: * Incident Team, Supervisor * * REPEAT OR SIMILAR CONDITION: * No, first occurrence * * IMMEDIATE ACTIONS AND RECOMMENDED ACTIONS: * The pump must be fully cleaned and inspected for any internal damage. A filtration mechanism should be put in place to avoid future clogging. * * 12/24/2016 17:29:51 RYAN ANDERSON (INCIDENT) * The pump was thoroughly cleaned and inspected, no damages were found. It is recommended to install a proper filtration device as preventive measure. The pump is now back in operation. | What immediate actions were taken after the clogging of the 9B pump and what further steps are recommended to prevent this? | The pump was thoroughly cleaned and inspected, no damages were found. It is recommended to install a proper filtration device as preventive measure. The pump is now back in operation.
428 | 2018-09-05 | 30785960 | 80263491 | 34B pump motor buzzing noise | S4CW -4CWE9 | * **************Incident Description************** * Notification 000030785960 Details * *********************************************************** * 09/05/2018 16:20:50 INCIDENT REPORT (INCIDENT REPORT) * Report submitted by: Mike Taylor ENTITY\INCIDENT: * * CONDITION DESCRIPTION/LOCATION (THE INAPPROPRIATE ACTION AND ITS NEGATIVE EFFECT/INCLUDE A DETAILED LOCATION DESCRIPTION): * Following routine maintenance, the 34B Pump motor has been emitting a buzzing noise. This noise is not consistent with the normal functioning of the motor. The pump temperatures and operational parameters remain within normal values; however, the noise continues unabated. * * ACTIVITIES, PROCESSES, PROCEDURES INVOLVED: * S4.OP.AB-CW-0002, S4.OP-SO.CW-0005 * * WHY DID CONDITION HAPPEN? * Unclear at the present moment. Potentially due to incorrect reassembly after maintenance or an internal defect not detected during maintenance. * * CONSEQUENCES: * Potential disruption of normal operation due to unknown factor causing the noise. If not addressed, it may lead to further unidentified problems or damage. * * REQUIREMENTS IMPACTED: * Operational readiness of 34B Pump * * ADVERSE PHYSICAL CONDITIONS: * Unidentified buzzing noise from 34B Pump motor * * WHO WAS NOTIFIED: * Supervisor, Maintenance Team * * KNOWLEDGEABLE INDIVIDUALS: * Maintenance Supervisor, Site Engineer * * REPEAT OR SIMILAR CONDITION: * No * * IMMEDIATE ACTIONS AND RECOMMENDED ACTIONS: * Recommend immediate inspection and, if necessary, disassembling the pump for detailed internal inspection. * 09/08/2018 10:34:41 JOHN DOE (INCIDENT) * Upon detailed inspection, it was determined that the buzzing noise was due to a misalignment in the motor assembly. The unit was properly aligned and reassembled. The noise has ceased and the motor is back in normal operation. | Why was there a buzzing noise coming from the 34B Pump motor after maintenance? | Upon detailed inspection, it was determined that the buzzing noise was due to a misalignment in the motor assembly.
429 | 2020-12-30 | 30945211 | 90234567 | Unusual vibration on 34B Pump | S4CW -4CWE7 | * **************Incident Description************** * Notification 000030945211 Details * *********************************************************** * 12/30/2020 10:23:00 INCIDENT REPORT (INCIDENT REPORT) * Report submitted by: Emma Black ENTITY\INCIDENT: * * CONDITION DESCRIPTION/LOCATION (THE INAPPROPRIATE ACTION AND ITS NEGATIVE EFFECT/INCLUDE A DETAILED LOCATION DESCRIPTION): * The 34B Pump, post-containment, was noticed having abnormal vibration during the routine surveillance on 12/30/2020. All other parameters, including current and temperature, were within normal limits. 34B Pump was not taken out of service due to the non-critical nature of the abnormality. Investigation to follow to rule out equipment failure or imbalances. * * ACTIVITIES, PROCESSES, PROCEDURES INVOLVED: * Ring test and other non-invasive testing methods to be performed. * * WHY DID CONDITION HAPPEN? * Unknown, pending investigation. * * CONSEQUENCES: * Potential internal damage leading to failure or reduced efficiency if not resolved. * * REQUIREMENTS IMPACTED: * Continuous safe operation of the unit. * * ADVERSE PHYSICAL CONDITIONS: * Vibrating pump possibly indicating imbalance or internal damage. * * WHO WAS NOTIFIED: * Supervisor, Operations Team. * * KNOWLEDGEABLE INDIVIDUALS: * Emma Black, Operations Team * * REPEAT OR SIMILAR CONDITION: * No, this issue has not previously reported on this asset. * * IMMEDIATE ACTIONS AND RECOMMENDED ACTIONS: * Scheduled investigation, potentially leading to maintenance or replacement of parts. * * 12/31/2020 08:45:00 EMMA BLACK (INCIDENT) * Scheduled investigation to take place. Based on findings could lead to work package for maintenance. | What could be the consequences of the abnormal vibration noticed in the 34B Pump? | Potential internal damage leading to failure or reduced efficiency if not resolved.
430 | 2019-12-18 | 30998624 | 80278532 | 18B Pump low-pressure alarm | S5CW -5CWE7 | * **************Incident Description************** * Notification 000030998624 Details * *********************************************************** * 12/18/2019 08:22:45 INCIDENT REPORT (INCIDENT REPORT) * Report submitted by: Sarah Miller ENTITY\INCIDENT: * * CONDITION DESCRIPTION/LOCATION (THE INAPPROPRIATE ACTION AND ITS NEGATIVE EFFECT/INCLUDE A DETAILED LOCATION DESCRIPTION): * At 0800 on 12/18/19, the control room reported a low-pressure alarm for the 18B Pump. In response, the pump was manually shut down. There was no immediate evidence of leakage. Inspection and corrective measures were initiated under S5.OP-AB.CW-0002. * * ACTIVITIES, PROCESSES, PROCEDURES INVOLVED: * S5.OP.AB-CW-0002, S5.OP-SO.CW-0004 * * WHY DID CONDITION HAPPEN? * Unknown. There were no prior indications of shrinking pressure. * * CONSEQUENCES: * Pump shutdown may affect production efficiency. Potential motor damage if not resolved quickly. * * REQUIREMENTS IMPACTED: * Shut down pump, production efficiency affected. * * ADVERSE PHYSICAL CONDITIONS: * Low-pressure alert on the 18B pump, potential internal damage. * * WHO WAS NOTIFIED: * Control Room, Maintenance Department. * * KNOWLEDGEABLE INDIVIDUALS: * Thompson, Davis, Reed. * * REPEAT OR SIMILAR CONDITION? * No. * * IMMEDIATE ACTIONS AND RECOMMENDED ACTIONS: * Maintenance is to investigate the 18B pump for the cause of low pressure. * 12/18/2019 15:07:32 SARAH MILLER (INCIDENT) * Pump inspection revealed a clog in the oil filter which led to the fall in pressure. The filter was replaced and pump pressure restored to normal. | What was the immediate action taken after the low-pressure alarm of the 18B pump? | The pump was manually shut down. Inspection and corrective measures were initiated under S5.OP-AB.CW-0002.
431 | 2019-03-30 | 30871124 | 80223456 | 34D Pump erratic vibration | S4CW -4CWE5 | * **************Incident Description************** * Notification 000030871124 Details * *********************************************************** * 03/30/2019 07:45:12 INCIDENT REPORT (INCIDENT REPORT) * Report submitted by: Richard Green ENTITY\INCIDENT: * * CONDITION DESCRIPTION/LOCATION (THE INAPPROPRIATE ACTION AND ITS NEGATIVE EFFECT/INCLUDE A DETAILED LOCATION DESCRIPTION): * During daily monitoring, the maintenance team reported erratic vibration in the 34D Pump. This alert caused an immediate investigation of the pump operation. No direct cause could be identified from visual inspection, but report was generated due to potential implications. * * ACTIVITIES, PROCESSES, PROCEDURES INVOLVED: * Regular operation observation, S4.OP-AB.CW-0003, S4.OP-SO.CW-0004 * * WHY DID CONDITION HAPPEN? * Unknown, vibration could be due to mechanical misalignment or bearing issues. * * CONSEQUENCES: * Potential loss of pump efficiency, pump damage if not addressed. * * REQUIREMENTS IMPACTED: * Normal pump operation * * ADVERSE PHYSICAL CONDITIONS: * High level of vibration at 34D pump * * WHO WAS NOTIFIED: * Plant Supervisor, Maintenance Management * * KNOWLEDGEABLE INDIVIDUALS: * Plant Supervisor, Senior Technician * * REPEAT OR SIMILAR CONDITION: * No, this is the first such incident with 34D Pump. * * IMMEDIATE AND RECOMMENDED ACTIONS: * Maintenance team to conduct thorough mechanical check on 34D pump and perform any necessary repairs. * 04/02/2019 13:00:32 RICHARD GREEN (INCIDENT) * The team discovered a slight misalignment in the pump setup. After realignment and test run, the pump operation normalized. Further monitoring will be carried out to ensure the issue does not persist. | What was the recommended immediate action after the discovery of high-level vibration at the 34D pump? | Maintenance team to conduct thorough mechanical check on 34D pump and perform any necessary repairs.
432 | 2018-09-03 | 30758590 | 80233545 | 9B pump motor low pressure | S1CW -1CWE7 | * **************Incident Description************** * Notification 000030758590 Details * *********************************************************** * 09/03/2018 10:23:10 INCIDENT REPORT (INCIDENT REPORT) * Report submitted by: Kelly Jones 123-786-5960 ENTITY\INCIDENT: * CONDITION DESCRIPTION/LOCATION (THE INAPPROPRIATE ACTION AND ITS NEGATIVE EFFECT/INCLUDE A DETAILED LOCATION DESCRIPTION): * At 0923 on 9/3/18, during a planned inspection, low pressure was identified in the 9B pump motor. Immediate actions were taken and the pump was shut down for inspection. There was no immediate damage but low pressure alarms initiated. Standard Operations Procedure S1.OP-AB.CW-0003 was initiated for Pump Low Pressure. * * ACTIVITIES, PROCESSES, PROCEDURES INVOLVED: * S1.OP-AB.CW-0003, S1.OP-SO.CW-0001 * * WHY DID CONDITION HAPPEN: * Unknown, investigations are underway to identify the root cause of low pressure. * * CONSEQUENCES: * Potential for reduced efficiency and motor damage * * REQUIREMENTS IMPACTED: * Pump shutdown, operations impacted * * ADVERSE PHYSICAL CONDITION: * Low pressure in 9B pump motor * * WHO WAS NOTIFIED: * Control Room, Operations Team * * KNOWLEDGEABLE INDIVIDUALS: * Thompson, Smith, Johnson * * REPEAT OR SIMILAR CONDITION: * No * * 09/03/2018 13:55:21 KELLY JONES (INCIDENT) * Diagnostic investigations ongoing. Engineers are evaluating the issue in more detail. * * IMMEDIATE AND RECOMMENDED ACTIONS: * Investigation to identify cause of low pressure. Restoration plan to be developed post identification of root cause. The operations team needs to stay alert to fluctuations in pump pressures. | What actions were taken when low pressure was identified in the 9B pump motor? | Immediate actions were taken and the pump was shut down for inspection.
433 | 2019-11-15 | 30986321 | 80543322 | Pump 33C Water leak | S2CW -2CWE8 | * **************Incident Description************** * Notification 000030986321 Details * *********************************************************** * 11/15/2019 07:32:14 INCIDENT REPORT (INCIDENT REPORT) * Report submitted by: Emily Stark 654-321-9870 ENTITY\INCIDENT: * * CONDITION DESCRIPTION/LOCATION (THE INAPPROPRIATE ACTION AND ITS NEGATIVE EFFECT/INCLUDE A DETAILED LOCATION DESCRIPTION): * At 0730 on 11/15/19, an engineer flagged a small water leak appearing from the base of the 33C Pump. The pump was promptly put into bypass mode, and operations team initiated a temporary shutdown to investigate the source of the leak. Inspection revealed corrosion on the pump housing that had caused a small fissure. * * ACTIVITIES, PROCESSES, PROCEDURES INVOLVED: * S2.OP.AB-CW-0012, S2.OP-SO.CW-0002 * * WHY DID CONDITION HAPPEN? * Continuous operation under harsh conditions likely led to accelerated corrosion. * * CONSEQUENCES: * Possible pump failure if the leak is not addressed promptly. Potential drop in efficiency resulting in increased energy usage. * * REQUIREMENTS IMPACTED: * Pump 33C operation * * ADVERSE PHYSICAL CONDITIONS: * Water leak from pump 33C * * WHO WAS NOTIFIED: * Operations control room, management team. * * KNOWLEDGEABLE INDIVIDUALS: * Emily Stark, Tom Jackson, and John Williams * * REPEAT OR SIMILAR CONDITION: * No, this is the first such incidence * * IMMEDIATE ACTIONS AND RECOMMENDED ACTIONS: * Immediate action was taken to replace the damaged component. An analysis was also initiated to determine if additional preventive measures are necessary. * * Updated: EMILY STARK 11.15.2019 15:45:19 * ------------------------------------------------------------ * 11/30/2019 08:45:00 JOHN WILLIAMS (NUSER) * The replacement of the damaged component has been completed successfully. The pump is now under observation for functionality. | Why did the water leak happen in pump 33C? | Continuous operation under harsh conditions likely led to accelerated corrosion.
434 | 2019-09-30 | 30958723 | 90127934 | Excessive vibration in feed pump A7 | S5PC -5PCE2-PUMA | * **************Incident Description************** * Notification 000030958723 Details * *********************************************************** * 09/30/2019 15:28:36 INCIDENT REPORT (INCIDENT REPORT) * Report submitted by: David Pearson ENTITY\INCIDENT: * * CONDITION DESCRIPTION/LOCATION (THE INAPPROPRIATE ACTION AND ITS NEGATIVE EFFECT/INCLUDE A DETAILED LOCATION DESCRIPTION): * During normal operation at 2350 on 09/30, feed pump A7 was detected with excessive vibration. Based on onsite measurements, vibration was higher than nominal levels. Strain sensors on the pump casing reported stresses above normal. Immediate shutdown was done from Unit 5 Control Room. No adverse effects were identified immediately after shutdown. * * ACTIVITIES, PROCESSES, PROCEDURES INVOLVED: * S5.OP-FE.A7-0001, S5.OP-SO.FE-0001 * * WHY DID CONDITION HAPPEN? * Possible wear and tear or internal damage to the pump. * * CONSEQUENCES: * Excessive vibration could have led to pump failure, potentially causing a disruption in the plant process. * * REQUIREMENTS IMPACTED: * Imperative to ensure the stability of feed pumps for smooth plant operation. * * ADVERSE PHYSICAL CONDITIONS: * Excessive vibration in Pump A7, possible mechanical damage * * WHO WAS NOTIFIED: * Plant Manager, Operations Supervisor * * KNOWLEDGEABLE INDIVIDUALS: * Operations Supervisor, David Pearson, Engineers * * REPEAT OR SIMILAR CONDITION: * No * * IMMEDIATE ACTIONS AND RECOMMENDED ACTIONS: * Maintenance team ordered to conduct an in-depth inspection. If required, replacing or repairing the pump. * 10/01/2019 08:00:17 DAVID PEARSON (INCIDENT) * Investigation underway: teardown of A7 pump initiated, aiming to identify the source of vibration. | What immediate action was taken when the excessive vibration of pump A7 was detected? | Immediate shutdown was done from Unit 5 Control Room.
435 | 2020-12-20 | 40782563 | 80225234 | Unusual vibration from 7B Pump | S3CW -3CWE8 | * **************Incident Description************** * Notification 000040782563 Details * *********************************************************** * 12/20/2020 13:29:00 INCIDENT REPORT (INCIDENT REPORT) * Report submitted by: Taylor Johnson 987-654-3210 ENTITY\INCIDENT: * * CONDITION DESCRIPTION/LOCATION (THE INAPPROPRIATE ACTION AND ITS NEGATIVE EFFECT/INCLUDE A DETAILED LOCATION DESCRIPTION): * During a routine inspection observed unusual vibrations in 7B Pump. Initial tests revealed no clear causes. There were no significant discrepancies in temperatures, pressures or power draw. The pump had been refurbished under work order 80224278 with no reported issues. * * ACTIVITIES, PROCESSES, PROCEDURES INVOLVED: * Routine inspection and vibration measurements, S2.OP-SO.CW-0010 procedure. * * WHY DID CONDITION HAPPEN? * The initial cause of the vibrations is unclear. Potential issues include imbalances, wear or damage on the components. * * CONSEQUENCES: * If left unchecked, vibrations could lead to internal damage and decreased performance in the pump. * * REQUIREMENTS IMPACTED: * Normal operation could be potentially affected. * * ADVERSE PHYSICAL CONDITIONS: * Unusual vibrations from the 7B Pump. * * WHO WAS NOTIFIED: * Immediate Supervisor, Engineering Team * * KNOWLEDGEABLE INDIVIDUALS: * Engineering Team, Maintenance Crew * * REPEAT OR SIMILAR CONDITION: * No, this is the first instance. * * IMMEDIATE ACTIONS AND RECOMMENDED ACTIONS: * Further investigation is required to pinpoint the cause of the vibrations. Maintenance team has been drafted to inspect the integrity of the 7B Pump. * 12/26/2020 09:45:00 KELLY SMITH (INCIDENT) * After a thorough inspection, it was found that a misalignment in the pump's internal rotor was causing the vibrations. Repair has been done and the pump is now functioning normal with no unusual vibrations. | What was the cause of the unusual vibrations in the 7B Pump and what action was taken to resolve it? | After a thorough inspection, it was found that a misalignment in the pump's internal rotor was causing the vibrations. Repair has been done and the pump is now functioning normal with no unusual vibrations.
436 | 2019-09-15 | 30971536 | 80258901 | 18B Compressor system failure | S4AC -4ACE2 | * **************Incident Description************** * Notification 000030971536 Details * *********************************************************** * 09/15/2019 08:45:31 INCIDENT REPORT (INCIDENT REPORT) * Report submitted by: Ethan Walker ENTITY\INCIDENT: * * CONDITION DESCRIPTION/LOCATION (THE INAPPROPRIATE ACTION AND ITS NEGATIVE EFFECT/INCLUDE A DETAILED LOCATION DESCRIPTION): * At 0800 on 9/15/19, the operator noted that 18B Compressor system had failed. The compressor was shut down immediately. Initial inspection revealed a potential issue with the cooling system, showing signs of leakage and possible overheating. The system is currently being analyzed for detailed faults. * * ACTIVITIES, PROCESSES, PROCEDURES INVOLVED: * S4.OP.AB.AC-0002, S4.OP-SO.AC-0001 * * WHY DID CONDITION HAPPEN? * Preliminary inspection suggests faults in the cooling system, possibly due to wear and tear. * * CONSEQUENCES: * Potential for decreased compressor system functionality, leading to inefficiencies. Costs associated with repair or replacement. * * REQUIREMENTS IMPACTED: * Normal operation of compressor * * ADVERSE PHYSICAL CONDITIONS: * Severe potential overheating and leakage in the cooling system * * WHO WAS NOTIFIED: * Maintenance and Control Room * * KNOWLEDGEABLE INDIVIDUALS: * Clark, Hamilton, Davis * * REPEAT OR SIMILAR CONDITION: * No, this is the first occurrence * * IMMEDIATE ACTIONS AND RECOMMENDED ACTIONS: * Run diagnostics, document findings, and perform necessary repairs or replacements. * 09/15/2019 14:30:25 ETHAN WALKER (INCIDENT) * Maintenance team has initiated the diagnostics and awaiting for results. At this stage, it's crucial to establish the root cause for the right corrective measures. | What immediate actions were recommended following the compressor system failure? | Run diagnostics, document findings, and perform necessary repairs or replacements.
437 | 2020-02-17 | 30853294 | 80346907 | 16B PUMP reduction in flow rate | S2CW -2CWE7 | * **************Incident Description************** * Notification 000030853294 Details * ************************************************************* * 02/17/2020 10:23:47 INCIDENT REPORT (INCIDENT REPORT) * Report submitted by: Tim Grey ENTITY\INCIDENT: * * CONDITION DESCRIPTION/LOCATION: (THE INAPPROPRIATE ACTION AND ITS NEGATIVE EFFECT/INCLUDE A DETAILED LOCATION DESCRIPTION): * At approximately 1020 on 2/17/20, the operation team identified a reduction in the flow rate of 16B Pump during routine operation. The reduction was identified through monitoring system anomaly and the pump was shut off immediately. In the absence of any external signs of damage or unusual noise from the pump, the flow disruption could potentially be due to an internal fault or clog. * *ACTIVITIES, PROCESSES, PROCEDURES INVOLVED: * S3.OP.AB-CW-0002, S3.OP-SO.CW-0003 * * WHY DID CONDITION HAPPEN: * The exact reason is unclear, although issues with internal components or clogging due to foreign substances can't be ruled out. * *CONSEQUENCES: * Decreased operational efficiency, potential for pump damage, and the risk of unexpected downtime. * * REQUIREMENTS IMPACTED: * Normal operation of 16B Pump, impacting the overall process continuity. * * ADVERSE PHYSICAL CONDITIONS: * No immediate physical conditions observed, but potential for internal pump damage. * * WHO WAS NOTIFIED: * Maintenance Team, Operation Supervisor, Control Room * * KNOWLEDGEABLE INDIVIDUALS: * Operation Team, Maintenance Team, HSE Representatives, Drake, Philips * * REPEAT OR SIMILAR CONDITION: * No, this is the first occurrence of such event with 16B Pump. * * IMMEDIATE ACTIONS AND RECOMMENDED ACTIONS: * Immediate action needed to investigate the internal parts of the 16B Pump for any obstruction or damage. Following the initial assessment, repair or replacement of components may be required. * * Updated: TIM GREY 02.17.2020 14:29:19 * | What were the immediate actions recommended after identifying the issue with the 16B Pump? | Immediate action needed to investigate the internal parts of the 16B Pump for any obstruction or damage. Following the initial assessment, repair or replacement of components may be required.
438 | 2021-03-18 | 30985467 | 80462189 | 18B Pump severe vibration post overhaul | S4CW -4CWE8 | * **************Incident Description************** * Notification 000030985467 Details * *********************************************************** * 03/18/2021 16:37:00 INCIDENT REPORT (INCIDENT REPORT) * Report submitted by: Daniel Green ENTITY\INCIDENT: * * CONDITION DESCRIPTION/LOCATION (THE INAPPROPRIATE ACTION AND ITS NEGATIVE EFFECT/INCLUDE A DETAILED LOCATION DESCRIPTION): * After the completion of scheduled maintenance of 18B pump under work order 80439872, the operator observed severe vibration during operation. The pump was immediately shutdown as per S4.OP-AB.CW-0002 Emergency Shutdown Procedure to avoid any potential damage. * * ACTIVITIES, PROCESSES, PROCEDURES INVOLVED: * S4.OP-AB.CW-0002 Emergency Shutdown and S4.OP-SO.CW-0002 Start-up * * WHY DID CONDITION HAPPEN? * Initial investigation revealed misalignment in pump assembly post-maintenance. * * CONSEQUENCES: * Potential severe damage to the pump if left operating under severe vibrations. * * REQUIREMENTS IMPACTED: * Pump operation and delivery North side. * * ADVERSE PHYSICAL CONDITIONS: * Severe vibration in 18B pump post-maintenance. * * WHO WAS NOTIFIED: * Control Room, Maintenance Team. * * KNOWLEDGEABLE INDIVIDUALS: * Maintenance Supervisor, Operator. * * REPEAT OR SIMILAR CONDITION: * No, first such incident. * * IMMEDIATE ACTIONS AND RECOMMENDED ACTIONS: * Maintenance team to inspect 18B Pump, ensure alignment and other parameters as per overhaul protocol. If necessary, the pump assembly should be rechecked and validated. * 03/20/2021 10:28:52 JANE DOE (INCIDENT) * The investigation concluded that the vibration was due to minuscule misalignment during assembly. The pump has been realigned, tested, and returned to normal operation. Necessary documentation for the misalignment correction has been updated in work order 80462189. | What immediate actions were taken following the detection of severe vibrations in the 18B pump? | Maintenance team to inspect 18B Pump, ensure alignment and other parameters as per overhaul protocol. If necessary, the pump assembly should be rechecked and validated.
439 | 2015-11-25 | 30712513 | 80185210 | Unusual spike in 14D Pump pressure | S4CW -4CWE8 | * **************Incident Description************** * Notification 000030712513 Details * *********************************************************** * 11/25/2015 16:22:11 INCIDENT REPORT (INCIDENT REPORT) * Report submitted by: Donald White ENTITY\INCIDENT: * * CONDITION DESCRIPTION/LOCATION (THE INAPPROPRIATE ACTION AND ITS NEGATIVE EFFECT/INCLUDE A DETAILED LOCATION DESCRIPTION): * During regular monitoring, it was noted that the pressure in Pump 14D experienced an unusual spike of 18 psi. This irregularity is not normal for 14D pump. Investigations into the incident have commenced. * * ACTIVITIES, PROCESSES, PROCEDURES INVOLVED: * Regular on-site inspection and monitoring of pump pressures. * * WHY DID CONDITION HAPPEN? * The cause of the pressure spike is unknown at the moment. Further investigation is required to determine the source of this irregularity. * * CONSEQUENCES: * The sudden increase in pressure could potentially lead to internal damage or leakage which could disrupt operation cycle. * * REQUIREMENTS IMPACTED: * Possibility of disrupting the normal pump operations. * * ADVERSE PHYSICAL CONDITIONS: * Unexplained spike in pump pressure. * * WHO WAS NOTIFIED: * Supervisor, Incident Team * * KNOWLEDGEABLE INDIVIDUALS: * Supervisor, Incident Team, Engineering Team * * REPEAT OR SIMILAR CONDITION: * No, this is the first occurrence of its kind on the 14D Pump. * * IMMEDIATE ACTIONS AND RECOMMENDED ACTIONS: * Initiate immediate inspection of the pump. If the issue remains unresolved, bring in experts and verify any potential faults or failures. * 11/26/2015 09:15:32 DONALD WHITE (INCIDENT) * First inspection showed no apparent physical damage to the pump. The issue is still under investigation. Further expertise is advised for detailed inspection. | What was the anomaly identified during the regular monitoring of Pump 14D? | It was noted that the pressure in Pump 14D experienced an unusual spike of 18 psi. This irregularity is not normal for 14D pump.
440 | 2020-05-10 | 30815672 | 80325641 | Vibration at Pump 17B post overhaul | S4CW -4CWE7 | * **************Incident Description************** * Notification 000030815672 Details * *********************************************************** * 05/10/2020 15:32:15 INCIDENT REPORT (INCIDENT REPORT) * Report submitted by: George Allen ENTITY\INCIDENT: * * CONDITION DESCRIPTION/LOCATION (THE INAPPROPRIATE ACTION AND ITS NEGATIVE EFFECT/INCLUDE A DETAILED LOCATION DESCRIPTION): * Notification 30815672 was created on 5/10/20 at 1237 hours upon report by operator that restarted 17B Pump was displaying abnormal vibration. A detailed inspection was prompted by this condition, which may threaten the pump functionality. * * ACTIVITIES, PROCESSES, PROCEDURES INVOLVED: * Pump 17B Restart, S4.OP-AB.CW-0007 * * WHY DID CONDITION HAPPEN? * Unclear at this time, potentially due to incorrect installation during overhaul. * * CONSEQUENCES: * Potential pump failure, disruption of normal operation * * REQUIREMENTS IMPACTED: * Pump operation, Equipment reliability * * ADVERSE PHYSICAL CONDITIONS: * Abnormal Vibrations from the 17B Pump * * WHO WAS NOTIFIED: * Operations Supervisor, Maintenance Department * * KNOWLEDGEABLE INDIVIDUALS: * George Allen, Maintenance Supervisor, Operations Team * * REPEAT OR SIMILAR CONDITION: * No * * IMMEDIATE ACTIONS AND RECOMMENDED ACTIONS: * Stop operation and conduct a detailed inspection on 17B, inspect installation. * * Updated: GEORGE ALLEN 05.10.2020 16:51:22 * ------------------------------------------------------------ * 05/11/2020 11:56:43 JOHN DOE (NUSER) * The inspection revealed that misalignment during installation after the pump overhaul was causing the abnormal vibrations. The pump was realigned and the vibrations ceased. The pump has now been put back into service following successful operational testing. | What was the immediate remedial action suggested when abnormal vibrations were observed in Pump 17B? | Stop operation and conduct a detailed inspection on 17B, inspect installation.
441 | 2020-09-15 | 30982571 | 90239486 | Abrupt Voltage dip in 14B motor | S5EL -5ELE4 | * **************Incident Description************** * Notification 000030982571 Details * *********************************************************** * 09/15/2020 10:21:45 INCIDENT REPORT (INCIDENT REPORT) * Report submitted by: Emily Johnson ENTITY\INCIDENT: * * 1) CONDITION DESCRIPTION/LOCATION (THE INAPPROPRIATE ACTION AND ITS NEGATIVE EFFECT/INCLUDE A DETAILED LOCATION DESCRIPTION): * At 0930 on 15/09/20, it was reported that 14B Motor experienced a sudden drop in voltage while operating under normal conditions. The motor was brought down to avoid additional equipment damage. The dip in voltage was witnessed on the central monitoring system. Staff on site confirmed the dip with handheld equipment. The cause of the condition is currently unknown. * * 2) ACTIVITIES, PROCESSES, PROCEDURES INVOLVED: * S5.OP.EL.0004, S5.OP.EL.1231 * * 3) WHY DID CONDITION HAPPEN: * Cause is unknown at this point. Investigations are ongoing. * * 4) CONSEQUENCES: * Potential damage to motor and surrounding equipment, leading to downtime and reduced operational efficiency. * * 5) REQUIREMENTS IMPACTED: * Normal operations were affected, critical power supply equipment suddenly went offline. * * 6) ADVERSE PHYSICAL CONDITION: * Sharp drop in voltage recorded in 14B Motor. * * 7) WHO WAS NOTIFIED: * Control Room, Electrical Department, Safety Department * * 8) KNOWLEDGEABLE INDIVIDUALS: * Baker, Cooper, Green * * 9) REPEAT OR SIMILAR CONDITION: * No previous conditions of this nature have been recorded. * * 10) IMMEDIATE AND RECOMMENDED ACTIONS: * Electricians to assess and repair the 14B Motor, Operations team to investigate the cause of voltage fluctuation. * * Updated: EMILY JOHNSON 09.15.2020 11:30:25 * ------------------------------------------------------------ * 09/28/2020 08:45:33 | What were the potential consequences of the sudden voltage drop in the 14B Motor? | Potential damage to motor and surrounding equipment, leading to downtime and reduced operational efficiency.
442 | 2020-10-20 | 30970321 | 80210218 | Aberrant vibration on 10B cooler motor | S2CW -2CWF4-B8MD | * **************Incident Description************** * Notification 000030970321 Details * *********************************************************** * 10/20/2020 15:23:12 INCIDENT REPORT (INCIDENT REPORT) * Report submitted by: Kate Johnson 147-963-8520 * ENTITY\INCIDENT: * * CONDITION DESCRIPTION/LOCATION (THE INAPPROPRIATE ACTION AND ITS NEGATIVE EFFECT/INCLUDE A DETAILED LOCATION DESCRIPTION): * During regular maintenance checks, a high vibration was noted on the 10B cooler motor. The increase in vibration has been steady since the last check and is now outside the recommended limits. The cooler was shut down to prevent damage and a detailed inspection is initiated. * * ACTIVITIES, PROCESSES, PROCEDURES INVOLVED: * Regular Maintenance check * * WHY DID CONDITION HAPPEN? * Currently not identified, potential causes could be a misalignment, a faulty bearing or wear and tear. * * CONSEQUENCES: * Further use of the motor can cause severe damage. * * REQUIREMENTS IMPACTED: * Normal Operation * * ADVERSE PHYSICAL CONDITIONS: * Abnormal vibration on 10B cooler motor * * WHO WAS NOTIFIED: * Maintenance Supervisor, INCIDENT TEAM * * KNOWLEDGEABLE INDIVIDUALS: * Incident Team * * REPEAT OR SIMILAR CONDITION: * No * * IMMEDIATE ACTIONS AND RECOMMENDED ACTIONS: * Motor has been shut off. A detailed review of the cooler installation will be conducted including checks of alignment and inspection of the motor and rotary elements. Recommendations will be undertaken based on the inspection. * 10/21/2020 09:02:42 LISA SMITH (INCIDENT) * The inspection revealed that the main bearing of the motor was damaged. The bearing and motor were replaced, the alignment was checked and found to be correct. The cooler has been restarted and is operating within the expected parameters. | What immediate and recommended actions were taken due to the high vibration on the 10B cooler motor? | Motor has been shut off. A detailed review of the cooler installation will be conducted including checks of alignment and inspection of the motor and rotary elements. Recommendations will be undertaken based on the inspection. The inspection revealed that the main bearing of the motor was damaged. The bearing and motor were replaced, the alignment was checked and found to be correct. The cooler has been restarted and is operating within the expected parameters.
443 | 2022-01-10 | 30987201 | 80223456 | 9C Pump unexpected stoppage | S1CW -1CWE7 | * **************Incident Description************** * Notification 000030987201 Details * *********************************************************** * 01/10/2022 07:47:07 INCIDENT REPORT (INCIDENT REPORT) * Report submitted by: Robert Smith ENTITY\INCIDENT: * * CONDITION DESCRIPTION/LOCATION (THE INAPPROPRIATE ACTION AND ITS NEGATIVE EFFECT/INCLUDE A DETAILED LOCATION DESCRIPTION): * During an operation earlier today, the 9C Pump unexpectedly stopped working. The incident occurred at Station S1CW -1CWE7. All warning lights were active, and the control system indicated a severe malfunction. The initial checks didn't identify the failure. * * ACTIVITIES, PROCESSES, PROCEDURES INVOLVED: * Daily operation of the 9C Pump, diagnostic check. * * WHY DID CONDITION HAPPEN? * At this stage, the cause of the condition is unclear. The last maintenance was performed less than a month ago and no potential issues were reported then. * * CONSEQUENCES: * Imminent failure, possible system-wide disruption if the pump outage continues for an extended period, halt in operations. * * REQUIREMENTS IMPACTED: * Pump operations and system function. * * ADVERSE PHYSICAL CONDITIONS: * Sudden pump stoppage, warning lights active. * * WHO WAS NOTIFIED: * Maintenance Supervisor, Control Room, Incident Response Team. * * KNOWLEDGEABLE INDIVIDUALS: * Maintenance Team, System Operators. * * REPEAT OR SIMILAR CONDITION: * No, this is the first occurrence. * * IMMEDIATE ACTIONS AND RECOMMENDED ACTIONS: * Immediate inspection and diagnosis of the pump followed by necessary repairs or replacement. Review the maintenance and operation processes for potential updating. * 01/11/2022 10:22:44 ELIZABETH JOHNS (INCIDENT) * Inspection is underway; however, preliminary investigation indicates a potential electrical failure. Replacement parts have been ordered. I recommend a comprehensive audit of all similar pump systems for similar issues. | What immediate actions were recommended following the pump malfunction incident? | Immediate inspection and diagnosis of the pump followed by necessary repairs or replacement. Review the maintenance and operation processes for potential updating.
444 | 2019-10-01 | 30941276 | 80512356 | Overheating of Fuse Box M12 | S4E-4EL1-FBBX | * **************Incident Description************** * Notification 000030941276 Details * *********************************************************** * 10/01/2019 07:32:44 INCIDENT REPORT (INCIDENT REPORT) * Report submitted by: Samantha Green ENTITY\INCIDENT: * * CONDITION DESCRIPTION/LOCATION (THE INAPPROPRIATE ACTION AND ITS NEGATIVE EFFECT/INCLUDE A DETAILED LOCATION DESCRIPTION): * During early morning rounds, operator on shift noticed an unusual overheating condition on Fuse Box M12. Immediate shut-down was ordered from the Control Room. Subsequent inspection by Safety and Maintenance team revealed no fire but there was moderate smoke discharge. FuseBox M12 showed signs of external damage. S4.OP-AB.EB-0001 FuseBox Abnormality was initiated due to the emergency shutdown of M12 FuseBox. * * ACTIVITIES, PROCESSES, PROCEDURES INVOLVED: * S4.OP.AB-EB-0001, S4.OP-SO.EB-0001 * * WHY DID CONDITION HAPPEN: * Unknown at present, previous similar incidents involved short-circuiting. * * CONSEQUENCES: * Potential fire hazard and interruption of electrical service if not addressed promptly. * * REQUIREMENTS IMPACTED: * Routine operation of electrical circuits * * ADVERSE PHYSICAL CONDITION: * Overheating issue of M12 Fuse box, possible internal damage * * WHO WAS NOTIFIED: * Control Room, Safety, Maintenance, Supervisor * * KNOWLEDGEABLE INDIVIDUALS: * Green, Black, Cooper * * REPEAT OR SIMILAR CONDITION: * Unknown * * IMMEDIATE AND RECOMMENDED ACTIONS: * Maintenance to check and carry out necessary repairs on M12 FuseBox. * * Updated: SAMANTHA GREEN 10.01.2019 08:32:12 * ------------------------------------------------------------ * 10/07/2019 09:12:43 JOHN DOE (NUSER) * An inspection confirmed a short-circuit caused the overheating. The fusebox was repaired, electrical safety checks completed and it is now back under | What was the immediate action taken when the operator noticed the unusual overheating condition on Fuse Box M12? | Immediate shut-down was ordered from the Control Room.
445 | 2018-10-09 | 30775302 | 80255897 | 16B Pump Oil Leak | S4CW -4CWE6-OILG | * **************Incident Description************** * Notification 000030775302 Details * *********************************************************** * 10/09/2018 07:13:15 INCIDENT REPORT (INCIDENT REPORT) * Report submitted by: Sam Wilson 987-654-3210 ENTITY\INCIDENT: * CONDITION DESCRIPTION/LOCATION (THE INAPPROPRIATE ACTION AND ITS NEGATIVE EFFECT/INCLUDE A DETAILED LOCATION DESCRIPTION): * During a routine inspection, the 16B Pump was observed leaking oil. The pump was immediately shutdown and serviced. The leak was traced to a damaged seal within the pump. * * ACTIVITIES, PROCESSES, PROCEDURES INVOLVED: * Regular maintenance check. * * WHY DID CONDITION HAPPEN? * A worn-out seal was identified as the potential cause of the leak. * * CONSEQUENCES: * Increase in operating cost and decrease in pump efficiency. * * REQUIREMENTS IMPACTED: * Pump operation and maintenance routine. * * ADVERSE PHYSICAL CONDITIONS: * Oil leakage from the 16B Pump * * WHO WAS NOTIFIED: * Maintenance Team, Safety Department * * KNOWLEDGEABLE INDIVIDUALS: * Maintenance Team * * REPEAT OR SIMILAR CONDITION: * No, this is the first occurrence. * * IMMEDIATE ACTIONS AND RECOMMENDED ACTIONS: * Pump was immediately shut down. Seal needs to be replaced and pump should undergo a check-up to prevent future leaks. * * 10/09/2018 16:48:05 SAM WILSON (INCIDENT) * Seal replaced and pump thoroughly inspected. The system is now ready for operation and will be closely monitored for any similar issues. | What was the identified cause of the oil leak in the 16B Pump? | A worn-out seal was identified as the potential cause of the leak.
446 | 2021-09-15 | 30938512 | 80234567 | Overheating of turbine 5A | S4TR -4TRE5 | * *************Incident Description************** * Notification 000030938512 Details * *********************************************************** * 09/15/2021 16:32:12 INCIDENT REPORT (INCIDENT REPORT) * Report submitted by: Samuel Harper ENTITY\INCIDENT: * * CONDITION DESCRIPTION/LOCATION (THE INAPPROPRIATE ACTION AND ITS NEGATIVE EFFECT/INCLUDE A DETAILED LOCATION DESCRIPTION): * During a regular inspection, elevated temperature measurements were recorded from Turbine 5A. On further investigation, an abnormal noise was identified coming from the turbine. Prompt shutdown was initiated. Clear indications of external burn marks were visible on inspection. Possible internal damage suspected. * * ACTIVITIES, PROCESSES, PROCEDURES INVOLVED: * S4.OP.AB-TR-0005, S4.OP-SO.TR-0005 routine turbine check. * * WHY DID CONDITION HAPPEN? * Need to inspect further to establish the exact reason. However, issues like wear and tear, internal blockage or possible shaft misalignment could be potential reasons. * * CONSEQUENCES: * If not addressed, this could lead to reduced turbine efficiency and potential failure, impacting overall plant operations. * * REQUIREMENTS IMPACTED: * Normal Machinery Operations * * ADVERSE PHYSICAL CONDITIONS: * Overheating and abnormal noise from Turbine 5A * * WHO WAS NOTIFIED: * Control Room Supervisor, Engineering Team * * KNOWLEDGEABLE INDIVIDUALS: * Williams, Johnson, Rogers * * REPEAT OR SIMILAR CONDITION: * No * * IMMEDIATE ACTIONS AND RECOMMENDED ACTIONS: * Prompt shutdown of Turbine 5A, initiate full scale mechanical inspection, clear the turbine internals and examine the shaft for any possible misaligned positions. * 09/18/2021 10:14:32 SAMUEL HARPER (INCIDENT) * The issue was identified as internal debris accumulation due to wear and tear. The debris was cleared, internal components have been replaced. Turbine 5A is now back in operation with all parameters normal. | What was the identified issue with Turbine 5A and what immediate actions were taken? | The issue was identified as internal debris accumulation due to wear and tear. The debris was cleared, internal components have been replaced. Turbine 5A is now back in operation with all parameters normal.
447 | 2022-03-17 | 30954062 | 90205631 | Oil Leakage at Pump 33B | S4CW -4CWE7 | * **************Incident Description************** * Notification 000030954062 Details * *********************************************************** * 03/17/2022 14:35:36 INCIDENT REPORT (INCIDENT REPORT) * Report submitted by: Peter Thompson (PT) ENTITY\INCIDENT: * * CONDITION DESCRIPTION/LOCATION : * During a routine inspection, 33B pump showed signs of a potential internal oil leakage. The area around the pump was stained with lubrication oil. Sensing the potential of a bigger issue, immediate measures were taken. * * ACTIVITIES, PROCESSES, PROCEDURES INVOLVED: * S4.OP.AB-CW-0007, S4.OP-SO.CW-0004 * * WHY DID CONDITION HAPPEN? * The reason could be due to wear and tear over time, or a failure in the pump sealing mechanism, which needs further investigation. * * CONSEQUENCES: * Potential risk of a pump failure, operator safety, and environmental impact. * * REQUIREMENTS IMPACTED: * Normal pump operation, safety and environmental regulations * * ADVERSE PHYSICAL CONDITIONS: * Visible oil stain surrounding the pump, potential internal pump damage * * WHO WAS NOTIFIED: * Supervisor, Safety Officer, Maintenance Team * * KNOWLEDGEABLE INDIVIDUALS: * Thompson, Lee, Johnston * * REPEAT OR SIMILAR CONDITION: * No, first instance of such issue * * IMMEDIATE ACTIONS AND RECOMMENDED ACTIONS: * Pump 33B has been isolated and prepared for a detailed investigation and repair by the maintenance team. Recommendation to review the maintenance history of pump 33B and the maintenance procedure S4.OP-SO.CW-0004. * Updated: PETER THOMPSON 03.17.2022 16:12:20 * ------------------------------------------------------------ * 03/19/2022 10:17:25 PAUL WILLIAMS (NUSER) * Maintenance team performed the operation, replacement of faulty seal was carried out. Post-maintenance inspection did not reveal any additional issues. 33B Pump now back to normal operation. | What immediate action was taken after discovering the potential oil leakage in pump 33B? | Pump 33B has been isolated and prepared for a detailed investigation and repair by the maintenance team. Recommendation to review the maintenance history of pump 33B and the maintenance procedure S4.OP-SO.CW-0004.
448 | 2019-05-07 | 31002018 | 90192945 | Segment leak in 18B Heat Exchanger | S4HT - 4CWE8 | * **************Incident Description************** * Notification 000031002018 Details * *********************************************************** * 05/07/2019 10:34:55 INCIDENT REPORT (INCIDENT REPORT) * Report submitted by: Robert Frost ENTITY\INCIDENT: * CONDITION DESCRIPTION/LOCATION (THE INAPPROPRIATE ACTION AND ITS NEGATIVE EFFECT/INCLUDE A DETAILED LOCATION DESCRIPTION): * While performing a pressure test of the 18B Heat Exchanger, a segment leak was observed. A shutdown was initiated for inspection and repair. The leak has potential to reduce the effectiveness of the heat exchange process if left unchecked. * * ACTIVITIES, PROCESSES, PROCEDURES INVOLVED: * Pressure testing under Procedure S4.OP-HT-XC-0003. * * WHY DID CONDITION HAPPEN? * The exact cause is unknown. The leak may be due to segment wear or material degradation. * * CONSEQUENCES: * Potential for reduced efficiency of heat exchanger, potential for coolant leakage. * * REQUIREMENTS IMPACTED: * Operability of 18B Heat Exchanger. * * ADVERSE PHYSICAL CONDITIONS: * Leak in a segment of the 18B Heat Exchanger. * * WHO WAS NOTIFIED: * Supervisor, Maintenance Team. * * KNOWLEDGEABLE INDIVIDUALS: * Supervisor, Maintenance Team, Mechanic, Engineer. * * REPEAT OR SIMILAR CONDITION: * Yes, minor leaks have been detected and fixed before. * * IMMEDIATE ACTIONS AND RECOMMENDED ACTIONS: * Shutdown of 18B Heat Exchanger, investigation, and repair as necessary under Procedure S4.OP-HT-XC-0003. * 05/07/2019 15:15:32 ROBERT FROST (INCIDENT) * A maintenance order was created for the repair of 18B Heat Exchanger. Leak was repaired and the exchanger is back in service. Procedure revision S4.OP-HT-XC-0004 was released to include additional checks for segment leaks during routine testing and procedures to ensure they are attended to timely. | What actions were taken following the detection of a leak in the 18B Heat Exchanger? | Shutdown of 18B Heat Exchanger, investigation, and repair as necessary under Procedure S4.OP-HT-XC-0003. A maintenance order was created for the repair of 18B Heat Exchanger. Leak was repaired and the exchanger is back in service. Procedure revision S4.OP-HT-XC-0004 was released to include additional checks for segment leaks during routine testing and procedures to ensure they are attended to timely.
449 | 2019-03-15 | 30970826 | 80202030 | Leak detected in 8B Pipeline | T5PL -5PLB2 | * **************Incident Description************** * Notification 000030970826 Details * *********************************************************** * 03/15/2019 08:30:12 INCIDENT REPORT (INCIDENT REPORT) * Report submitted by: Robert Thompson 979-654-3210 ENTITY\INCIDENT: * * CONDITION DESCRIPTION/LOCATION (THE INAPPROPRIATE ACTION AND ITS NEGATIVE EFFECT/INCLUDE A DETAILED LOCATION DESCRIPTION): * During a daily inspection, it was identified that there was a leak in the 8B Pipeline. Pipeline was immediately shut off from Unit 5 Control Room in order to prevent further leakage. The leaked fluid was collected and sealed on site to prevent environmental hazards. No fire was reported as immediate actions were taken. * * ACTIVITIES, PROCESSES, PROCEDURES INVOLVED: * T5.OP-AB.PP-0025, T5.OP-SO.PP-0025 * * WHY DID CONDITION HAPPEN: * Unknown, inspection for damage or corrosion is needed. * * CONSEQUENCES: * Temporary unavailability of 8B Pipeline, potential environmental hazard if not managed effectively. * * REQUIREMENTS IMPACTED: * Daily operations and delivery timelines. * * ADVERSE PHYSICAL CONDITIONS: * Leakage in 8B Pipeline, possibly due to internal damages or corrosions. * * WHO WAS NOTIFIED: * Control Room, Incident Team, Environmental Management * * KNOWLEDGEABLE INDIVIDUALS: * Thompson, Patel, Williams * * REPEAT OR SIMILAR CONDITION: * No, first occurrence of such incident. * * IMMEDIATE AND RECOMMENDED ACTIONS: * Engineering team to perform a thorough inspection of 8B Pipeline for any damages or corrosions and repair as necessary. * * Updated: ROBERT THOMPSON 03.15.2019 09:45:19 * ------------------------------------------------------------ * 03/20/2019 10:43:00 ELIZA JONES (NUSER) * After thorough investigation, it was identified that corrosion was the cause of the leak. The pipeline has been repaired and preventive measures, such as implementation of corrosion inhibitor, | What was the cause of the leak in the 8B Pipeline? | After thorough investigation, it was identified that corrosion was the cause of the leak.
450 | 2019-04-15 | 30872146 | 80987650 | 23B pump vibration post overhaul | S4CW -4CWE5 | * **************Incident Description************** * Notification 000030872146 Details * *********************************************************** * 04/15/2019 14:50:00 INCIDENT REPORT (INCIDENT REPORT) * Report submitted by: Thomas Green ENTITY\INCIDENT: * * CONDITION DESCRIPTION/LOCATION (THE INAPPROPRIATE ACTION AND ITS NEGATIVE EFFECT/INCLUDE A DETAILED LOCATION DESCRIPTION): * During the onsite review post major maintenance on 23B pump under work order 80987650 completed in March 2019, it was noted that pump was vibrating more than usual during operations. This is a concern as it could lead to early failure of the pump and even trip the circuit breaker. * * ACTIVITIES, PROCESSES, PROCEDURES INVOLVED: * Completed major maintenance, under S3.OP-SO.CW-0002. * * WHY DID CONDITION HAPPEN? * Possible misalignment of rotating elements or imbalance in rotation during repair. * * CONSEQUENCES: * Increased vibration can lead to failure of the pump motor leading to unplanned shutdown. * * REQUIREMENTS IMPACTED: * Achieving stable and continuous pump operations. * * ADVERSE PHYSICAL CONDITIONS: * High vibration of the pump motor. * * WHO WAS NOTIFIED: * Supervisor, Maintenance Team, Operations * * KNOWLEDGEABLE INDIVIDUALS: * Maintenance Team, Engineering group * * REPEAT OR SIMILAR CONDITION: * No, this is first time post maintenance or any major overhaul replacement on this pump. * * IMMEDIATE ACTIONS AND RECOMMENDED ACTIONS: * Assembly of motor and pump drive train to be checked and any alignment issues should be corrected. Continue to monitor vibration levels. * 04/18/2019 10:30:27 THOMAS GREEN (INCIDENT) * Verification of alignment completed under work order 80997102. Imbalance corrected with replacing worn-out parts. Vibration returned to normal. Recommend revisiting the maintenance procedure S4.OP-SO.CW-0003 for avoiding similar miss alignments in future. | What immediate actions were taken to correct the vibrating issue of the pump? | Assembly of motor and pump drive train to be checked and any alignment issues should be corrected. Continue to monitor vibration levels. Verification of alignment completed under work order 80997102. Imbalance corrected with replacing worn-out parts. Vibration returned to normal.
451 | 2017-09-30 | 30765314 | 80231495 | Unexpected Power Interruption to 17A Motor | S4CW -4CWE1 | * **************Incident Description************** * Notification 000030765314 Details * *********************************************************** * 09/30/2017 14:35:17 INCIDENT REPORT (INCIDENT REPORT) * Report submitted by: Samuel Williams ENTITY\INCIDENT: * * CONDITION DESCRIPTION/LOCATION (THE INAPPROPRIATE ACTION AND ITS NEGATIVE EFFECT/INCLUDE A DETAILED LOCATION DESCRIPTION): * At 1330 hours, the operator reported an unexpected power interruption to the 17A motor. The motor was immediately shut down to prevent further damage. There was no fire or other safety related hazards detected. A routine inspection revealed a temporary drop in voltage supply to the motor. Order initiated to resolve the issue. * * ACTIVITIES, PROCESSES, PROCEDURES INVOLVED: * Routine operation, S4.OP.AB-CW-0012 * * WHY DID CONDITION HAPPEN? * An unexpected drop in supply voltage, root cause still under investigation. * * CONSEQUENCES: * Potential damage to motor if operation had continued under low voltage. * * REQUIREMENTS IMPACTED: * Normal operation of 17A motor. * * ADVERSE PHYSICAL CONDITIONS: * No, timely shutdown prevented physical damage * * WHO WAS NOTIFIED: * Control Room, Maintenance Department * * KNOWLEDGEABLE INDIVIDUALS: * Operators, Maintenance Team, Electrical Engineers * * REPEAT OR SIMILAR CONDITION: * No * * IMMEDIATE ACTIONS AND RECOMMENDED ACTIONS: * Maintenance to check and correct the voltage supply issue. Further investigation required if issue recurs. * 09/30/2017 16:39:42 SAMUEL WILLIAMS (INCIDENT) * The maintenance team rectified the power supply issue. The pump has resumed normal operation. The root cause of the voltage drop is under investigation. | What was the initial response to the unexpected power interruption to the 17A motor? | The motor was immediately shut down to prevent further damage. A routine inspection revealed a temporary drop in voltage supply to the motor. Order initiated to resolve the issue.
452 | 2018-12-15 | 30983450 | 80245670 | OVERHEATING IN 6A GENERATOR | S1GE -1GE23-DLMT | * **************Incident Description************** * Notification 000030983450 Details * *********************************************************** * 12/15/2018 09:52:00 INCIDENT REPORT (INCIDENT REPORT) * Report submitted by: Jenna Kendall ENTITY\INCIDENT: * * CONDITION DESCRIPTION/LOCATION (THE INAPPROPRIATE ACTION AND ITS NEGATIVE EFFECT/INCLUDE A DETAILED LOCATION DESCRIPTION): * During post-maintenance calibration, the operator noticed significant overheating in the 6A Generator. Despite numerous coolant cycles, the system did not return to normal operational temperature. 6A Generator was taken offline to avoid potential damage. Engineering team and Safety Unit were notified to investigate further. * * ACTIVITIES, PROCESSES, PROCEDURES INVOLVED: * Routine calibration following standard S1.OP-GN.0001 procedure. * * WHY DID CONDITION HAPPEN? * Initial investigation points towards a possible coolant system failure or faulty temperature monitoring system. A detailed investigation is being performed. * * CONSEQUENCES: * Potential generator damage or even catastrophic failure if the unit operates at too high a temperature. * * REQUIREMENTS IMPACTED: * Normal operation and reliability of 6A Generator. * * ADVERSE PHYSICAL CONDITIONS: * Elevated operational temperature in 6A Generator. * * WHO WAS NOTIFIED: * Engineering Team, Safety Unit, Control Room. * * KNOWLEDGEABLE INDIVIDUALS: * Engineering Team, Safety Unit. * * REPEAT OR SIMILAR CONDITION: * No previous incident of this nature has been reported. * * IMMEDIATE ACTIONS AND RECOMMENDED ACTIONS: * Investigate the coolant system and temperature monitoring system for any anomalies; 6A Generator to remain offline until the issue is fully resolved. * 12/15/2018 16:11:42 JENNA KENDALL (INCIDENT) * The cause of the overheating has been isolated to a faulty coolant pump. Replacement parts have been ordered and the generator will be back online after necessary repairs and recalibration. | Why was the 6A Generator overheating during post-maintenance calibration? | Initial investigation points towards a possible coolant system failure or faulty temperature monitoring system.
453 | 2019-10-27 | 30975031 | 80291345 | Surging detected in 9B Pump | S1CW -1CWE1 | * **************Incident Description************** * Notification 000030975031 Details * *********************************************************** * 10/27/2019 14:12:15 INCIDENT REPORT (INCIDENT REPORT) * Report submitted by: Daniel Anderson ENTITY\INCIDENT: * * CONDITION DESCRIPTION/LOCATION (THE INAPPROPRIATE ACTION AND ITS NEGATIVE EFFECT/INCLUDE A DETAILED LOCATION DESCRIPTION): * During operations, it was detected that 9B Pump was surging indicating a possible blockage or damage. The surge was identified through elevated vibration levels and pressure oscillations. The pump was isolated and emergency shut down protocol S1.OP-AB.CW-0008 was followed. * * ACTIVITIES, PROCESSES, PROCEDURES INVOLVED: * Regular operational monitoring, Emergency shutdown protocol S1.OP-AB.CW-0008 * * WHY DID CONDITION HAPPEN? * Cause unknown. The blockage may have been introduced through the inlet, or internal damage may have caused the pump to fail. * * CONSEQUENCES: * Failure of 9B Pump would affect pressure in the system, disrupt normal operation and potentially result in further system damage. * * REQUIREMENTS IMPACTED: * Normal operation and redundancy of pump system. * * ADVERSE PHYSICAL CONDITIONS: * Surging in 9B Pump, possible pump damage. * * WHO WAS NOTIFIED: * Maintenance Supervisor, Health and Safety Team. * * KNOWLEDGEABLE INDIVIDUALS: * Daniel Anderson, Maintenance Supervisor, H&S Team. * * REPEAT OR SIMILAR CONDITION: * No, this is the first instance of surging detected within 9B Pump. * * IMMEDIATE ACTIONS AND RECOMMENDED ACTIONS: * The pump was isolated and emergency shutdown procedure was initiated. Further inspection of pump and pipework to determine cause of surging is recommended. * 10/30/2019 13:52:50 DANIEL ANDERSON (INCIDENT) * The inspection revealed no blockages, surmised it was a malfunction in the pump mechanism itself. Therefore, a replacement was ordered and fitted, and the | What was the immediate action taken upon detection of the issue with the 9B Pump? | The pump was isolated and emergency shutdown procedure was initiated.
454 | 2018-10-10 | 30991234 | 80256390 | Unusual vibration from 30B Pump | S4CW -4CWE5 | * **************Incident Description************** * Notification 000030991234 Details * *********************************************************** * 10/10/2018 15:15:00 INCIDENT REPORT (INCIDENT REPORT) * Report submitted by: James Stewart ENTITY\INCIDENT: * * CONDITION DESCRIPTION/LOCATION (THE INAPPROPRIATE ACTION AND ITS NEGATIVE EFFECT/INCLUDE A DETAILED LOCATION DESCRIPTION): * Following routine check, the 30B Pump was observed to be exhibiting unusual vibrations. Preliminary measurement of vibrations was at 0.45 inches/second, which is above typical vibration spectrum. No specific operational conditions such as elevated temperatures or unusual noises were observed. The vibration levels demand a detailed inspection and diagnosis to root out possible misalignment, rotor imbalance, or cavitation issues. * * ACTIVITIES, PROCESSES, PROCEDURES INVOLVED: * Routine operational check under S4.OP-PQ.CW-0008 and vibration analysis required. * * WHY DID CONDITION HAPPEN? * Unknown, frequency and intensity of vibrations suggest an imbalance or misalignment. * * CONSEQUENCES: * Potential deterioration of pump elements leading to sudden pump failure. * * REQUIREMENTS IMPACTED: * Normal operation, pump reliability. * * ADVERSE PHYSICAL CONDITIONS: * Increased vibration level from 30B Pump motor. * * WHO WAS NOTIFIED: * Control Room, Maintenance Team. * * KNOWLEDGEABLE INDIVIDUALS: * James Stewart, Maintenance Team. * * REPEAT OR SIMILAR CONDITION: * No prior episodes relating to this pump were reported. * * IMMEDIATE ACTIONS AND RECOMMENDED ACTIONS: * Shut down 30B Pump for further analysis and conduct root cause investigation into vibration cause. * 10/12/2018 10:10:59 JAMES STEWART (INCIDENT) * As per the incident analysis, the source of vibration was a misalignment in the rotor shaft. The shaft has been realigned and pump has been restored to operation with vibration levels within the acceptable range. | What was the immediately recommended action following the detection of unusual vibrations in the 30B Pump? | Shut down 30B Pump for further analysis and conduct root cause investigation into vibration cause.
455 | 2017-11-18 | 30872135 | 80256320 | Overheating of Generator 18B | S4EN -4ENG2 | * **************Incident Description************** * Notification 000030872135 Details * *********************************************************** * 11/18/2017 17:32:14 INCIDENT REPORT (INCIDENT REPORT) * Report submitted by: James Adler ENTITY\INCIDENT: * * CONDITION DESCRIPTION/LOCATION (THE INAPPROPRIATE ACTION AND ITS NEGATIVE EFFECT/INCLUDE A DETAILED LOCATION DESCRIPTION): * * At 1732hrs on 18/11/17, it was reported that Generator 18B was overheating. The generator was immediately shut down. Although there was no visible smoke, the high temperature alarm was triggered. Maintenance team's inspection revealed no visible external damage, but the internal parameters confirmed over-heating. An operational check under supervision has been initiated. * * ACTIVITIES, PROCESSES, PROCEDURES INVOLVED: * S4.OP.AB-EN-0002, S4.OP-SO.EN-0002 * * WHY DID CONDITION HAPPEN? * * The cause of the overheating is currently unknown, but there have been previous incidents of generator overheating. * * CONSEQUENCES: * Overheating could potentially cause complete generator failure, affecting the unit's power output. * * REQUIREMENTS IMPACTED: * Generator availability, Reduced power output * * ADVERSE PHYSICAL CONDITIONS: * Overheating of Generator 18B, potential internal damage. * * WHO WAS NOTIFIED: * Control Room, Maintenance Team * * KNOWLEDGEABLE INDIVIDUALS: * Peterson, Stark, Cruise * * REPEAT OR SIMILAR CONDITION: * Yes, there were similar incidents with other generators in the past. * * IMMEDIATE ACTIONS AND RECOMMENDED ACTIONS: * Immediate inspection of over-heated Generator 18B, Perform maintenance check on all units, Update operation procedures to address overheating issue. * * 11/21/2017 11:52:16 JAMES ADLER (INCIDENT) * Cooling system was found to be responsible for the overheating, an obstruction was found and now cleared. The generator is back in operation post a successful test run. Recommend a more vigorous | What was the immediate action taken after overheating was detected in Generator 18B? | The generator was immediately shut down. At 1732hrs on 18/11/17, it was reported that Generator 18B was overheating. The generator was immediately shut down. Although there was no visible smoke, the high temperature alarm was triggered. Maintenance team's inspection revealed no visible external damage, but the internal parameters confirmed over-heating. An operational check under supervision has been initiated.
456 | 2018-11-12 | 30843650 | 80234529 | 17B pump leak detected | S3CW -3CWE5 | * **************Incident Description************** * Notification 000030843650 Details * *********************************************************** * 11/12/2018 15:40:30 INCIDENT REPORT (INCIDENT REPORT) * Report submitted by: David White 123-456-8910 ENTITY\INCIDENT: * * CONDITION DESCRIPTION/LOCATION (THE INAPPROPRIATE ACTION AND ITS NEGATIVE EFFECT/INCLUDE A DETAILED LOCATION DESCRIPTION): * Routine check performed at 15:30 revealed a small leak at the bottom of 17B pump. The leakage was not noticed during the morning inspection. No noticeable impact to the pump's performance or efficiency at the moment of discovery. Leak could potentially increase if not addressed. * * ACTIVITIES, PROCESSES, PROCEDURES INVOLVED: * Daily monitoring activities * * WHY DID CONDITION HAPPEN? * It's currently undetermined. Possible reasons could be worn-out seals or tiny cracks in the pump casing. * * CONSEQUENCES: * If not addressed, could lead to larger leaks, damaging the pump and causing operational inefficiencies. * * REQUIREMENTS IMPACTED: * Continued operation of 17B Pump * * ADVERSE PHYSICAL CONDITIONS: * Leakage at the bottom of the 17B pump * * WHO WAS NOTIFIED: * Supervisor, Maintenance Team * * KNOWLEDGEABLE INDIVIDUALS: * Supervisor, Maintenance Team, Site Manager * * REPEAT OR SIMILAR CONDITION: * No, this is a first report of leakage on the 17B pump * * IMMEDIATE ACTIONS AND RECOMMENDED ACTIONS: * Deployment of the maintenance team to assess and repair the leak. Further evaluation might be required if the source of the leak isn't an obvious seal failure. * 11/14/2018 10:33:52 DAVID WHITE (INCIDENT) * Maintenance team has addressed the leakage. Seals were replaced and casing thoroughly examined with no extra issues identified. An additional check will be carried out during the next shift to confirm repair success. | What immediate actions were taken after the leak in the 17B pump was discovered? | Deployment of the maintenance team to assess and repair the leak. Further evaluation might be required if the source of the leak isn't an obvious seal failure.
457 | 2022-01-07 | 30937583 | 80564289 | Elevated temperature in 17B generator | S5GE -5GEK3 | * **************Incident Description************** * Notification 000030937583 Details * *********************************************************** * 01/07/2022 14:12:17 INCIDENT REPORT (INCIDENT REPORT) * Report submitted by: Parker Lewis ENTITY\INCIDENT: * * CONDITION DESCRIPTION/LOCATION (THE INAPPROPRIATE ACTION AND ITS NEGATIVE EFFECT/INCLUDE A DETAILED LOCATION DESCRIPTION): * During the regular maintenance check, 17B generator showed an elevated temperature. The generator as per schedule was running under nominal load and had cooling system working properly. There was however concerning temperature rise of 20 degrees above the standard temperature. It did not exceed the safety limits but such a drastic rise is abnormal and potentially damaging. * * ACTIVITIES, PROCESSES, PROCEDURES INVOLVED: * Regular maintenance check, temperature measurement. * * WHY DID CONDITION HAPPEN? * The exact cause of elevated temperature is not clear, though fault in cooling system or internal generator malfunction could be the reasons. * * CONSEQUENCES: * Prolonged high operating temperature may cause premature generator fatigue, efficiency loss and possible breakdown. * * REQUIREMENTS IMPACTED: * Continuous running of generator * * ADVERSE PHYSICAL CONDITIONS: * Elevated temperature with potential internal damage to generator * * WHO WAS NOTIFIED: * Maintenance Department, Supervisor * * KNOWLEDGEABLE INDIVIDUALS: * Parker Lewis, Supervisor, Maintenance Team * * REPEAT OR SIMILAR CONDITION: * No, first occurrence * * IMMEDIATE ACTIONS AND RECOMMENDED ACTIONS: * Generator to be closely monitored, additional diagnostics suggested for cooling and load system. Immediate maintenance might be required. * 01/10/2022 09:32:53 PARKER LEWIS (INCIDENT) * Preliminary investigation shows no apparent malfunction in the cooling system but internal generator components show signs of stress. Detailed examination scheduled to happen and may require potential overhaul of the generator. | What immediate actions were recommended following the incident of the generator's elevated temperature? | Generator to be closely monitored, additional diagnostics suggested for cooling and load system. Immediate maintenance might be required.
458 | 2018-11-12 | 30975043 | 80390158 | Unexpected vibrations from 17B Cooling Fan | S4CW -4CWE6 | * **************Incident Description************** * Notification 000030975043 Details * *********************************************************** * 11/12/2018 09:02:04 INCIDENT REPORT (INCIDENT REPORT) * Report submitted by: Daniel Green ENTITY\INCIDENT: * * CONDITION DESCRIPTION/LOCATION (THE INAPPROPRIATE ACTION AND ITS NEGATIVE EFFECT/INCLUDE A DETAILED LOCATION DESCRIPTION): * During the routine morning checks, the 17B cooling fan exhibited unexpected vibrations. These vibrations were harsh, consistent and not normal for this fan. The fan was promptly switched off for safety and to prevent potential damage to the system. * * ACTIVITIES, PROCESSES, PROCEDURES INVOLVED: * Routine operations check * * WHY DID CONDITION HAPPEN? * As of now, the source and the cause of these vibrations is unclear. A thorough inspection is required to be carried out. * * CONSEQUENCES: * Operational functionality could be compromised which could lead to downtime. * * REQUIREMENTS IMPACTED: * The efficiency of the system. * * ADVERSE PHYSICAL CONDITIONS: * Harsh vibrations from 17B Cooling fan. * * WHO WAS NOTIFIED: * Operations Supervisor, Engineering department * * KNOWLEDGEABLE INDIVIDUALS: * Engineering department, Maintenance team, Daniel Green * * REPEAT OR SIMILAR CONDITION: * No, not as per available records. * * IMMEDIATE ACTIONS AND RECOMMENDED ACTIONS: * The Fan should be examined in detail. If the cause of vibrations cannot be resolved, replacement might be necessary. * 13/11/2018 10:17:01 DANIEL GREEN (INCIDENT) * The detailed inspection revealed a bearing failure which explains the sudden severe vibrations. The fan has been scheduled for part replacementand further monitoring. | What was the immediate action taken after the unexpected vibrations in the 17B cooling fan were detected? | The fan was promptly switched off for safety and to prevent potential damage to the system.
459 | 2018-09-25 | 30810956 | 80256345 | Odd 17B pump vibration post alignment | S4CW -4CWE5 | * **************Incident Description************** * Notification 000030810956 Details * *********************************************************** * 09/25/2018 16:15:00 INCIDENT REPORT (INCIDENT REPORT) * Report submitted by: Daniel Adams ENTITY\INCIDENT: * * CONDITION DESCRIPTION/LOCATION (THE INAPPROPRIATE ACTION AND ITS NEGATIVE EFFECT/INCLUDE A DETAILED LOCATION DESCRIPTION): * Following scheduled alignment under work order 80256345, abnormal vibration was detected on 17B Pump during startup process. The vibration was noticed by the control room operators and reported. Pump was shut down for safety until further investigation can be carried out. Detailed location: Level 3 Pump area. * * ACTIVITIES, PROCESSES, PROCEDURES INVOLVED: * Conducting alignment for pump under S4.OP-SC.CW-0003 procedure. * * WHY DID CONDITION HAPPEN? * Possible alignment issue or worn-out parts needing replacement. * * CONSEQUENCES: * Potential equipment failure, reduced efficiency, and unexpected downtime. * * REQUIREMENTS IMPACTED: * Pump startup * * ADVERSE PHYSICAL CONDITIONS: * High vibration on 17B pump * * WHO WAS NOTIFIED: * Control Room, Maintenance Team * * KNOWLEDGEABLE INDIVIDUALS: * Control Room Operators, Maintenance Team, George Barnes * * REPEAT OR SIMILAR CONDITION: * No * * IMMEDIATE ACTIONS AND RECOMMENDED ACTIONS: * Halted operation of the pump. Scheduled for second alignment check and parts inspection. * * Updated by: DANIEL ADAMS 09.25.2018 18:35:42 * ------------------------------------------------------------- * 10/03/2018 11:54:21 JOHN SMITH (MAINTENANCE) * Close examination revealed that the alignment was not the cause of the vibration. A worn out bearing was discovered and replaced. After the replacement, 17B pump vibration is within normal limits. Checked other pumps for preventive measures. | What was the cause of the abnormal vibration detected on the 17B Pump? | A worn out bearing was discovered and replaced. After the replacement, 17B pump vibration is within normal limits.
460 | 2017-05-22 | 30946312 | 80235876 | AC24A Vibration detected | S4AC -4ACE5-TUR | * **************Incident Description************** * Notification 000030946312 Details * *********************************************************** * 05/22/2017 18:31:43 INCIDENT REPORT (INCIDENT REPORT) * Report submitted by: Emma Harris ENTITY\INCIDENT: * * CONDITION DESCRIPTION/LOCATION (THE INAPPROPRIATE ACTION AND ITS NEGATIVE EFFECT/INCLUDE A DETAILED LOCATION DESCRIPTION): * During the routine inspection, AC24A turbine showed a higher than normal vibration. The vibration was unexpected as all prior checks were within limits. Immediate shut down was performed, and there were no signs of overt mechanical damage upon physical inspection. * * ACTIVITIES, PROCESSES, PROCEDURES INVOLVED: * Routine condition monitoring, S4.OP-SO.AC-0003. * * WHY DID CONDITION HAPPEN? * The cause is unknown at this time; it could be a bearing problem, imbalance, or loose components. * * CONSEQUENCES: * Prolonged operation with high vibration can lead to serious damage and potential unit shutdown. * * REQUIREMENTS IMPACTED: * Stabilized operation of turbine AC24A * * ADVERSE PHYSICAL CONDITIONS: * Abnormal vibration of AC24A turbine * * WHO WAS NOTIFIED: * Maintenance Supervisor, Operations Manager * * KNOWLEDGEABLE INDIVIDUALS: * Operations Manager, Lead Mechanical Engineer * * REPEAT OR SIMILAR CONDITION: * No, this is the first time for AC24A Turbine * * IMMEDIATE ACTIONS AND RECOMMENDED ACTIONS: * Scheduling a thorough investigation of the turbine, a potential borescope inspection could reveal any hidden internal factors contributing to the vibration. * 05/25/2017 14:16:59 EMMA HARRIS (INCIDENT) * The investigation concluded that the turbine experienced a temporary imbalance due to debris in the exhaust path. The exhaust path was cleaned, balance restored, and the turbine has been restarted with normal operation parameters. | What was the immediate response after the abnormal vibration was discovered in the turbine AC24A? | Immediate shut down was performed, and there were no signs of overt mechanical damage upon physical inspection.
461 | 2020-05-16 | 31908767 | 83015912 | Unusual operation of 18B pump | SC3W -3CWE5 | * **************Incident Description************** * Notification 000031908767 Details * *********************************************************** * 05/16/2020 10:35:00 INCIDENT REPORT (INCIDENT REPORT) * Report filed by: Sarah Thompson ENTITY\INCIDENT: * * CONDITION DESCRIPTION/LOCATION (THE INAPPROPRIATE ACTION AND ITS NEGATIVE EFFECT/INCLUDE A DETAILED LOCATION DESCRIPTION): * At 09:36 on 5/16/2020, the operator noted that the 18B pump was not running smoothly. The pump was manually shut down from the Unit 3 Control Room and inspected. The inspection, carried out by the Operations team and the Fire Department, did not reveal any signs of excessive heat or smoke but indicated vibration beyond the normal operating range. Motor and pump temperatures were within normal parameters. The unusual operation triggered SC3W.OP.AB.CW-0003 - Pump Abnormality procedure. * * ACTIVITIES, PROCESSES, PROCEDURES INVOLVED: * SC3W.OP.AB.CW-0003, SC3W.OP-SO.CW-0001 * * WHY DID CONDITION HAPPEN? * Unknown, possibly due to imbalance in the pump or a fault in the drive motor. * * CONSEQUENCES: * Unidentified failure could potentially lead to a breakdown or dangerous condition. * * REQUIREMENTS IMPACTED: * Normal operating of 18B pump. * * ADVERSE PHYSICAL CONDITIONS: * Unusual operation of 18B pump, possible issue with parts balance or alignment. * * WHO WAS NOTIFIED: * Supervisor, Fire Department * * KNOWLEDGEABLE INDIVIDUALS: * Operations team, Fire Department, Jackson, Mathews, Pearson * * REPEAT OR SIMILAR CONDITION: * No * * IMMEDIATE ACTIONS AND RECOMMENDED ACTIONS: * Maintenance team to conduct a thorough investigation of 18B pump and report findings. * * Updated: SARAH THOMPSON 05.16.2020 13:30:00 * ------------------------------------------------------------ * 05/24/2020 09:10:20 JACOB SMITH | What were the consequences of the inappropriate action related to the 18B pump? | Unidentified failure could potentially lead to a breakdown or dangerous condition.
462 | 2018-03-19 | 30876345 | 80239628 | D8 Generator unusual vibration | S4PW -4PWE11-GETR | * **************Incident Description************** * Notification 000030876345 Details * *********************************************************** * 03/19/2018 18:33:24 INCIDENT REPORT (INCIDENT REPORT) * Report submitted by: Sarah Thompson ENTITY\INCIDENT: * * 1) CONDITION DESCRIPTION/LOCATION (THE INAPPROPRIATE ACTION AND ITS NEGATIVE EFFECT/INCLUDE A DETAILED LOCATION DESCRIPTION): * In the course of performance monitoring, D8 Generator displayed irregular vibration. Operators cross-checked with similar generators in operation and confirmed anomaly. Minimal external damage was identified, yet the vibrational frequency of D8 was significantly higher. * * 2) ACTIVITIES, PROCESSES, PROCEDURES INVOLVED: * Regular performance monitoring and check, Procedure S4.OP.GE.SV-0031 * * 3) WHY DID CONDITION HAPPEN?: * Preliminary analysis suggests possibly worn-out bearings or misalignment of the rotor. Further investigation is necessary. * * 4) CONSEQUENCES: * If unchecked, continuous vibration could result in critical damage to components, unplanned shutdowns, and reduced efficiency. * * 5) REQUIREMENTS IMPACTED: * Regular operation and performance of D8 generator * * 6) ADVERSE PHYSICAL CONDITIONS: * Excessive vibration of the D8 Generator * * 7) WHO WAS NOTIFIED: * Supervisor and Maintenance Team * * 8) KNOWLEDGEABLE INDIVIDUALS: * Maintenance Team, Sarah Thompson * * 9) REPEAT OR SIMILAR CONDITION: * No, this is the first instance with D8 Generator. * * 10) IMMEDIATE ACTIONS AND RECOMMENDED ACTIONS: * Reduce D8 Generator operation speed, schedule for immediate maintenance inspection to identify the root cause. * 03/22/2018 14:40:34 SARAH THOMPSON (INCIDENT) * Scheduled for maintenance investigation. Further update upon completion and analysis. | What was the initial cause of the irregular vibration in the D8 Generator? | Preliminary analysis suggests possibly worn-out bearings or misalignment of the rotor. Further investigation is necessary.
463 | 2019-03-12 | 30903124 | 90241283 | 17B Auxiliary system irregular oil pressure | S4CW -4CWE1 | * **************Incident Description************** * Notification 000030903124 Details * *********************************************************** * 03/12/2019 15:42:00 INCIDENT REPORT (INCIDENT REPORT) * Report submitted by: Peter Thompson ENTITY\INCIDENT: * * CONDITION DESCRIPTION/LOCATION (THE INAPPROPRIATE ACTION AND ITS NEGATIVE EFFECT/INCLUDE A DETAILED LOCATION DESCRIPTION): * During regular working hours, an irregular oil pressure was detected in the 17B Auxiliary system. The low pressure alarm showed at 1452. Immediately, the system was shut down to avoid any potential damage. Further investigation needs to be made to identify what caused the low oil pressure alarm in the auxiliary system. * * ACTIVITIES, PROCESSES, PROCEDURES INVOLVED: * S4.OP.AB-CW-0001, S4.OP-SO.CW-0001 * * WHY DID CONDITION HAPPEN? * It is indeterminate at the moment, an investigation has been initiated to identify the cause of the low oil pressure. * * CONSEQUENCES: * If not resolved promptly, it could result in system failure and operational down-time. * * REQUIREMENTS IMPACTED: * Auxiliary system operation * * ADVERSE PHYSICAL CONDITIONS: * Irregular oil pressure in the 17B Auxiliary system * * WHO WAS NOTIFIED: * Maintenance Supervisor, Operations Manager * * KNOWLEDGEABLE INDIVIDUALS: * Nancy Watson, Robert Lopez, Scott Jackson * * REPEAT OR SIMILAR CONDITION: * No, this is the first occurrence * * IMMEDIATE ACTIONS AND RECOMMENDED ACTIONS: * The 17B Auxiliary System has been shut down for investigation. If necessary, components should be replaced to prevent damage or failure. * 03/15/2019 08:16:47 PETER THOMPSON (INCIDENT) * The auxiliary system was thoroughly inspected, and it was found that the oil filter was blocked, causing the low pressure alarm. After cleaning and replacing the oil filter, the system resumed normal operations. Regular maintenance and checking activities should be increased to prevent such occurrences. | What was the cause of the low oil pressure alarm in the 17B Auxiliary system? | The auxiliary system was thoroughly inspected, and it was found that the oil filter was blocked, causing the low pressure alarm. After cleaning and replacing the oil filter, the system resumed normal operations.
464 | 2018-02-18 | 30735373 | 80245362 | 14B Overspeed motor operation | S4CW -4CWE9-POLY | * **************Incident Description************** * Notification 000030735373 Details * *********************************************************** * 02/18/2018 16:16:32 INCIDENT REPORT (INCIDENT REPORT) * Report submitted by: Emily Johnson 987-654-3210 ENTITY\INCIDENT: * CONDITION DESCRIPTION/LOCATION (THE INAPPROPRIATE ACTION AND ITS NEGATIVE EFFECT/INCLUDE A DETAILED LOCATION DESCRIPTION): * During the shift turnover, it was observed that 14B Pump was speeding up. A local inspection revealed a vibration and abnormal noise at 14B Pump that was not evident in any other pump motor. The 14B Pump was immediately removed from service for inspection. * * ACTIVITIES, PROCESSES, PROCEDURES INVOLVED: * S4.OP.AB-S7-0012, S4.OP-SO.CW-0023 * * WHY DID CONDITION HAPPEN? * Cause of overspeed is unknown, motor governor to be inspected. * * CONSEQUENCES: * Risk of mechanical damage with potential impacts on pump service effectiveness and reliability. Immediate removal from service resulted in loss of redundancy. * * REQUIREMENTS IMPACTED: * Out of service pump reduced system redundancy * * ADVERSE PHYSICAL CONDITIONS: * Elevated pump speed and abnormal vibration * * WHO WAS NOTIFIED: * Unit Control Room, Maintenance Department * * KNOWLEDGEABLE INDIVIDUALS: * Anderson, Thompson, Miller * * REPEAT OR SIMILAR CONDITION: * No * * IMMEDIATE ACTIONS AND RECOMMENDED ACTIONS: * Immediate removal of 14B from service. Maintenance actions to follow include inspection and correction of adverse conditions, specifically pump governor inspection. * 02/19/2018 07:32:42 EMILY JOHNSON (INCIDENT) * The overspeed condition was found to be due to a faulty governor in the pump motor. The governor was replaced and the pump has returned to regular service condition. | What was the reason for the overspeed condition of the 14B Pump? | The overspeed condition was found to be due to a faulty governor in the pump motor.
465 | 2017-07-18 | 30782418 | 80258673 | Cooling tower 16B unusual vibrations | S3CW -3CWE7 | * **************Incident Description************** * Notification 000030782418 Details* * *********************************************************** * 07/18/2017 14:59:23 INCIDENT REPORT (INCIDENT REPORT) * Report submitted by: Robert Smith ENTITY\INCIDENT: * * CONDITION DESCRIPTION/LOCATION (THE INAPPROPRIATE ACTION AND ITS NEGATIVE EFFECT/INCLUDE A DETAILED LOCATION DESCRIPTION): * During daily operation, Cooling Tower 16B started producing unusual vibrations. Operation parameters were within normal limits. Despite the continuous cooling tower function, the unusual vibrations are a sign of potential mechanical issue. * * ACTIVITIES, PROCESSES, PROCEDURES INVOLVED: * Daily operation and monitoring procedures * WHY DID CONDITION HAPPEN? * Unknown, possible mechanical failure or wear and tear. * * CONSEQUENCES: * Potential severe damage to Cooling Tower if not addressed promptly. * * REQUIREMENTS IMPACTED: * Possible disruption to normal operations. * * ADVERSE PHYSICAL CONDITIONS: * Vibration levels of Cooling Tower 16B. * * WHO WAS NOTIFIED: * Maintenance Supervisor/ INCIDENT TEAM * * KNOWLEDGEABLE INDIVIDUALS: * Incident Team, Operator John Taylor * * REPEAT OR SIMILAR CONDITION: * No, this condition is unusual. * * IMMEDIATE ACTIONS AND RECOMMENDED ACTIONS: * Initiate fault diagnosis, follow maintenance procedures. Potential shutdown may be necessary. * 07/18/2017 17:24:16 ROBERT SMITH (INCIDENT) * Maintenance has been sighted at Cooling Tower 16B. Fault diagnosis under process. Immediate shutdown not necessary at this time. | What were the immediate actions and recommended actions after the unusual vibrations in Cooling Tower 16B were detected? | Initiate fault diagnosis, follow maintenance procedures. Potential shutdown may be necessary.
466 | 2018-12-12 | 30887654 | 80245612 | Overheating in Valve 4D | S1CW -1CWE8 | * **************Incident Description************** * Notification 000030887654 Details * **************************************************************** * 12/12/2018 07:34:36 INCIDENT REPORT (INCIDENT REPORT) * Report submitted by: Sam Worthington 987-654-3210 ENTITY\INCIDENT: * CONDITION DESCRIPTION/LOCATION (THE INAPPROPRIATE ACTION AND ITS NEGATIVE EFFECT/INCLUDE A DETAILED LOCATION DESCRIPTION): * At 07:15 on 12/12/2018, routine check up revealed an overheating in valve 4D of the unit 2 in service 1. Valve 4D was immediately shut down, Fire Department and Operations conducted an inspection. Though no external signs of damage were evident, abnormal temperature was felt. Valve abnormality was indicated due to emergency shutdown. * * ACTIVITIES, PROCESSES, PROCEDURES INVOLVED: * Regular inspection, S1.OP.AB-CW-0002, S1.OP-SO.CW-0002 * * WHY DID CONDITION HAPPEN: * Unknown at this point, although previous occurrences of overheating have been recorded. * * CONSEQUENCES: * Potential valve damage can lead to reduced efficiency. Fire hazard when left unchecked. * * REQUIREMENTS IMPACTED: * Valve availability and normal operation impacted. * * ADVERSE PHYSICAL CONDITIONS: * Overheating in Valve 4D, potential internal damage. * * WHO WAS NOTIFIED: * Operations Control Room, Fire Department * * KNOWLEDGEABLE INDIVIDUALS: * Daniels, Williams, Johnson * * REPEAT OR SIMILAR CONDITION: * Yes, previous instances recorded * * IMMEDIATE ACTION AND RECOMMENDED ACTIONS: * Maintenance team to investigate Valve 4D * 12/12/2018 15:37:45 SAM WORTHINGTON (INCIDENT) * The problem seems to be due to worn-out parts. Parts replaced, valve reconditioned, and now back online. Will monitor closely. | What actions were taken in response to the overheating of valve 4D? | Valve 4D was immediately shut down, Fire Department and Operations conducted an inspection. Maintenance team to investigate Valve 4D. The problem seems to be due to worn-out parts. Parts replaced, valve reconditioned, and now back online.
467 | 2018-04-27 | 30987416 | 80542090 | Unusual vibration in 16D Pump | S4DW -4DWE9-PMP | * **************Incident Description************** * Notification 000030987416 Details * *********************************************************** * 04/27/2018 14:07:19 INCIDENT REPORT (INCIDENT REPORT) * Report submitted by: Robert Green ENTITY\INCIDENT: * * CONDITION DESCRIPTION/LOCATION (THE INAPPROPRIATE ACTION AND ITS NEGATIVE EFFECT/INCLUDE A DETAILED LOCATION DESCRIPTION): * On 4/27/18, during the routine inspection, an unusual vibration was observed in 16D Pump. The pump was then immediately put to halt to prevent possible damage to adjacent systems. The analyzing team was summoned for further investigation. Their inspection revealed that the vibration was exclusively associated to the 16D pump itself and not conveyed from any neighboring systems or components. * * ACTIVITIES, PROCESSES, PROCEDURES INVOLVED: * Routine inspection, emergency shutdown of 16D Pump, S4.OP.AB-CW-0002, S4.OP-SO.CW-0002 * * WHY DID CONDITION HAPPEN: * The reason for the vibration is uncertain at the moment. Although, it is possible that it could have been a result of impairments or internal spoils in the pump system. * * CONSEQUENCES: * Potential pump damage can lead to system disruption, reduced efficiency, and increased repairing cost. * * REQUIREMENTS IMPACTED: * Normal operation * * ADVERSE PHYSICAL CONDITIONS: * Unusual vibration in 16D Pump which may lead to internal or external damage. * * WHO WAS NOTIFIED: * Control Room, Maintenance Team * * KNOWLEDGEABLE INDIVIDUALS: * Robert Green, Anthony Brown, Kelly Parker * * REPEAT OR SIMILAR CONDITION: * Unreported previously * * IMMEDIATE ACTIONS AND RECOMMENDED ACTIONS: * Suspend the pump operation temporarily, find the source of vibration, repair if necessary. * 04/29/2018 10:31:42 ROBERT GREEN (INCIDENT) * After detailed inspection and analysis, it was revealed that the vibration was due to an imbalance in the internal pump system. | What was the root cause of the unusual vibration in the 16D Pump? | The vibration was due to an imbalance in the internal pump system.
468 | 2016-09-12 | 30860745 | 80221459 | Sudden pressure drop in 20B Pump | S1CW -1CWE1 | * **************Incident Description************** * Notification 000030860745 Details * *********************************************************** * 09/12/2016 14:22:37 INCIDENT REPORT (INCIDENT REPORT) * Report submitted by: Derek Johnson ENTITY\INCIDENT: * * CONDITION DESCRIPTION/LOCATION (THE INAPPROPRIATE ACTION AND ITS NEGATIVE EFFECT/INCLUDE A DETAILED LOCATION DESCRIPTION): * On routine supervision it was noticed that Pump 20B displayed a sudden pressure drop. This occurred without indication or any visible changes in operating conditions. The pressure drop was resolved by resetting the pump system but causes remain unclear. * * ACTIVITIES, PROCESSES, PROCEDURES INVOLVED: * Daily pump monitoring and maintenance activities. specifically procedure S1.OP-SO.CW-0002. * * WHY DID CONDITION HAPPEN? * The exact cause is uncertain, possible component failure or fault in control system. * * CONSEQUENCES: * Unexpected pumping interruptions and possible system damages if not resolved quickly. * * REQUIREMENTS IMPACTED: * Efficient operations and continuous pumping were impacted. * * ADVERSE PHYSICAL CONDITIONS: * Unexpected pump pressure drop. * * WHO WAS NOTIFIED: * Supervisor, management team and safety officer. * * KNOWLEDGEABLE INDIVIDUALS: * Field maintenance team and supervisors. * * REPEAT OR SIMILAR CONDITION: * No, this is a first-time occurrence. * * IMMEDIATE ACTIONS AND RECOMMENDED ACTIONS: * Immediate pump reset performed and stable operation confirmed. Recommended in-depth inspection, potential component replacement, and system test to avoid reoccurrence. * 09/12/2016 17:13:12 DEREK JOHNSON (INCIDENT) * The cause of the pressure drop has been traced to a control valve malfunction, and the valve has been replaced under work order 80221459. The pump is back to normal operation. | What was the immediate and recommended action after the sudden pressure drop in Pump 20B? | Immediate pump reset performed and stable operation confirmed. Recommended in-depth inspection, potential component replacement, and system test to avoid reoccurrence.
469 | 2018-10-02 | 30805260 | 80245230 | Low oil pressure in 32B motor | S4CW -4CWE1 | * **************Incident Description************** * Notification 000030805260 Details * *********************************************************** * 10/02/2018 14:50:42 INCIDENT REPORT (INCIDENT REPORT) * Report submitted by: David Watson ENTITY\INCIDENT: * * CONDITION DESCRIPTION/LOCATION (THE INAPPROPRIATE ACTION AND ITS NEGATIVE EFFECT/INCLUDE A DETAILED LOCATION DESCRIPTION): * During the preventative maintenance of 32B pump motor, it was noticed that the oil pressure was lower than usual. This was an unexpected and unusual scenario as the oil filters were recently replaced. No external damages were found and the oil leakage was also ruled out. Upon informal inspection, the other operational parameters were within allowed limits. * * ACTIVITIES, PROCESSES, PROCEDURES INVOLVED: * Routine preventative maintenance check. * * WHY DID CONDITION HAPPEN? * Unknown. Biological contamination in the oil is being suspected. * * CONSEQUENCES: * Wear and tear of the motor, possible operational failure affecting the unit's operations * * REQUIREMENTS IMPACTED: * Normal functionality and operation of the motor and pump * * ADVERSE PHYSICAL CONDITIONS: * Low oil pressure in the motor. * * WHO WAS NOTIFIED: * Supervisor, Operation and Maintenance team * * KNOWLEDGEABLE INDIVIDUALS: * Maintenance Team, Mechanical Engineer * * REPEAT OR SIMILAR CONDITION: * No, this is the first instance. * * IMMEDIATE ACTIONS AND RECOMMENDED ACTIONS: * Detailed inspection and additional testing of the oil quality and the oil pumps functioning will be carried out urgently. * 10/02/2018 19:03:04 DAVID WATSON (INCIDENT) * The inspection of the oil pump confirmed the suspicion of biological contamination. Immediate oil change was performed and the filters were replaced. The oil pressure in the 32B motor is now back within the normal operational limits. | What immediate actions were taken after the suspicion of biological contamination in the oil of the pump motor? | The inspection of the oil pump confirmed the suspicion of biological contamination. Immediate oil change was performed and the filters were replaced. The oil pressure in the 32B motor is now back within the normal operational limits.
470 | 2019-12-05 | 30952086 | 80295610 | Unstoppable water leak valve 7B | S4CW -4CWE1 | * **************Incident Description************** * Notification 000030952086 Details * *********************************************************** * 12/05/2019 15:26:00 INCIDENT REPORT (VALVE LEAK REPORT) * Report submitted by: Robert Edwin 567-890-1234 * ENTITY\INCIDENT: * CONDITION DESCRIPTION/LOCATION (THE INAPPROPRIATE ACTION AND ITS NEGATIVE EFFECT/INCLUDE A DETAILED LOCATION DESCRIPTION): * The maintenance team notified of an unstoppable water leak at valve 7B Pump during routine operations. Preliminary inspection did not reveal any obvious signs of wear or mechanical damage. The leakage has caused flooding in the pump room. * * ACTIVITIES, PROCESSES, PROCEDURES INVOLVED: * Valve inspection, S4.OP-PA.VL-0002 maintenance procedure. * * WHY DID CONDITION HAPPEN? * Possible internal valve defect, erosion or valve linkage malfunction is suspected * * CONSEQUENCES: * Pump room flooding - Impacting operations, possible equipment corrosion. * * REQUIREMENTS IMPACTED: * Operational Safety, Efficiency * * ADVERSE PHYSICAL CONDITIONS: * Water leakage, pump room flooded. * * WHO WAS NOTIFIED: * Supervisor, Operations, Safety Team. * * KNOWLEDGEABLE INDIVIDUALS: * Supervisor, Maintenance Lead, Peter Walter- Valve Specialist. * * REPEAT OR SIMILAR CONDITION: * No, this is the first instance. * * IMMEDIATE ACTIONS AND RECOMMENDED ACTIONS: * Deployment of a mobile pump to manage the water level, Immediate replacement or repair of valve 7B to stop the leak, Investigation on the cause of a leak. * 12/07/2019 09:02:47 ROBERT EDWIN (INCIDENT) * The valve has been replaced and the leak stopped. The water has been cleared and pump room cleaning is underway. Further inspection to assess any damage to other equipment due to water exposure is scheduled. | What immediate actions were taken following the incident of the water leak at valve 7B pump? | Deployment of a mobile pump to manage the water level, Immediate replacement or repair of valve 7B to stop the leak, Investigation on the cause of a leak.
471 | 2019-04-23 | 30921345 | 80248935 | 13B Pump vibration exceeded threshold | S4CW -4CWE7 | * **************Incident Description************** * Notification 000030921345 Details * *********************************************************** * 04/23/2019 15:50:54 INCIDENT REPORT (INCIDENT REPORT) * Report submitted by: Sam Williams ENTITY\INCIDENT: * * CONDITION DESCRIPTION/LOCATION (THE INAPPROPRIATE ACTION AND ITS NEGATIVE EFFECT/INCLUDE A DETAILED LOCATION DESCRIPTION): * During routine monitoring, the vibration level on the 13B pump exceeded the allowable threshold. Immediate shutdown implemented as a precaution to prevent possible damage to the pump or adjoining systems. * * ACTIVITIES, PROCESSES, PROCEDURES INVOLVED: * S4.OP-SO.CW-0003, S4.OP-AB.CW-0008 * * WHY DID CONDITION HAPPEN? * Unknown at this point, additional investigation to be conducted. Possible issues could be bearing wear or impeller imbalance. * * CONSEQUENCES: * Possible pump damage if continued running. Reduced water circulation while the unit is offline. * * REQUIREMENTS IMPACTED: * Equipment reliability and normal circulation of water in the system. * * ADVERSE PHYSICAL CONDITIONS: * Excessive vibration on the 13B pump. * * WHO WAS NOTIFIED: * Control Room, Supervisors * * KNOWLEDGEABLE INDIVIDUALS: * Williams, Thompson, Green * * REPEAT OR SIMILAR CONDITION: * No * * IMMEDIATE ACTIONS AND RECOMMENDED ACTIONS: * Conduct inspection of 13B Pump and identify cause of vibration. Repairs as necessary. Initiate S4.OP-AB.CW-0008 Pump Abnormality Procedure. * 04/24/2019 09:33:25 SAM WILLIAMS (INCIDENT) * Investigation is ongoing, pump remains shut down until cause of vibration can be identified and corrected. | What immediate actions were taken following the detection of excessive vibration on the 13B pump? | Immediate shutdown implemented as a precaution to prevent possible damage to the pump or adjoining systems. Conduct inspection of 13B Pump and identify cause of vibration. Repairs as necessary. Initiate S4.OP-AB.CW-0008 Pump Abnormality Procedure.
472 | 2022-03-17 | 41058234 | 90012456 | 18B motor unusual vibration | S4CW -4CWE1 | * **************Incident Description************** * Notification 000041058234 Details * *********************************************************** * 03/17/2022 15:39:00 INCIDENT REPORT (INCIDENT REPORT) * Report submitted by: Lucas Anderson ENTITY\INCIDENT: * * CONDITION DESCRIPTION/LOCATION (THE INAPPROPRIATE ACTION AND ITS NEGATIVE EFFECT/INCLUDE A DETAILED LOCATION DESCRIPTION): * At 1500 on 17/03/22 the operator detected abnormal vibrations in the 18B Motor. An emergency shutdown was initiated from Unit 4 Control Room and the vibrations ceased. After inspection, no external damage was noted, however, the cause of the vibrations remain unknown. Procedure S4.OP-AB.CW-0003 Motor Abnormality was initiated due to the sudden shutdown of 18B Motor. * * ACTIVITIES, PROCESSES, PROCEDURES INVOLVED: * S4.OP.AB-CW-0003, S4.OP-SO.CW-0003 * * WHY DID CONDITION HAPPEN: * Unknown, despite similar events occurring in the past. * * CONSEQUENCES: * Potential harm to personnel, equipment damage, reduced operation efficiency. * * REQUIREMENTS IMPACTED: * Unavailable motor * * ADVERSE PHYSICAL CONDITION: * Abnormal vibration from 18B Motor, potential internal damage * * WHO WAS NOTIFIED: * Control Room, Maintenance * * KNOWLEDGEABLE INDIVIDUALS: * Williams, Kelly, Robinson * * REPEAT OR SIMILAR CONDITION: * Yes, previously occurred incidents. * * IMMEDIATE AND RECOMMENDED ACTIONS: * Investigation into the 18B Motor vibrations to identify potential causes. * * Updated: JANE DOE 03.18.2022 07:31:25 * ------------------------------------------------------------ * 03/19/2022 10:10:55 LUCAS ANDERSON (NUSER) * The investigation indicated that the balancing of the motor was disrupted by a buildup of dust and debris in key components. The motor was thoroughly cleaned and re-balanced and is now back in | What was the cause of the abnormal vibrations detected in the 18B Motor? | The investigation indicated that the balancing of the motor was disrupted by a buildup of dust and debris in key components.
473 | 2022-01-12 | 30821456 | 90110235 | 11B Pump Motor Failure | S2CW -2CWE7-MTRF | * **************Incident Description************** * Notification 000030821456 Details * *********************************************************** * SUMMARY: NEED TO EVALUATE CURRENT CONDITIONS OF PUMP MOTOR ACCORDING TO * ****PS-AA-125 "MOTOR FAILURE IDENTIFICATION AND TROUBLESHOOTING PROCESS"***** * 1) CONDITION DESCRIPTION/LOCATION (The inappropriate action and its negative effect/Include a detailed location description): * At 1549 on 1/12/22, the control room received a report of a Motor Failure Incident on 11B Pump. The pump was hastily shut down to prevent further damage. An initial inspection by the technical team revealed a potential motor failure, evidenced by power drop and excessive vibration. The cause of the failure is yet to be determined. * 2) ACTIVITIES, PROCESSES, PROCEDURES INVOLVED: * S2.OP.AB-CW-0005, S2.OP-SO.CW-0008 * 3) WHY DID CONDITION HAPPEN: * The exact cause is unknown at the moment, but previous incidents indicate possible internal damage or debris build-up. * 4) CONSEQUENCES: * Continuous use of the pump motor may potentially lead to complete breakdown or reduced efficiency. * 5) REQUIREMENTS IMPACTED: * Normal operations were interrupted. Scheduled routine checks will be disrupted until the issue is resolved completely. * 6) ADVERSE PHYSICAL CONDITION: * Power loss and excessive vibration in 11B Pump motor implies internal complications. * 7) WHO WAS NOTIFIED: * Control Room, Technical Department, Supervisor * 8) KNOWLEDGEABLE INDIVIDUALS: * Davis, Roberts, O'Brien * 9) REPEAT OR SIMILAR CONDITION: * It has occurred before on Pump 11A. * 10) IMMEDIATE AND RECOMMENDED ACTIONS: * Ensure immediate shutdown of the pump. Initiate a thorough failure analysis and inspection by the Maintenance Team. * Updated: JOHN SMITH 01.12.2022 17:31:21 * ------------------------------------------------------------ * 01/15/2022 09:43:51 L | What were the initial signs indicating a potential motor failure in the 11B Pump? | Power drop and excessive vibration.
474 | 2020-10-15 | 31066666 | 80555555 | Unusual vibration from 13B Pump Motor | S4BP -4BPE7-TURB | * **************Incident Description************** * Notification 000031066666 Details * *********************************************************** * 10/15/2020 11:07:20 INCIDENT REPORT (INCIDENT REPORT) * Report submitted by: Noah Thompson * * 1) CONDITION DESCRIPTION/LOCATION (The inappropriate action and its negative effect/Include a detailed location description): * During inspection at 1107 hours on 15/10/20, an unusual vibration was flagged from the 13B Pump Motor. The Motor was stopped immediately. There were no signs of visible damage, but strong vibration may indicate potential internal issues. The issue was logged and the S4.MA-RO.BP-0002 Pump Vibration Abnormality procedure was initiated. * * 2) ACTIVITIES, PROCESSES, PROCEDURES INVOLVED: * S4.MA-RO.BP-0002, S4.MA-SI.BP-0002 * * 3) WHY DID CONDITION HAPPEN: * Cause unknown, though note that pump motors have experienced vibration issues in the past. * * 4) CONSEQUENCES: * Potential motor damage could result in the drop in efficiency or complete failure of the motor when resumed. * * 5) REQUIREMENTS IMPACTED: * Possible shutdown of the pump until further investigation. * * 6) ADVERSE PHYSICAL CONDITION: * Unusual vibration from 13B Pump Motor, potential internal damage. * * 7) WHO WAS NOTIFIED: * Control Room, Maintenance Dept. * * 8) KNOWLEDGEABLE INDIVIDUALS: * Thompson, Williams, Peterson * * 9) REPEAT OR SIMILAR CONDITION: * Yes, there have been similar issues in the past with other motors. * * 10) IMMEDIATE AND RECOMMENDED ACTIONS: * Maintenance team to investigate the 13B Pump Motor. * * Updated: NOAH THOMPSON 10.15.2020 15:22:42 * ------------------------------------------------------------ * 10/20/2020 16:09 | What were the immediate actions taken after the unusual vibration was noticed in the 13B Pump Motor? | The Motor was stopped immediately. The issue was logged and the S4.MA-RO.BP-0002 Pump Vibration Abnormality procedure was initiated. Maintenance team to investigate the 13B Pump Motor.
475 | 2022-02-12 | 30981456 | 80233692 | Unusual Vibrations from 18C Pump | S1AW -1AWE1 | * **************Incident Description************** * Notification 000030981456 Details * *********************************************************** * 02/12/2022 07:30:00 INCIDENT REPORT (INCIDENT REPORT) * Report submitted by: Emily Johnson ENTITY\INCIDENT: * * 1) CONDITION DESCRIPTION/LOCATION (THE INAPPROPRIATE ACTION AND ITS NEGATIVE EFFECT/INCLUDE A DETAILED LOCATION DESCRIPTION): * While conducting a routine check on 2/12/22, operator reported unusual vibrations from the 18C Pump. The pump was shut down immediately based on emergency standard operating procedures. Preliminary inspection revealed no external signs of damage. Pump vibration parameters were outside the normal operational range. Maintenance team initiated troubleshooting procedures aligned with S1.OP-AB.AW-0002. * * 2) ACTIVITIES, PROCESSES, PROCEDURES INVOLVED: * S1.OP.AB-AW-0002 * * 3) WHY DID CONDITION HAPPEN? * Cause of intervention is unknown. However, misalignment or potential internal wear and tear are suspected based on past incidents. * * 4) CONSEQUENCES: * Pump outage creates interruptions in process flow, which can reduce operation efficiency. * * 5) REQUIREMENTS IMPACTED: * Operations and Maintenance schedules. * * 6) ADVERSE PHYSICAL CONDITION: * Unusual Pump vibration, potential mechanical damage. * * 7) WHO WAS NOTIFIED: * Control Room, Maintenance Team * * 8) KNOWLEDGEABLE INDIVIDUALS: * Emily Johnson, Operational Supervisor; Maintenance Team lead - Bob Wilson * * 9) REPEAT OR SIMILAR CONDITION: * No past known cases of similar nature in recent history. * * 10) IMMEDIATE AND RECOMMENDED ACTIONS: * Inspection and troubleshooting by maintenance team. * * Updated: EMILY JOHNSON 02.12.2022 09:15:25 * --------------------------------------------------------------- * 02/18/2022 13:28:47 BOB WILSON ( | What were the adverse physical conditions observed from the incident with the pump on 2/12/22? | Unusual Pump vibration, potential mechanical damage.
476 | 2018-04-30 | 30985321 | 80231568 | Sudden pressure drop in Pump 33B | S4CW -4CWE7 | * **************Incident Description************** * Notification 000030985321 Details * *********************************************************** * 04/30/2018 16:17:12 INCIDENT REPORT (INCIDENT REPORT) * Report submitted by: Daniel White ENTITY\INCIDENT: * * CONDITION DESCRIPTION/LOCATION (THE INAPPROPRIATE ACTION AND ITS NEGATIVE EFFECT/INCLUDE A DETAILED LOCATION DESCRIPTION): * At 1617 hours on 4/30/18, the operator noticed a sudden drop in pressure in the 33B pump. An emergency shutdown was initiated from Unit 4 Control Room and the pressure was successfully stabilized. The Fire Department and Operations inspection revealed no signs of a leak but detected a strong scent of coolant fluids. The sudden pressure drop could imply a potential valve issue or air lock. S4.OP-AB.CW-0002 Pump Abnormality was initiated due to the emergency shutdown of 33B Pump. * * ACTIVITIES, PROCESSES, PROCEDURES INVOLVED: * S4.OP.AB-CW-0002, S4.OP-SO.CW-0002 * * WHY DID CONDITION HAPPEN: * Unknown, potential valve issues or air lock. * * CONSEQUENCES: * Unexpected emergency shutdown, potential damage to the pipeline or pump could result in downtime when the unit is back online. * * REQUIREMENTS IMPACTED: * Unavailable pump * * ADVERSE PHYSICAL CONDITION: * Sudden pressure drop in 33B Pump. * * WHO WAS NOTIFIED: * Control Room, Fire Department * * KNOWLEDGEABLE INDIVIDUALS: * Evans, Thompson, Phillips * * REPEAT OR SIMILAR CONDITION: * No * * IMMEDIATE AND RECOMMENDED ACTIONS: * Operations and Maintenance teams to investigate 33B Pump issue * * Updated: DANIEL WHITE 04.30.2018 20:13:44 * ------------------------------------------------------------ * 05/03/2018 13:14:33 JANE SMITH (NUSER) * Maintenance confirmed the incident was due to an air lock that had formed and potentially disrupted the normal pump operations. | What caused the sudden pressure drop in the 33B Pump? | Unknown, potential valve issues or air lock.
477 | 2018-12-27 | 40732176 | 90234712 | Overheating in Converter G4 | S4AC -4ACE7-TG4 | * **************Incident Description************** * Notification 000040732177 Details * *********************************************************** * 12/27/2018 10:26:57 INCIDENT REPORT (INCIDENT REPORT) * Report submitted by: Oliver Jones, ENTITY\INCIDENT: * * CONDITION DESCRIPTION/LOCATION (THE INAPPROPRIATE ACTION AND ITS NEGATIVE EFFECT/INCLUDE A DETAILED LOCATION DESCRIPTION): * In the early morning hours of 27/12/18, noticeable overheating was detected in Converter G4 during routine operation. Emergency protocol S4.OP-AB.AC-0002 was initiated, grounding the converter until further notice. The temperature slowly returned to safe levels without any visible external damage. However, the incident reiterated the importance of having regularly scheduled maintenance and thorough inspection of all internal system. * * ACTIVITIES, PROCESSES, PROCEDURES INVOLVED: * S4.OP.AB-AC-0002, S4.OP-SO.AC-0003 * * WHY DID CONDITION HAPPEN? * Unknown at this time. Although, prior instances of overheating in converters have been noted. * * CONSEQUENCES: * Potential system malfunction or shutdown if overheating remains unchecked. * * REQUIREMENTS IMPACTED: * Potential issues with power supply stability. * * ADVERSE PHYSICAL CONDITIONS: * Overheating of Converter G4, possible internal damage. * * WHO WAS NOTIFIED: * Supervisor, Maintenance Team * * KNOWLEDGEABLE INDIVIDUALS: * Johnson, Smith, Davis * * REPEAT OR SIMILAR CONDITION: * Yes, previous issues with AC system converters have been reported. * * IMMEDIATE ACTIONS AND RECOMMENDED ACTIONS: * Immediate inspection and diagnosis of Converter G4 by the maintenance team. Development of mitigation strategies. * 12/27/2018 14:30:08 OLIVER JONES (INCIDENT) * Converter G4 inspection has been initiated. Maintenance team is working on determining the cause and resolution. | What was the initial response to the overheating of Converter G4? | Emergency protocol S4.OP-AB.AC-0002 was initiated, grounding the converter until further notice. The temperature slowly returned to safe levels without any visible external damage.
478 | 2020-12-12 | 30991234 | 80298250 | 18A Motor Overheating observed | S4CW -4CWE2 | * **************Incident Description************** * Notification 000030991234 Details * *********************************************************** * 12/12/2020 16:05:00 INCIDENT REPORT (INCIDENT REPORT) * Report submitted by: Jack Johnson ENTITY\INCIDENT: * * CONDITION DESCRIPTION/LOCATION (THE INAPPROPRIATE ACTION AND ITS NEGATIVE EFFECT/INCLUDE A DETAILED LOCATION DESCRIPTION): * During a routine walk-through of the boiler room, the operator noticed an abnormal rise in temperature coming off the 18A pump motor. The system was inspected, readings confirmed an overheat under normal operation conditions. No visible damage was noted on the pump and motor assembly. * * ACTIVITIES, PROCESSES, PROCEDURES INVOLVED: * S4.OP.AB-CW-0012, S4.OP-SO.CW-0005 * * WHY DID CONDITION HAPPEN? * The exact cause of overheat is uncertain. Prior incidents have implicated failing bearings or improper alignment. * * CONSEQUENCES: * Potential shutdown might be required; the increased heat could lead to 18A motor failure, which could impact the boiler operation efficiency. * * REQUIREMENTS IMPACTED: * Normal operation and equipment reliability. * * ADVERSE PHYSICAL CONDITIONS: * Increased heat from 18A pump motor. * * WHO WAS NOTIFIED: * Maintenance Supervisor, Operations Team * * KNOWLEDGEABLE INDIVIDUALS: * Thompson, Jackson, Mitchell * * REPEAT OR SIMILAR CONDITION: * No, this is the first event of this nature on 18A Motor. * * IMMEDIATE ACTIONS AND RECOMMENDED ACTIONS: * Immediate inspection and necessary maintenance of 18A pump motor is suggested, under guidance from the maintenance supervisor and engineering team. * 12/14/2020 13:05:00 LUCY SMITH (REPORT) * Bearings were replaced and pump motor alignment was corrected under guidance of the engineering team. 18A pump motor was brought back to operation after a successful round of testing. Supervision will continue to monitor the situation. | What were the immediate actions and recommended actions after noticing an abnormal rise in temperature of the 18A pump motor? | Immediate inspection and necessary maintenance of 18A pump motor is suggested, under guidance from the maintenance supervisor and engineering team.
479 | 2019-04-30 | 30987450 | 80239876 | Unusual vibration in 18B Blower | S5BL -3BLE6 | * **************Incident Description************** * Notification 000030987450 Details * *********************************************************** * 04/30/2019 15:49:00 INCIDENT REPORT (INCIDENT REPORT) * Report submitted by: Daniel Brown ENTITY\INCIDENT: * * CONDITION DESCRIPTION/LOCATION (THE INAPPROPRIATE ACTION AND ITS NEGATIVE EFFECT/INCLUDE A DETAILED LOCATION DESCRIPTION): * During an operational check, a higher than usual vibration was detected from the blower unit 18B. Operator reported the anomaly and further inspection revealed slight wobble in the belt drive. This deviation is not normal for the 18B Blower Unit. * * ACTIVITIES, PROCESSES, PROCEDURES INVOLVED: * S5.OP-AB.BL-0002, S5.OP-SO.BL-0001 * * WHY DID CONDITION HAPPEN? * Preliminary analysis points towards a possible misalignment in the drive assembly or wear and tear of the belt. * * CONSEQUENCES: * Can lead to blower damage if not rectified. This could potentially affect system efficiency and bear heavy repair costs. * * REQUIREMENTS IMPACTED: * The blower operation may need to be stopped for repairs. * * ADVERSE PHYSICAL CONDITIONS: * High vibration levels, probable drive misalignment * * WHO WAS NOTIFIED: * Supervisor, Maintenance Team * * KNOWLEDGEABLE INDIVIDUALS: * Supervisor; Team Lead, Mechanical; Maintenance Engineers * * REPEAT OR SIMILAR CONDITION: * No, first such incident * * IMMEDIATE ACTIONS AND RECOMMENDED ACTIONS: * Maintenance team to inspect the Blower Assembly, specific focus on the drive belt and alignment. If required, replace or adjust the components. * 05/02/2019 09:18:45 RACHEL GREEN (INCIDENT) * Blower has been inspected and the misalignment corrected. The drive belt showed signs of wear and has been replaced. Blower now operating within normal parameters. | What measures were taken to correct the issue with the blower unit? | Blower has been inspected and the misalignment corrected. The drive belt showed signs of wear and has been replaced. Blower now operating within normal parameters.
480 | 2021-09-15 | 30985240 | 80589752 | Abnormal vibration in Fan 5A | S5AI -5AIE3 | * **************Incident Description************** * Notification 000030985240 Details * *********************************************************** * 09/15/2021 18:20:49 INCIDENT REPORT (INCIDENT REPORT) * Report submitted by: Samantha Adams ENTITY\INCIDENT: * * CONDITION DESCRIPTION/LOCATION (THE INAPPROPRIATE ACTION AND ITS NEGATIVE EFFECT/INCLUDE A DETAILED LOCATION DESCRIPTION): * During the routine maintenance check, abnormal vibration was detected in Fan 5A. The vibration level was beyond the accepted limit which triggered the alarm. Fan 5A was shut down for further inspections. There was no apparent damage or leakage. S5.OP-AB.AI-0003 Fan Abnormality was initiated due to the emergency shutdown of Fan 5A. * * ACTIVITIES, PROCESSES, PROCEDURES INVOLVED: * S5.OP.AB-AI-0003, S5.OP-SO.AI-0001 * * WHY DID CONDITION HAPPEN? * Unknown, need to investigate the cause of abnormal vibrations. * * CONSEQUENCES: * Continuous operation with abnormal vibration may lead to fan damage, decreased equipment life and potential safety hazards. * * REQUIREMENTS IMPACTED: * Abnormal shutdown of Fan 5A * * ADVERSE PHYSICAL CONDITIONS: * High vibration in Fan 5A, risk of equipment failure. * * WHO WAS NOTIFIED: * Supervisor, Maintenance Team * * KNOWLEDGEABLE INDIVIDUALS: * Parker, Davis, Thompson * * REPEAT OR SIMILAR CONDITION: * No * * IMMEDIATE ACTIONS AND RECOMMENDED ACTIONS: * Engineering team will inspect Fan 5A to determine the cause of the high vibration. If necessary, components will be replaced. * 09/17/2021 09:32:19 ROBERT SMITH (INCIDENT) * Post inspection, it was discovered that the abnormal vibrations were due to a misaligned fan blade. The component was adjusted and Fan 5A is now operating normally without any abnormal vibrations. | What was the cause of the abnormal vibrations in Fan 5A? | The abnormal vibrations were due to a misaligned fan blade.
481 | 2019-04-28 | 30920832 | 80287345 | 29B Pump unusual vibration detected | S1CW -1CWE5 | * **************Incident Description************** * Notification 000030920832 Details * *********************************************************** * 04/28/2019 14:34:12 INCIDENT REPORT (INCIDENT REPORT) * Report submitted by: Laura Thompson ENTITY\INCIDENT: * * CONDITION DESCRIPTION/LOCATION (THE INAPPROPRIATE ACTION AND ITS NEGATIVE EFFECT/INCLUDE A DETAILED LOCATION DESCRIPTION): * During daily operations, the 29B Pump was identified as vibrating more than the normal limits. Its rpm readings were off the standard curve and the vibration was also audible. The pump was operating under normal inlet pressure. Similar vibration traces were last noticed prior to maintenance on 31A pump. * * ACTIVITIES, PROCESSES, PROCEDURES INVOLVED: * Regular Operation * * WHY DID CONDITION HAPPEN? * The reason for the excessive vibration is not known yet. It could be a misalignment or internal pump damage. * * CONSEQUENCES: * Potential equipment failure, decreased operational efficiency and safety risks. * * REQUIREMENTS IMPACTED: * Continued normal operation of the 29B pump. * * ADVERSE PHYSICAL CONDITIONS: * Abnormal vibration of 29B pump. * * WHO WAS NOTIFIED: * Operational Control Room, Maintenance Team * * KNOWLEDGEABLE INDIVIDUALS: * Operational Team, Maintenance Team * * REPEAT OR SIMILAR CONDITION: * Yes, with the 31A pump * * IMMEDIATE ACTIONS AND RECOMMENDED ACTIONS: * Immediate shutdown of the 29B pump and maintenance inspection to determine the cause of the excessive vibration. * 04/28/2019 20:05:56 LAURA THOMPSON (INCIDENT) * The 29B pump has been shut down for maintenance. The internal inspection is due to be performed and any necessary repairs will be performed. Expected to be back in operation once the issue has been fully addressed. | What actions were recommended upon identifying the abnormal condition of the 29B pump? | Immediate shutdown of the 29B pump and maintenance inspection to determine the cause of the excessive vibration.